## DCS_IO_DB_FCS0703
AREA | PID_SHT | PID_TAG | COMMENT(Chinese) | COMMENT | FCS_COMP_NAME | FCS | NODE | SLOT | TERMINAL | MODULE | SIGNAL | DUPLEX | DIOTAG | LOOP | DCS_TAG | TYPNO | DRAWNO | TGCOMM | ENG_LO | ENG_HI | ENG_UNITS | IOADDR_SYSTAG | IO_TYPE | Wire_Type | MRP_COMP_Name | BoardModel | Board_No | Board_TB_No | Board_TB_No | Board_TB_No | TBNo. | TB A or (+) | TB B or (-) | TB C | Remarks | Source | Type | I/O | HHH | HH | H | L | LL | LLL | LOG | SOE | DCS Subfunction | Power Supply | Excitation Voltage | Drawing No. | Chinese Remark | English Remark
区域 |  | 测点编号 | 测点中文名称 | 测点英文名称 | 控制柜机柜名 | 控制器编号 | 节点编号 | 插槽编号 | 通道编号 | 卡见类型 | 信号类型 | 冗余 | 通道编号 | 回路 | DCS测点编号 | 类型 | DR图号 | 注释 | 下限 | 上限 | 单位 | 系统地址 | IO类型 | 线制 | 接线柜柜号 | 端子板类型 | 端子板编号 | 端子编号 | 端子编号 | 端子编号 | 端子编号 | 端子A编号 | 端子B编号 | 端子C编号 | 备注 | 信号来源 | 信号制 | 信号类别 | 报警 | [5 empty] | 记录 |  | DCS 子功能 | 供电方 | 励磁电压 | 图号 | 中文备注 | 英文备注
|  | 70HJF10CP101 | 油点火燃烧器供油母管压力 | Oil ignition burner oli supply main pipe pressure | 70CRA07 | FCS0703 | 1 | 1 | 1 | AAI143-H | 4~20mA | N | %Z011101 | [5 empty] | 0 | 2.5 | Mpa | %Z011101 | AI |  | 70CRA08 | [5 empty] | TBB01 | 1 | 2 |  |  | 70HJF10CP101 | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-001
|  | 70HBB10CT101A | 锅炉炉膛床温1 | Boiler furnace bed temperature 1 | 70CRA07 | FCS0703 | 1 | 1 | 2 | AAI143-H | 4~20mA | N | %Z011102 | [5 empty] | 0 | 1200 | ℃ | %Z011102 | AI |  | 70CRA08 | [5 empty] | TBB01 | 3 | 4 |  |  | 70HBB10CT101A | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CT101D | 锅炉炉膛床温4 | Boiler furnace bed temperature 4 | 70CRA07 | FCS0703 | 1 | 1 | 3 | AAI143-H | 4~20mA | N | %Z011103 | [5 empty] | 0 | 1200 | ℃ | %Z011103 | AI |  | 70CRA08 | [5 empty] | TBB01 | 5 | 6 |  |  | 70HBB10CT101D | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CT101G | 锅炉炉膛床温7 | Boiler furnace bed temperature 7 | 70CRA07 | FCS0703 | 1 | 1 | 4 | AAI143-H | 4~20mA | N | %Z011104 | [5 empty] | 0 | 1200 | ℃ | %Z011104 | AI |  | 70CRA08 | [5 empty] | TBB01 | 7 | 8 |  |  | 70HBB10CT101G | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CT104A | 锅炉炉膛出口烟气温度左1 | Boiler furnace outlet flue gas temperature left 1 | 70CRA07 | FCS0703 | 1 | 1 | 5 | AAI143-H | 4~20mA | N | %Z011105 | [5 empty] | 0 | 1200 | ℃ | %Z011105 | AI |  | 70CRA08 | [5 empty] | TBB01 | 9 | 10 |  |  | 70HBB10CT104A | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CT105A | 锅炉炉膛出口烟气温度右1 | Boiler furnace outlet flue gas temperature right 1 | 70CRA07 | FCS0703 | 1 | 1 | 6 | AAI143-H | 4~20mA | N | %Z011106 | [5 empty] | 0 | 1200 | ℃ | %Z011106 | AI |  | 70CRA08 | [5 empty] | TBB01 | 11 | 12 |  |  | 70HBB10CT105A | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HLA40CP101A | 1#风室热一次风压力1 | 1# wind box hot primary air pressure 1 | 70CRA07 | FCS0703 | 1 | 1 | 7 | AAI143-H | 4~20mA | N | %Z011107 | [5 empty] | 0 | 30 | KPa | %Z011107 | AI |  | 70CRA08 | [5 empty] | TBB01 | 13 | 14 |  |  | 70HLA40CP101A | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-008
|  | 70HLA50CP101A | 2#风室热一次风压力1 | 2# wind box hot primary air pressure 1 | 70CRA07 | FCS0703 | 1 | 1 | 8 | AAI143-H | 4~20mA | N | %Z011108 | [5 empty] | 0 | 30 | KPa | %Z011108 | AI |  | 70CRA08 | [5 empty] | TBB01 | 15 | 16 |  |  | 70HLA50CP101A | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-008
|  | 70HJF11CB101XQ01 | 1#油点火燃烧器火焰强度 | 1# oil ignition burner flame strength | 70CRA07 | FCS0703 | 1 | 1 | 9 | AAI143-H | 4~20mA | N | %Z011109 | [5 empty] | 0 | 100 | % | %Z011109 | AI | 4W | 70CRA08 | [5 empty] | TBB01 | 17 | 18 |  |  | 70HJF10GH002 | 4~20mA | AI | [8 empty] | FSSS | U |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
|  | 70HJF12CB101XQ01 | 2#油点火燃烧器火焰强度 | 2# oil ignition burner flame strength | 70CRA07 | FCS0703 | 1 | 1 | 10 | AAI143-H | 4~20mA | N | %Z011110 | [5 empty] | 0 | 100 | % | %Z011110 | AI | 4W | 70CRA08 | [5 empty] | TBB01 | 19 | 20 |  |  | 70HJF10GH002 | 4~20mA | AI | [8 empty] | FSSS | U |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
[5 empty] | 70CRA07 | FCS0703 | 1 | 1 | 11 | AAI143-H | 4~20mA | N | %Z011111 | [8 empty] | %Z011111 | AI |  | 70CRA08 | [5 empty] | TBB01 | 21 | 22
[5 empty] | 70CRA07 | FCS0703 | 1 | 1 | 12 | AAI143-H | 4~20mA | N | %Z011112 | [8 empty] | %Z011112 | AI |  | 70CRA08 | [5 empty] | TBB01 | 23 | 24
[5 empty] | 70CRA07 | FCS0703 | 1 | 1 | 13 | AAI143-H | 4~20mA | N | %Z011113 | [8 empty] | %Z011113 | AI |  | 70CRA08 | [5 empty] | TBB01 | 25 | 26
[5 empty] | 70CRA07 | FCS0703 | 1 | 1 | 14 | AAI143-H | 4~20mA | N | %Z011114 | [8 empty] | %Z011114 | AI |  | 70CRA08 | [5 empty] | TBB01 | 27 | 28
[5 empty] | 70CRA07 | FCS0703 | 1 | 1 | 15 | AAI143-H | 4~20mA | N | %Z011115 | [8 empty] | %Z011115 | AI |  | 70CRA08 | [5 empty] | TBB01 | 29 | 30
[5 empty] | 70CRA07 | FCS0703 | 1 | 1 | 16 | AAI143-H | 4~20mA | N | %Z011116 | [8 empty] | %Z011116 | AI |  | 70CRA08 | [5 empty] | TBB01 | 31 | 32
|  | 70HJF20CP101 | 油点火燃烧器回油母管压力 | Oil ignition burner oli return main pipe pressure | 70CRA07 | FCS0703 | 2 | 1 | 1 | AAI143-H | 4~20mA | N | %Z021101 | [5 empty] | 0 | 2.5 | Mpa | %Z021101 | AI |  | 70CRA08 | [5 empty] | TBB02 | 1 | 2 |  |  | 70HJF20CP101 | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-001
|  | 70HBB10CT101B | 锅炉炉膛床温2 | Boiler furnace bed temperature 2 | 70CRA07 | FCS0703 | 2 | 1 | 2 | AAI143-H | 4~20mA | N | %Z021102 | [5 empty] | 0 | 1200 | ℃ | %Z021102 | AI |  | 70CRA08 | [5 empty] | TBB02 | 3 | 4 |  |  | 70HBB10CT101B | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CT101E | 锅炉炉膛床温5 | Boiler furnace bed temperature 5 | 70CRA07 | FCS0703 | 2 | 1 | 3 | AAI143-H | 4~20mA | N | %Z021103 | [5 empty] | 0 | 1200 | ℃ | %Z021103 | AI |  | 70CRA08 | [5 empty] | TBB02 | 5 | 6 |  |  | 70HBB10CT101E | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CT101H | 锅炉炉膛床温8 | Boiler furnace bed temperature 8 | 70CRA07 | FCS0703 | 2 | 1 | 4 | AAI143-H | 4~20mA | N | %Z021104 | [5 empty] | 0 | 1200 | ℃ | %Z021104 | AI |  | 70CRA08 | [5 empty] | TBB02 | 7 | 8 |  |  | 70HBB10CT101H | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CT104B | 锅炉炉膛出口烟气温度左2 | Boiler furnace outlet flue gas temperature left 2 | 70CRA07 | FCS0703 | 2 | 1 | 5 | AAI143-H | 4~20mA | N | %Z021105 | [5 empty] | 0 | 1200 | ℃ | %Z021105 | AI |  | 70CRA08 | [5 empty] | TBB02 | 9 | 10 |  |  | 70HBB10CT104B | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CT105B | 锅炉炉膛出口烟气温度右2 | Boiler furnace outlet flue gas temperature right 2 | 70CRA07 | FCS0703 | 2 | 1 | 6 | AAI143-H | 4~20mA | N | %Z021106 | [5 empty] | 0 | 1200 | ℃ | %Z021106 | AI |  | 70CRA08 | [5 empty] | TBB02 | 11 | 12 |  |  | 70HBB10CT105B | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HLA40CP101B | 1#风室热一次风压力2 | 1# wind box hot primary air pressure 2 | 70CRA07 | FCS0703 | 2 | 1 | 7 | AAI143-H | 4~20mA | N | %Z021107 | [5 empty] | 0 | 30 | KPa | %Z021107 | AI |  | 70CRA08 | [5 empty] | TBB02 | 13 | 14 |  |  | 70HLA40CP101B | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-008
|  | 70HLA50CP101B | 2#风室热一次风压力2 | 2# wind box hot primary air pressure 2 | 70CRA07 | FCS0703 | 2 | 1 | 8 | AAI143-H | 4~20mA | N | %Z021108 | [5 empty] | 0 | 30 | KPa | %Z021108 | AI |  | 70CRA08 | [5 empty] | TBB02 | 15 | 16 |  |  | 70HLA50CP101B | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-008
|  | 70HJF13CB101XQ01 | 3#油点火燃烧器火焰强度 | 3# oil ignition burner flame strength | 70CRA07 | FCS0703 | 2 | 1 | 9 | AAI143-H | 4~20mA | N | %Z021109 | [5 empty] | 0 | 100 | % | %Z021109 | AI | 4W | 70CRA08 | [5 empty] | TBB02 | 17 | 18 |  |  | 70HJF10GH002 | 4~20mA | AI | [8 empty] | FSSS | U |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
|  | 70HJF14CB101XQ01 | 4#油点火燃烧器火焰强度 | 4# oil ignition burner flame strength | 70CRA07 | FCS0703 | 2 | 1 | 10 | AAI143-H | 4~20mA | N | %Z021110 | [5 empty] | 0 | 100 | % | %Z021110 | AI | 4W | 70CRA08 | [5 empty] | TBB02 | 19 | 20 |  |  | 70HJF10GH002 | 4~20mA | AI | [8 empty] | FSSS | U |  | K0202-003 | 火检电源柜 | Flame detection power cabinet
[5 empty] | 70CRA07 | FCS0703 | 2 | 1 | 11 | AAI143-H | 4~20mA | N | %Z021111 | [8 empty] | %Z021111 | AI |  | 70CRA08 | [5 empty] | TBB02 | 21 | 22
[5 empty] | 70CRA07 | FCS0703 | 2 | 1 | 12 | AAI143-H | 4~20mA | N | %Z021112 | [8 empty] | %Z021112 | AI |  | 70CRA08 | [5 empty] | TBB02 | 23 | 24
[5 empty] | 70CRA07 | FCS0703 | 2 | 1 | 13 | AAI143-H | 4~20mA | N | %Z021113 | [8 empty] | %Z021113 | AI |  | 70CRA08 | [5 empty] | TBB02 | 25 | 26
[5 empty] | 70CRA07 | FCS0703 | 2 | 1 | 14 | AAI143-H | 4~20mA | N | %Z021114 | [8 empty] | %Z021114 | AI |  | 70CRA08 | [5 empty] | TBB02 | 27 | 28
[5 empty] | 70CRA07 | FCS0703 | 2 | 1 | 15 | AAI143-H | 4~20mA | N | %Z021115 | [8 empty] | %Z021115 | AI |  | 70CRA08 | [5 empty] | TBB02 | 29 | 30
[5 empty] | 70CRA07 | FCS0703 | 2 | 1 | 16 | AAI143-H | 4~20mA | N | %Z021116 | [8 empty] | %Z021116 | AI |  | 70CRA08 | [5 empty] | TBB02 | 31 | 32
|  | 70HJF20CF101 | 油点火燃烧器回油母管流量 | Oil ignition burner oli return main pipe flow | 70CRA07 | FCS0703 | 3 | 1 | 1 | AAI143-H | 4~20mA | N | %Z031101 | [5 empty] | 0 | 10 | t/h | %Z031101 | AI | 4W | 70CRA08 | [5 empty] | TBB03 | 1 | 2 |  |  | 70HJF20CF101 | 4~20mA | AI | [8 empty] | FSSS | U |  | K0202-001
|  | 70HBB10CT101C | 锅炉炉膛床温3 | Boiler furnace bed temperature 3 | 70CRA07 | FCS0703 | 3 | 1 | 2 | AAI143-H | 4~20mA | N | %Z031102 | [5 empty] | 0 | 1200 | ℃ | %Z031102 | AI |  | 70CRA08 | [5 empty] | TBB03 | 3 | 4 |  |  | 70HBB10CT101C | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CT101F | 锅炉炉膛床温6 | Boiler furnace bed temperature 6 | 70CRA07 | FCS0703 | 3 | 1 | 3 | AAI143-H | 4~20mA | N | %Z031103 | [5 empty] | 0 | 1200 | ℃ | %Z031103 | AI |  | 70CRA08 | [5 empty] | TBB03 | 5 | 6 |  |  | 70HBB10CT101F | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
[5 empty] | 70CRA07 | FCS0703 | 3 | 1 | 4 | AAI143-H | 4~20mA | N | %Z031104 | [8 empty] | %Z031104 | AI |  | 70CRA08 | [5 empty] | TBB03 | 7 | 8
|  | 70HBB10CT104C | 锅炉炉膛出口烟气温度左3 | Boiler furnace outlet flue gas temperature left 3 | 70CRA07 | FCS0703 | 3 | 1 | 5 | AAI143-H | 4~20mA | N | %Z031105 | [5 empty] | 0 | 1200 | ℃ | %Z031105 | AI |  | 70CRA08 | [5 empty] | TBB03 | 9 | 10 |  |  | 70HBB10CT104C | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CT105C | 锅炉炉膛出口烟气温度右3 | Boiler furnace outlet flue gas temperature right 3 | 70CRA07 | FCS0703 | 3 | 1 | 6 | AAI143-H | 4~20mA | N | %Z031106 | [5 empty] | 0 | 1200 | ℃ | %Z031106 | AI |  | 70CRA08 | [5 empty] | TBB03 | 11 | 12 |  |  | 70HBB10CT105C | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-005
|  | 70HLA40CP101C | 1#风室热一次风压力3 | 1# wind box hot primary air pressure 3 | 70CRA07 | FCS0703 | 3 | 1 | 7 | AAI143-H | 4~20mA | N | %Z031107 | [5 empty] | 0 | 30 | KPa | %Z031107 | AI |  | 70CRA08 | [5 empty] | TBB03 | 13 | 14 |  |  | 70HLA40CP101C | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-008
|  | 70HLA50CP101C | 2#风室热一次风压力3 | 2# wind box hot primary air pressure 3 | 70CRA07 | FCS0703 | 3 | 1 | 8 | AAI143-H | 4~20mA | N | %Z031108 | [5 empty] | 0 | 30 | KPa | %Z031108 | AI |  | 70CRA08 | [5 empty] | TBB03 | 15 | 16 |  |  | 70HLA50CP101C | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-008
|  | 70HJF15CB101XQ01 | 5#油点火燃烧器火焰强度 | 5# oil ignition burner flame strength | 70CRA07 | FCS0703 | 3 | 1 | 9 | AAI143-H | 4~20mA | N | %Z031109 | [5 empty] | 0 | 100 | % | %Z031109 | AI |  | 70CRA08 | [5 empty] | TBB03 | 17 | 18 |  |  | 70HJF10GH002 | 4~20mA | AI | [8 empty] | FSSS | D |  | K0202-003 | 火检电源柜 | Flame detection power cabinet
[5 empty] | 70CRA07 | FCS0703 | 3 | 1 | 10 | AAI143-H | 4~20mA | N | %Z031110 | [8 empty] | %Z031110 | AI |  | 70CRA08 | [5 empty] | TBB03 | 19 | 20
[5 empty] | 70CRA07 | FCS0703 | 3 | 1 | 11 | AAI143-H | 4~20mA | N | %Z031111 | [8 empty] | %Z031111 | AI |  | 70CRA08 | [5 empty] | TBB03 | 21 | 22
[5 empty] | 70CRA07 | FCS0703 | 3 | 1 | 12 | AAI143-H | 4~20mA | N | %Z031112 | [8 empty] | %Z031112 | AI |  | 70CRA08 | [5 empty] | TBB03 | 23 | 24
[5 empty] | 70CRA07 | FCS0703 | 3 | 1 | 13 | AAI143-H | 4~20mA | N | %Z031113 | [8 empty] | %Z031113 | AI |  | 70CRA08 | [5 empty] | TBB03 | 25 | 26
[5 empty] | 70CRA07 | FCS0703 | 3 | 1 | 14 | AAI143-H | 4~20mA | N | %Z031114 | [8 empty] | %Z031114 | AI |  | 70CRA08 | [5 empty] | TBB03 | 27 | 28
[5 empty] | 70CRA07 | FCS0703 | 3 | 1 | 15 | AAI143-H | 4~20mA | N | %Z031115 | [8 empty] | %Z031115 | AI |  | 70CRA08 | [5 empty] | TBB03 | 29 | 30
[5 empty] | 70CRA07 | FCS0703 | 3 | 1 | 16 | AAI143-H | 4~20mA | N | %Z031116 | [8 empty] | %Z031116 | AI |  | 70CRA08 | [5 empty] | TBB03 | 31 | 32
|  | 70HFB10AF001XB01 | 1#给煤机运行 | 1# coal feeder running | 70CRA07 | FCS0703 | 1 | 2 | 1 | ADV151-P | SI | N | 70HFB10AF001XB01 |  | 70HFB10AF001XB01 |  |  | 1# coal feeder running |  |  |  | %Z012101 | DI |  | 70CRA08 | [5 empty] | TBF01 | 1 | 2 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB02 | 1#给煤机清扫运行 | 1# coal feeder sweeper running | 70CRA07 | FCS0703 | 1 | 2 | 2 | ADV151-P | SI | N | 70HFB10AF001XB02 |  | 70HFB10AF001XB02 |  |  | 1# coal feeder sweeper running |  |  |  | %Z012102 | DI |  | 70CRA08 | [5 empty] | TBF01 | 3 | 4 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB03 | 1#给煤机容积输出显示 | 1# coal feeder volume output display | 70CRA07 | FCS0703 | 1 | 2 | 3 | ADV151-P | SI | N | 70HFB10AF001XB03 |  | 70HFB10AF001XB03 |  |  | 1# coal feeder volume output display |  |  |  | %Z012103 | DI |  | 70CRA08 | [5 empty] | TBF01 | 5 | 6 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB11 | 1#给煤机停止信号 | 1# coal feeder stopped signal | 70CRA07 | FCS0703 | 1 | 2 | 4 | ADV151-P | SI | N | 70HFB10AF001XB11 |  | 70HFB10AF001XB11 |  |  | 1# coal feeder stopped signal |  |  |  | %Z012104 | DI |  | 70CRA08 | [5 empty] | TBF01 | 7 | 8 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB21 | 1#给煤机远控备妥 | 1# coal feeder remote control already | 70CRA07 | FCS0703 | 1 | 2 | 5 | ADV151-P | SI | N | 70HFB10AF001XB21 |  | 70HFB10AF001XB21 |  |  | 1# coal feeder remote control already |  |  |  | %Z012105 | DI |  | 70CRA08 | [5 empty] | TBF01 | 9 | 10 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB31 | 1#给煤机电机故障 | 1# coal feeder motor fault | 70CRA07 | FCS0703 | 1 | 2 | 6 | ADV151-P | SI | N | 70HFB10AF001XB31 |  | 70HFB10AF001XB31 |  |  | 1# coal feeder motor fault |  |  |  | %Z012106 | DI |  | 70CRA08 | [5 empty] | TBF01 | 11 | 12 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB32 | 1#给煤机清扫电机故障 | 1# coal feeder sweeper motor fault | 70CRA07 | FCS0703 | 1 | 2 | 7 | ADV151-P | SI | N | 70HFB10AF001XB32 |  | 70HFB10AF001XB32 |  |  | 1# coal feeder sweeper motor fault |  |  |  | %Z012107 | DI |  | 70CRA08 | [5 empty] | TBF01 | 13 | 14 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB33 | 1#给煤机跑偏报警 | 1# coal feeder offset alarm | 70CRA07 | FCS0703 | 1 | 2 | 8 | ADV151-P | SI | N | 70HFB10AF001XB33 |  | 70HFB10AF001XB33 |  |  | 1# coal feeder offset alarm |  |  |  | %Z012108 | DI |  | 70CRA08 | [5 empty] | TBF01 | 15 | 16 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB34 | 1#给煤机出口堵料故障 | 1# coal feeder exit blockage fault | 70CRA07 | FCS0703 | 1 | 2 | 9 | ADV151-P | SI | N | 70HFB10AF001XB34 |  | 70HFB10AF001XB34 |  |  | 1# coal feeder exit blockage fault |  |  |  | %Z012109 | DI |  | 70CRA08 | [5 empty] | TBF01 | 17 | 18 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB35 | 1#给煤机断料故障 | 1# coal feeder material-shortage | 70CRA07 | FCS0703 | 1 | 2 | 10 | ADV151-P | SI | N | 70HFB10AF001XB35 |  | 70HFB10AF001XB35 |  |  | 1# coal feeder material-shortage |  |  |  | %Z012110 | DI |  | 70CRA08 | [5 empty] | TBF01 | 19 | 20 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB36 | 1#给煤机给料偏差报警 | 1# coal feeder feed rate error | 70CRA07 | FCS0703 | 1 | 2 | 11 | ADV151-P | SI | N | 70HFB10AF001XB36 |  | 70HFB10AF001XB36 |  |  | 1# coal feeder feed rate error |  |  |  | %Z012111 | DI |  | 70CRA08 | [5 empty] | TBF01 | 21 | 22 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB37 | 1#给煤机超温故障 | 1# coal feeder over-temperature fault | 70CRA07 | FCS0703 | 1 | 2 | 12 | ADV151-P | SI | N | 70HFB10AF001XB37 |  | 70HFB10AF001XB37 |  |  | 1# coal feeder over-temperature fault |  |  |  | %Z012112 | DI |  | 70CRA08 | [5 empty] | TBF01 | 23 | 24 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001XB38 | 1#给煤机进口煤流报警 | 1# coal feeder coal flow monitor alarm | 70CRA07 | FCS0703 | 1 | 2 | 13 | ADV151-P | SI | N | 70HFB10AF001XB38 |  | 70HFB10AF001XB38 |  |  | 1# coal feeder coal flow monitor alarm |  |  |  | %Z012113 | DI |  | 70CRA08 | [5 empty] | TBF01 | 25 | 26 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA001XB01 | 1#给煤机进口电动闸阀全开状态 | 1# coal feeder inlet MOV full opened status | 70CRA07 | FCS0703 | 1 | 2 | 14 | ADV151-P | SI | N | 70HFB10AA001XB01 |  | 70HFB10AA001XB01 |  |  | 1# coal feeder inlet MOV full opened status |  |  |  | %Z012114 | DI |  | 70CRA08 | [5 empty] | TBF01 | 27 | 28 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA001XB11 | 1#给煤机进口电动闸阀全关状态 | 1# coal feeder inlet MOV full closed status | 70CRA07 | FCS0703 | 1 | 2 | 15 | ADV151-P | SI | N | 70HFB10AA001XB11 |  | 70HFB10AA001XB11 |  |  | 1# coal feeder inlet MOV full closed status |  |  |  | %Z012115 | DI |  | 70CRA08 | [5 empty] | TBF01 | 29 | 30 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA001XB21 | 1#给煤机进口电动闸阀远控允许 | 1# coal feeder inlet MOV remote control permitted | 70CRA07 | FCS0703 | 1 | 2 | 16 | ADV151-P | SI | N | 70HFB10AA001XB21 |  | 70HFB10AA001XB21 |  |  | 1# coal feeder inlet MOV remote control permitted |  |  |  | %Z012116 | DI |  | 70CRA08 | [5 empty] | TBF01 | 31 | 32 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA001XB31 | 1#给煤机进口电动闸阀故障 | 1# coal feeder inlet MOV fault | 70CRA07 | FCS0703 | 1 | 2 | 17 | ADV151-P | SI | N | 70HFB10AA001XB31 |  | 70HFB10AA001XB31 |  |  | 1# coal feeder inlet MOV fault |  |  |  | %Z012117 | DI |  | 70CRA08 | [5 empty] | TBF01 | 33 | 34 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA002XB01 | 1#给煤机出口气动阀全开状态 | 1# coal feeder outlet PV full opened status | 70CRA07 | FCS0703 | 1 | 2 | 18 | ADV151-P | SI | N | 70HFB10AA002XB01 |  | 70HFB10AA002XB01 |  |  | 1# coal feeder outlet PV full opened status |  |  |  | %Z012118 | DI |  | 70CRA08 | [5 empty] | TBF01 | 35 | 36 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA002XB11 | 1#给煤机出口气动阀全关状态 | 1# coal feeder outlet PV full closed status | 70CRA07 | FCS0703 | 1 | 2 | 19 | ADV151-P | SI | N | 70HFB10AA002XB11 |  | 70HFB10AA002XB11 |  |  | 1# coal feeder outlet PV full closed status |  |  |  | %Z012119 | DI |  | 70CRA08 | [5 empty] | TBF01 | 37 | 38 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA002XB21 | 1#给煤机出口气动阀远控允许 | 1# coal feeder outlet PV remote control permitted | 70CRA07 | FCS0703 | 1 | 2 | 20 | ADV151-P | SI | N | 70HFB10AA002XB21 |  | 70HFB10AA002XB21 |  |  | 1# coal feeder outlet PV remote control permitted |  |  |  | %Z012120 | DI |  | 70CRA08 | [5 empty] | TBF01 | 39 | 40 |  |  | 70HFB10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB60AF001XB01 | 污泥给料机运行 | Sludge feeder running | 70CRA07 | FCS0703 | 1 | 2 | 21 | ADV151-P | SI | N | 70HFB60AF001XB01 |  | 70HFB60AF001XB01 |  |  | Sludge feeder running |  |  |  | %Z012121 | DI |  | 70CRA08 | [5 empty] | TBF01 | 41 | 42 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
|  | 70HFB60AF001XB02 | 污泥给料机清扫运行 | Sludge feeder sweeper running | 70CRA07 | FCS0703 | 1 | 2 | 22 | ADV151-P | SI | N | 70HFB60AF001XB02 |  | 70HFB60AF001XB02 |  |  | Sludge feeder sweeper running |  |  |  | %Z012122 | DI |  | 70CRA08 | [5 empty] | TBF01 | 43 | 44 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
|  | 70HFB60AF001XB03 | 污泥给料机容积输出显示 | Sludge feeder volume output display | 70CRA07 | FCS0703 | 1 | 2 | 23 | ADV151-P | SI | N | 70HFB60AF001XB03 |  | 70HFB60AF001XB03 |  |  | Sludge feeder volume output display |  |  |  | %Z012123 | DI |  | 70CRA08 | [5 empty] | TBF01 | 45 | 46 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
|  | 70HFB60AF001XB11 | 污泥给料机停止信号 | Sludge feeder stopped signal | 70CRA07 | FCS0703 | 1 | 2 | 24 | ADV151-P | SI | N | 70HFB60AF001XB11 |  | 70HFB60AF001XB11 |  |  | Sludge feeder stopped signal |  |  |  | %Z012124 | DI |  | 70CRA08 | [5 empty] | TBF01 | 47 | 48 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
|  | 70HFB60AF001XB21 | 污泥给料机远控备妥 | Sludge feeder remote control already | 70CRA07 | FCS0703 | 1 | 2 | 25 | ADV151-P | SI | N | 70HFB60AF001XB21 |  | 70HFB60AF001XB21 |  |  | Sludge feeder remote control already |  |  |  | %Z012125 | DI |  | 70CRA08 | [5 empty] | TBF01 | 49 | 50 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
[5 empty] | 70CRA07 | FCS0703 | 1 | 2 | 26 | ADV151-P | SI | N | [9 empty] | %Z012126 | DI |  | 70CRA08 | [5 empty] | TBF01 | 51 | 52
[5 empty] | 70CRA07 | FCS0703 | 1 | 2 | 27 | ADV151-P | SI | N | [9 empty] | %Z012127 | DI |  | 70CRA08 | [5 empty] | TBF01 | 53 | 54
[5 empty] | 70CRA07 | FCS0703 | 1 | 2 | 28 | ADV151-P | SI | N | [9 empty] | %Z012128 | DI |  | 70CRA08 | [5 empty] | TBF01 | 55 | 56
[5 empty] | 70CRA07 | FCS0703 | 1 | 2 | 29 | ADV151-P | SI | N | [9 empty] | %Z012129 | DI |  | 70CRA08 | [5 empty] | TBF01 | 57 | 58
[5 empty] | 70CRA07 | FCS0703 | 1 | 2 | 30 | ADV151-P | SI | N | [9 empty] | %Z012130 | DI |  | 70CRA08 | [5 empty] | TBF01 | 59 | 60
[5 empty] | 70CRA07 | FCS0703 | 1 | 2 | 31 | ADV151-P | SI | N | [9 empty] | %Z012131 | DI |  | 70CRA08 | [5 empty] | TBF01 | 61 | 62
[5 empty] | 70CRA07 | FCS0703 | 1 | 2 | 32 | ADV151-P | SI | N | [9 empty] | %Z012132 | DI |  | 70CRA08 | [5 empty] | TBF01 | 63 | 64
|  | 70HFB20AF001XB01 | 2#给煤机运行 | 2# coal feeder running | 70CRA07 | FCS0703 | 1 | 3 | 1 | ADV151-P | SI | N | 70HFB20AF001XB01 |  | 70HFB20AF001XB01 |  |  | 2# coal feeder running |  |  |  | %Z013101 | DI |  | 70CRA08 | [5 empty] | TBF02 | 1 | 2 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB02 | 2#给煤机清扫运行 | 2# coal feeder sweeper running | 70CRA07 | FCS0703 | 1 | 3 | 2 | ADV151-P | SI | N | 70HFB20AF001XB02 |  | 70HFB20AF001XB02 |  |  | 2# coal feeder sweeper running |  |  |  | %Z013102 | DI |  | 70CRA08 | [5 empty] | TBF02 | 3 | 4 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB03 | 2#给煤机容积输出显示 | 2# coal feeder volume output display | 70CRA07 | FCS0703 | 1 | 3 | 3 | ADV151-P | SI | N | 70HFB20AF001XB03 |  | 70HFB20AF001XB03 |  |  | 2# coal feeder volume output display |  |  |  | %Z013103 | DI |  | 70CRA08 | [5 empty] | TBF02 | 5 | 6 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB11 | 2#给煤机停止信号 | 2# coal feeder stopped signal | 70CRA07 | FCS0703 | 1 | 3 | 4 | ADV151-P | SI | N | 70HFB20AF001XB11 |  | 70HFB20AF001XB11 |  |  | 2# coal feeder stopped signal |  |  |  | %Z013104 | DI |  | 70CRA08 | [5 empty] | TBF02 | 7 | 8 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB21 | 2#给煤机远控备妥 | 2# coal feeder remote control already | 70CRA07 | FCS0703 | 1 | 3 | 5 | ADV151-P | SI | N | 70HFB20AF001XB21 |  | 70HFB20AF001XB21 |  |  | 2# coal feeder remote control already |  |  |  | %Z013105 | DI |  | 70CRA08 | [5 empty] | TBF02 | 9 | 10 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB31 | 2#给煤机电机故障 | 2# coal feeder motor fault | 70CRA07 | FCS0703 | 1 | 3 | 6 | ADV151-P | SI | N | 70HFB20AF001XB31 |  | 70HFB20AF001XB31 |  |  | 2# coal feeder motor fault |  |  |  | %Z013106 | DI |  | 70CRA08 | [5 empty] | TBF02 | 11 | 12 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB32 | 2#给煤机清扫电机故障 | 2# coal feeder sweeper motor fault | 70CRA07 | FCS0703 | 1 | 3 | 7 | ADV151-P | SI | N | 70HFB20AF001XB32 |  | 70HFB20AF001XB32 |  |  | 2# coal feeder sweeper motor fault |  |  |  | %Z013107 | DI |  | 70CRA08 | [5 empty] | TBF02 | 13 | 14 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB33 | 2#给煤机跑偏报警 | 2# coal feeder offset alarm | 70CRA07 | FCS0703 | 1 | 3 | 8 | ADV151-P | SI | N | 70HFB20AF001XB33 |  | 70HFB20AF001XB33 |  |  | 2# coal feeder offset alarm |  |  |  | %Z013108 | DI |  | 70CRA08 | [5 empty] | TBF02 | 15 | 16 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB34 | 2#给煤机出口堵料故障 | 2# coal feeder exit blockage fault | 70CRA07 | FCS0703 | 1 | 3 | 9 | ADV151-P | SI | N | 70HFB20AF001XB34 |  | 70HFB20AF001XB34 |  |  | 2# coal feeder exit blockage fault |  |  |  | %Z013109 | DI |  | 70CRA08 | [5 empty] | TBF02 | 17 | 18 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB35 | 2#给煤机断料故障 | 2# coal feeder material-shortage | 70CRA07 | FCS0703 | 1 | 3 | 10 | ADV151-P | SI | N | 70HFB20AF001XB35 |  | 70HFB20AF001XB35 |  |  | 2# coal feeder material-shortage |  |  |  | %Z013110 | DI |  | 70CRA08 | [5 empty] | TBF02 | 19 | 20 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB36 | 2#给煤机给料偏差报警 | 2# coal feeder feed rate error | 70CRA07 | FCS0703 | 1 | 3 | 11 | ADV151-P | SI | N | 70HFB20AF001XB36 |  | 70HFB20AF001XB36 |  |  | 2# coal feeder feed rate error |  |  |  | %Z013111 | DI |  | 70CRA08 | [5 empty] | TBF02 | 21 | 22 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB37 | 2#给煤机超温故障 | 2# coal feeder over-temperature fault | 70CRA07 | FCS0703 | 1 | 3 | 12 | ADV151-P | SI | N | 70HFB20AF001XB37 |  | 70HFB20AF001XB37 |  |  | 2# coal feeder over-temperature fault |  |  |  | %Z013112 | DI |  | 70CRA08 | [5 empty] | TBF02 | 23 | 24 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001XB38 | 2#给煤机进口煤流报警 | 2# coal feeder coal flow monitor alarm | 70CRA07 | FCS0703 | 1 | 3 | 13 | ADV151-P | SI | N | 70HFB20AF001XB38 |  | 70HFB20AF001XB38 |  |  | 2# coal feeder coal flow monitor alarm |  |  |  | %Z013113 | DI |  | 70CRA08 | [5 empty] | TBF02 | 25 | 26 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA001XB01 | 2#给煤机进口电动闸阀全开状态 | 2# coal feeder inlet MOV full opened status | 70CRA07 | FCS0703 | 1 | 3 | 14 | ADV151-P | SI | N | 70HFB20AA001XB01 |  | 70HFB20AA001XB01 |  |  | 2# coal feeder inlet MOV full opened status |  |  |  | %Z013114 | DI |  | 70CRA08 | [5 empty] | TBF02 | 27 | 28 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA001XB11 | 2#给煤机进口电动闸阀全关状态 | 2# coal feeder inlet MOV full closed status | 70CRA07 | FCS0703 | 1 | 3 | 15 | ADV151-P | SI | N | 70HFB20AA001XB11 |  | 70HFB20AA001XB11 |  |  | 2# coal feeder inlet MOV full closed status |  |  |  | %Z013115 | DI |  | 70CRA08 | [5 empty] | TBF02 | 29 | 30 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA001XB21 | 2#给煤机进口电动闸阀远控允许 | 2# coal feeder inlet MOV remote control permitted | 70CRA07 | FCS0703 | 1 | 3 | 16 | ADV151-P | SI | N | 70HFB20AA001XB21 |  | 70HFB20AA001XB21 |  |  | 2# coal feeder inlet MOV remote control permitted |  |  |  | %Z013116 | DI |  | 70CRA08 | [5 empty] | TBF02 | 31 | 32 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA001XB31 | 2#给煤机进口电动闸阀故障 | 2# coal feeder inlet MOV fault | 70CRA07 | FCS0703 | 1 | 3 | 17 | ADV151-P | SI | N | 70HFB20AA001XB31 |  | 70HFB20AA001XB31 |  |  | 2# coal feeder inlet MOV fault |  |  |  | %Z013117 | DI |  | 70CRA08 | [5 empty] | TBF02 | 33 | 34 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA002XB01 | 2#给煤机出口气动阀全开状态 | 2# coal feeder outlet PV full opened status | 70CRA07 | FCS0703 | 1 | 3 | 18 | ADV151-P | SI | N | 70HFB20AA002XB01 |  | 70HFB20AA002XB01 |  |  | 2# coal feeder outlet PV full opened status |  |  |  | %Z013118 | DI |  | 70CRA08 | [5 empty] | TBF02 | 35 | 36 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA002XB11 | 2#给煤机出口气动阀全关状态 | 2# coal feeder outlet PV full closed status | 70CRA07 | FCS0703 | 1 | 3 | 19 | ADV151-P | SI | N | 70HFB20AA002XB11 |  | 70HFB20AA002XB11 |  |  | 2# coal feeder outlet PV full closed status |  |  |  | %Z013119 | DI |  | 70CRA08 | [5 empty] | TBF02 | 37 | 38 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA002XB21 | 2#给煤机出口气动阀远控允许 | 2# coal feeder outlet PV remote control permitted | 70CRA07 | FCS0703 | 1 | 3 | 20 | ADV151-P | SI | N | 70HFB20AA002XB21 |  | 70HFB20AA002XB21 |  |  | 2# coal feeder outlet PV remote control permitted |  |  |  | %Z013120 | DI |  | 70CRA08 | [5 empty] | TBF02 | 39 | 40 |  |  | 70HFB20GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB60AF001XB31 | 污泥给料机电机故障 | Sludge feeder motor fault | 70CRA07 | FCS0703 | 1 | 3 | 21 | ADV151-P | SI | N | 70HFB60AF001XB31 |  | 70HFB60AF001XB31 |  |  | Sludge feeder motor fault |  |  |  | %Z013121 | DI |  | 70CRA08 | [5 empty] | TBF02 | 41 | 42 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
|  | 70HFB60AF001XB32 | 污泥给料机清扫电机故障 | Sludge feeder sweeper motor fault | 70CRA07 | FCS0703 | 1 | 3 | 22 | ADV151-P | SI | N | 70HFB60AF001XB32 |  | 70HFB60AF001XB32 |  |  | Sludge feeder sweeper motor fault |  |  |  | %Z013122 | DI |  | 70CRA08 | [5 empty] | TBF02 | 43 | 44 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
|  | 70HFB60AF001XB33 | 污泥给料机跑偏报警 | Sludge feeder offset alarm | 70CRA07 | FCS0703 | 1 | 3 | 23 | ADV151-P | SI | N | 70HFB60AF001XB33 |  | 70HFB60AF001XB33 |  |  | Sludge feeder offset alarm |  |  |  | %Z013123 | DI |  | 70CRA08 | [5 empty] | TBF02 | 45 | 46 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
|  | 70HFB60AF001XB34 | 污泥给料机出口堵料故障 | Sludge feeder exit blockage fault | 70CRA07 | FCS0703 | 1 | 3 | 24 | ADV151-P | SI | N | 70HFB60AF001XB34 |  | 70HFB60AF001XB34 |  |  | Sludge feeder exit blockage fault |  |  |  | %Z013124 | DI |  | 70CRA08 | [5 empty] | TBF02 | 47 | 48 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
|  | 70HFB60AF001XB35 | 污泥给料机断料故障 | Sludge feeder material-shortage | 70CRA07 | FCS0703 | 1 | 3 | 25 | ADV151-P | SI | N | 70HFB60AF001XB35 |  | 70HFB60AF001XB35 |  |  | Sludge feeder material-shortage |  |  |  | %Z013125 | DI |  | 70CRA08 | [5 empty] | TBF02 | 49 | 50 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
|  | 70HFB60AF001XB36 | 污泥给料机给料偏差报警 | Sludge feeder feed rate error | 70CRA07 | FCS0703 | 1 | 3 | 26 | ADV151-P | SI | N | 70HFB60AF001XB36 |  | 70HFB60AF001XB36 |  |  | Sludge feeder feed rate error |  |  |  | %Z013126 | DI |  | 70CRA08 | [5 empty] | TBF02 | 51 | 52 |  |  | 70HFB60GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
[5 empty] | 70CRA07 | FCS0703 | 1 | 3 | 27 | ADV151-P | SI | N | [9 empty] | %Z013127 | DI |  | 70CRA08 | [5 empty] | TBF02 | 53 | 54
[5 empty] | 70CRA07 | FCS0703 | 1 | 3 | 28 | ADV151-P | SI | N | [9 empty] | %Z013128 | DI |  | 70CRA08 | [5 empty] | TBF02 | 55 | 56
[5 empty] | 70CRA07 | FCS0703 | 1 | 3 | 29 | ADV151-P | SI | N | [9 empty] | %Z013129 | DI |  | 70CRA08 | [5 empty] | TBF02 | 57 | 58
[5 empty] | 70CRA07 | FCS0703 | 1 | 3 | 30 | ADV151-P | SI | N | [9 empty] | %Z013130 | DI |  | 70CRA08 | [5 empty] | TBF02 | 59 | 60
[5 empty] | 70CRA07 | FCS0703 | 1 | 3 | 31 | ADV151-P | SI | N | [9 empty] | %Z013131 | DI |  | 70CRA08 | [5 empty] | TBF02 | 61 | 62
[5 empty] | 70CRA07 | FCS0703 | 1 | 3 | 32 | ADV151-P | SI | N | [9 empty] | %Z013132 | DI |  | 70CRA08 | [5 empty] | TBF02 | 63 | 64
|  | 70HFB30AF001XB01 | 3#给煤机运行 | 3# coal feeder running | 70CRA07 | FCS0703 | 2 | 2 | 1 | ADV151-P | SI | N | 70HFB30AF001XB01 |  | 70HFB30AF001XB01 |  |  | 3# coal feeder running |  |  |  | %Z022101 | DI |  | 70CRA08 | [5 empty] | TBF03 | 1 | 2 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB02 | 3#给煤机清扫运行 | 3# coal feeder sweeper running | 70CRA07 | FCS0703 | 2 | 2 | 2 | ADV151-P | SI | N | 70HFB30AF001XB02 |  | 70HFB30AF001XB02 |  |  | 3# coal feeder sweeper running |  |  |  | %Z022102 | DI |  | 70CRA08 | [5 empty] | TBF03 | 3 | 4 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB03 | 3#给煤机容积输出显示 | 3# coal feeder volume output display | 70CRA07 | FCS0703 | 2 | 2 | 3 | ADV151-P | SI | N | 70HFB30AF001XB03 |  | 70HFB30AF001XB03 |  |  | 3# coal feeder volume output display |  |  |  | %Z022103 | DI |  | 70CRA08 | [5 empty] | TBF03 | 5 | 6 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB11 | 3#给煤机停止信号 | 3# coal feeder stopped signal | 70CRA07 | FCS0703 | 2 | 2 | 4 | ADV151-P | SI | N | 70HFB30AF001XB11 |  | 70HFB30AF001XB11 |  |  | 3# coal feeder stopped signal |  |  |  | %Z022104 | DI |  | 70CRA08 | [5 empty] | TBF03 | 7 | 8 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB21 | 3#给煤机远控备妥 | 3# coal feeder remote control already | 70CRA07 | FCS0703 | 2 | 2 | 5 | ADV151-P | SI | N | 70HFB30AF001XB21 |  | 70HFB30AF001XB21 |  |  | 3# coal feeder remote control already |  |  |  | %Z022105 | DI |  | 70CRA08 | [5 empty] | TBF03 | 9 | 10 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB31 | 3#给煤机电机故障 | 3# coal feeder motor fault | 70CRA07 | FCS0703 | 2 | 2 | 6 | ADV151-P | SI | N | 70HFB30AF001XB31 |  | 70HFB30AF001XB31 |  |  | 3# coal feeder motor fault |  |  |  | %Z022106 | DI |  | 70CRA08 | [5 empty] | TBF03 | 11 | 12 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB32 | 3#给煤机清扫电机故障 | 3# coal feeder sweeper motor fault | 70CRA07 | FCS0703 | 2 | 2 | 7 | ADV151-P | SI | N | 70HFB30AF001XB32 |  | 70HFB30AF001XB32 |  |  | 3# coal feeder sweeper motor fault |  |  |  | %Z022107 | DI |  | 70CRA08 | [5 empty] | TBF03 | 13 | 14 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB33 | 3#给煤机跑偏报警 | 3# coal feeder offset alarm | 70CRA07 | FCS0703 | 2 | 2 | 8 | ADV151-P | SI | N | 70HFB30AF001XB33 |  | 70HFB30AF001XB33 |  |  | 3# coal feeder offset alarm |  |  |  | %Z022108 | DI |  | 70CRA08 | [5 empty] | TBF03 | 15 | 16 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB34 | 3#给煤机出口堵料故障 | 3# coal feeder exit blockage fault | 70CRA07 | FCS0703 | 2 | 2 | 9 | ADV151-P | SI | N | 70HFB30AF001XB34 |  | 70HFB30AF001XB34 |  |  | 3# coal feeder exit blockage fault |  |  |  | %Z022109 | DI |  | 70CRA08 | [5 empty] | TBF03 | 17 | 18 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB35 | 3#给煤机断料故障 | 3# coal feeder material-shortage | 70CRA07 | FCS0703 | 2 | 2 | 10 | ADV151-P | SI | N | 70HFB30AF001XB35 |  | 70HFB30AF001XB35 |  |  | 3# coal feeder material-shortage |  |  |  | %Z022110 | DI |  | 70CRA08 | [5 empty] | TBF03 | 19 | 20 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB36 | 3#给煤机给料偏差报警 | 3# coal feeder feed rate error | 70CRA07 | FCS0703 | 2 | 2 | 11 | ADV151-P | SI | N | 70HFB30AF001XB36 |  | 70HFB30AF001XB36 |  |  | 3# coal feeder feed rate error |  |  |  | %Z022111 | DI |  | 70CRA08 | [5 empty] | TBF03 | 21 | 22 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB37 | 3#给煤机超温故障 | 3# coal feeder over-temperature fault | 70CRA07 | FCS0703 | 2 | 2 | 12 | ADV151-P | SI | N | 70HFB30AF001XB37 |  | 70HFB30AF001XB37 |  |  | 3# coal feeder over-temperature fault |  |  |  | %Z022112 | DI |  | 70CRA08 | [5 empty] | TBF03 | 23 | 24 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001XB38 | 3#给煤机进口煤流报警 | 3# coal feeder coal flow monitor alarm | 70CRA07 | FCS0703 | 2 | 2 | 13 | ADV151-P | SI | N | 70HFB30AF001XB38 |  | 70HFB30AF001XB38 |  |  | 3# coal feeder coal flow monitor alarm |  |  |  | %Z022113 | DI |  | 70CRA08 | [5 empty] | TBF03 | 25 | 26 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA001XB01 | 3#给煤机进口电动闸阀全开状态 | 3# coal feeder inlet MOV full opened status | 70CRA07 | FCS0703 | 2 | 2 | 14 | ADV151-P | SI | N | 70HFB30AA001XB01 |  | 70HFB30AA001XB01 |  |  | 3# coal feeder inlet MOV full opened status |  |  |  | %Z022114 | DI |  | 70CRA08 | [5 empty] | TBF03 | 27 | 28 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA001XB11 | 3#给煤机进口电动闸阀全关状态 | 3# coal feeder inlet MOV full closed status | 70CRA07 | FCS0703 | 2 | 2 | 15 | ADV151-P | SI | N | 70HFB30AA001XB11 |  | 70HFB30AA001XB11 |  |  | 3# coal feeder inlet MOV full closed status |  |  |  | %Z022115 | DI |  | 70CRA08 | [5 empty] | TBF03 | 29 | 30 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA001XB21 | 3#给煤机进口电动闸阀远控允许 | 3# coal feeder inlet MOV remote control permitted | 70CRA07 | FCS0703 | 2 | 2 | 16 | ADV151-P | SI | N | 70HFB30AA001XB21 |  | 70HFB30AA001XB21 |  |  | 3# coal feeder inlet MOV remote control permitted |  |  |  | %Z022116 | DI |  | 70CRA08 | [5 empty] | TBF03 | 31 | 32 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA001XB31 | 3#给煤机进口电动闸阀故障 | 3# coal feeder inlet MOV fault | 70CRA07 | FCS0703 | 2 | 2 | 17 | ADV151-P | SI | N | 70HFB30AA001XB31 |  | 70HFB30AA001XB31 |  |  | 3# coal feeder inlet MOV fault |  |  |  | %Z022117 | DI |  | 70CRA08 | [5 empty] | TBF03 | 33 | 34 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA002XB01 | 3#给煤机出口气动阀全开状态 | 3# coal feeder outlet PV full opened status | 70CRA07 | FCS0703 | 2 | 2 | 18 | ADV151-P | SI | N | 70HFB30AA002XB01 |  | 70HFB30AA002XB01 |  |  | 3# coal feeder outlet PV full opened status |  |  |  | %Z022118 | DI |  | 70CRA08 | [5 empty] | TBF03 | 35 | 36 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA002XB11 | 3#给煤机出口气动阀全关状态 | 3# coal feeder outlet PV full closed status | 70CRA07 | FCS0703 | 2 | 2 | 19 | ADV151-P | SI | N | 70HFB30AA002XB11 |  | 70HFB30AA002XB11 |  |  | 3# coal feeder outlet PV full closed status |  |  |  | %Z022119 | DI |  | 70CRA08 | [5 empty] | TBF03 | 37 | 38 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA002XB21 | 3#给煤机出口气动阀远控允许 | 3# coal feeder outlet PV remote control permitted | 70CRA07 | FCS0703 | 2 | 2 | 20 | ADV151-P | SI | N | 70HFB30AA002XB21 |  | 70HFB30AA002XB21 |  |  | 3# coal feeder outlet PV remote control permitted |  |  |  | %Z022120 | DI |  | 70CRA08 | [5 empty] | TBF03 | 39 | 40 |  |  | 70HFB30GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB60AA001XB01 | 污泥给料机入口电动插板阀全开状态 | Sludge feeder inlet MOV full opened status | 70CRA07 | FCS0703 | 2 | 2 | 21 | ADV151-P | SI | N | 70HFB60AA001XB01 |  | 70HFB60AA001XB01 |  |  | Sludge feeder inlet MOV full opened status |  |  |  | %Z022121 | DI |  | 70CRA08 | [5 empty] | TBF03 | 41 | 42 |  |  | 70HFB60AA001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013
|  | 70HFB60AA001XB11 | 污泥给料机入口电动插板阀全关 | Sludge feeder inlet MOV full closed status | 70CRA07 | FCS0703 | 2 | 2 | 22 | ADV151-P | SI | N | 70HFB60AA001XB11 |  | 70HFB60AA001XB11 |  |  | Sludge feeder inlet MOV full closed status |  |  |  | %Z022122 | DI |  | 70CRA08 | [5 empty] | TBF03 | 43 | 44 |  |  | 70HFB60AA001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013
|  | 70HFB60AA001XB21 | 污泥给料机入口电动插板阀远控允许 | Sludge feeder inlet MOV remote control permitted | 70CRA07 | FCS0703 | 2 | 2 | 23 | ADV151-P | SI | N | 70HFB60AA001XB21 |  | 70HFB60AA001XB21 |  |  | Sludge feeder inlet MOV remote control permitted |  |  |  | %Z022123 | DI |  | 70CRA08 | [5 empty] | TBF03 | 45 | 46 |  |  | 70HFB60AA001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013
|  | 70HFB60AA001XB31 | 污泥给料机入口电动插板阀故障 | Sludge feeder inlet MOV fault | 70CRA07 | FCS0703 | 2 | 2 | 24 | ADV151-P | SI | N | 70HFB60AA001XB31 |  | 70HFB60AA001XB31 |  |  | Sludge feeder inlet MOV fault |  |  |  | %Z022124 | DI |  | 70CRA08 | [5 empty] | TBF03 | 47 | 48 |  |  | 70HFB60AA001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013
|  | 70HHL40CP002LL | 高压流化风机出口母管压力低低1 | High pressure fludized fan outlet main pipe pressure LL1 | 70CRA07 | FCS0703 | 2 | 2 | 25 | ADV151-P | SI | N | 70HHL40CP002LL |  | 70HHL40CP002LL |  |  | High pressure fludized fan outlet main pipe pressure LL1 | 20 |  | kPa | %Z022125 | DI |  | 70CRA08 | [5 empty] | TBF03 | 49 | 50 |  |  | 70HHL40CP002 | NO | DI |  |  |  |  | √ |  |  |  | FSSS | D |  | K0202-012
|  | 70HHL40CP003LL | 高压流化风机出口母管压力低低2 | High pressure fludized fan outlet main pipe pressure LL2 | 70CRA07 | FCS0703 | 2 | 2 | 26 | ADV151-P | SI | N | 70HHL40CP003LL |  | 70HHL40CP003LL |  |  | High pressure fludized fan outlet main pipe pressure LL2 | 20 |  | kPa | %Z022126 | DI |  | 70CRA08 | [5 empty] | TBF03 | 51 | 52 |  |  | 70HHL40CP003 | NO | DI |  |  |  |  | √ |  |  |  | FSSS | D |  | K0202-012
|  | 70HHL40CP004LL | 高压流化风机出口母管压力低低3 | High pressure fludized fan outlet main pipe pressure LL3 | 70CRA07 | FCS0703 | 2 | 2 | 27 | ADV151-P | SI | N | 70HHL40CP004LL |  | 70HHL40CP004LL |  |  | High pressure fludized fan outlet main pipe pressure LL3 | 20 |  | kPa | %Z022127 | DI |  | 70CRA08 | [5 empty] | TBF03 | 53 | 54 |  |  | 70HHL40CP004 | NO | DI |  |  |  |  | √ |  |  |  | FSSS | D |  | K0202-012
[5 empty] | 70CRA07 | FCS0703 | 2 | 2 | 28 | ADV151-P | SI | N | [9 empty] | %Z022128 | DI |  | 70CRA08 | [5 empty] | TBF03 | 55 | 56
[5 empty] | 70CRA07 | FCS0703 | 2 | 2 | 29 | ADV151-P | SI | N | [9 empty] | %Z022129 | DI |  | 70CRA08 | [5 empty] | TBF03 | 57 | 58
[5 empty] | 70CRA07 | FCS0703 | 2 | 2 | 30 | ADV151-P | SI | N | [9 empty] | %Z022130 | DI |  | 70CRA08 | [5 empty] | TBF03 | 59 | 60
[5 empty] | 70CRA07 | FCS0703 | 2 | 2 | 31 | ADV151-P | SI | N | [9 empty] | %Z022131 | DI |  | 70CRA08 | [5 empty] | TBF03 | 61 | 62
[5 empty] | 70CRA07 | FCS0703 | 2 | 2 | 32 | ADV151-P | SI | N | [9 empty] | %Z022132 | DI |  | 70CRA08 | [5 empty] | TBF03 | 63 | 64
|  | 70HFB40AF001XB01 | 4#给煤机运行 | 4# coal feeder running | 70CRA07 | FCS0703 | 2 | 3 | 1 | ADV151-P | SI | N | 70HFB40AF001XB01 |  | 70HFB40AF001XB01 |  |  | 4# coal feeder running |  |  |  | %Z023101 | DI |  | 70CRA08 | [5 empty] | TBF04 | 1 | 2 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB02 | 4#给煤机清扫运行 | 4# coal feeder sweeper running | 70CRA07 | FCS0703 | 2 | 3 | 2 | ADV151-P | SI | N | 70HFB40AF001XB02 |  | 70HFB40AF001XB02 |  |  | 4# coal feeder sweeper running |  |  |  | %Z023102 | DI |  | 70CRA08 | [5 empty] | TBF04 | 3 | 4 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB03 | 4#给煤机容积输出显示 | 4# coal feeder volume output display | 70CRA07 | FCS0703 | 2 | 3 | 3 | ADV151-P | SI | N | 70HFB40AF001XB03 |  | 70HFB40AF001XB03 |  |  | 4# coal feeder volume output display |  |  |  | %Z023103 | DI |  | 70CRA08 | [5 empty] | TBF04 | 5 | 6 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB11 | 4#给煤机停止信号 | 4# coal feeder stopped signal | 70CRA07 | FCS0703 | 2 | 3 | 4 | ADV151-P | SI | N | 70HFB40AF001XB11 |  | 70HFB40AF001XB11 |  |  | 4# coal feeder stopped signal |  |  |  | %Z023104 | DI |  | 70CRA08 | [5 empty] | TBF04 | 7 | 8 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB21 | 4#给煤机远控备妥 | 4# coal feeder remote control already | 70CRA07 | FCS0703 | 2 | 3 | 5 | ADV151-P | SI | N | 70HFB40AF001XB21 |  | 70HFB40AF001XB21 |  |  | 4# coal feeder remote control already |  |  |  | %Z023105 | DI |  | 70CRA08 | [5 empty] | TBF04 | 9 | 10 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB31 | 4#给煤机电机故障 | 4# coal feeder motor fault | 70CRA07 | FCS0703 | 2 | 3 | 6 | ADV151-P | SI | N | 70HFB40AF001XB31 |  | 70HFB40AF001XB31 |  |  | 4# coal feeder motor fault |  |  |  | %Z023106 | DI |  | 70CRA08 | [5 empty] | TBF04 | 11 | 12 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB32 | 4#给煤机清扫电机故障 | 4# coal feeder sweeper motor fault | 70CRA07 | FCS0703 | 2 | 3 | 7 | ADV151-P | SI | N | 70HFB40AF001XB32 |  | 70HFB40AF001XB32 |  |  | 4# coal feeder sweeper motor fault |  |  |  | %Z023107 | DI |  | 70CRA08 | [5 empty] | TBF04 | 13 | 14 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB33 | 4#给煤机跑偏报警 | 4# coal feeder offset alarm | 70CRA07 | FCS0703 | 2 | 3 | 8 | ADV151-P | SI | N | 70HFB40AF001XB33 |  | 70HFB40AF001XB33 |  |  | 4# coal feeder offset alarm |  |  |  | %Z023108 | DI |  | 70CRA08 | [5 empty] | TBF04 | 15 | 16 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB34 | 4#给煤机出口堵料故障 | 4# coal feeder exit blockage fault | 70CRA07 | FCS0703 | 2 | 3 | 9 | ADV151-P | SI | N | 70HFB40AF001XB34 |  | 70HFB40AF001XB34 |  |  | 4# coal feeder exit blockage fault |  |  |  | %Z023109 | DI |  | 70CRA08 | [5 empty] | TBF04 | 17 | 18 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB35 | 4#给煤机断料故障 | 4# coal feeder material-shortage | 70CRA07 | FCS0703 | 2 | 3 | 10 | ADV151-P | SI | N | 70HFB40AF001XB35 |  | 70HFB40AF001XB35 |  |  | 4# coal feeder material-shortage |  |  |  | %Z023110 | DI |  | 70CRA08 | [5 empty] | TBF04 | 19 | 20 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB36 | 4#给煤机给料偏差报警 | 4# coal feeder feed rate error | 70CRA07 | FCS0703 | 2 | 3 | 11 | ADV151-P | SI | N | 70HFB40AF001XB36 |  | 70HFB40AF001XB36 |  |  | 4# coal feeder feed rate error |  |  |  | %Z023111 | DI |  | 70CRA08 | [5 empty] | TBF04 | 21 | 22 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB37 | 4#给煤机超温故障 | 4# coal feeder over-temperature fault | 70CRA07 | FCS0703 | 2 | 3 | 12 | ADV151-P | SI | N | 70HFB40AF001XB37 |  | 70HFB40AF001XB37 |  |  | 4# coal feeder over-temperature fault |  |  |  | %Z023112 | DI |  | 70CRA08 | [5 empty] | TBF04 | 23 | 24 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001XB38 | 4#给煤机进口煤流报警 | 4# coal feeder coal flow monitor alarm | 70CRA07 | FCS0703 | 2 | 3 | 13 | ADV151-P | SI | N | 70HFB40AF001XB38 |  | 70HFB40AF001XB38 |  |  | 4# coal feeder coal flow monitor alarm |  |  |  | %Z023113 | DI |  | 70CRA08 | [5 empty] | TBF04 | 25 | 26 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA001XB01 | 4#给煤机进口电动闸阀全开状态 | 4# coal feeder inlet MOV full opened status | 70CRA07 | FCS0703 | 2 | 3 | 14 | ADV151-P | SI | N | 70HFB40AA001XB01 |  | 70HFB40AA001XB01 |  |  | 4# coal feeder inlet MOV full opened status |  |  |  | %Z023114 | DI |  | 70CRA08 | [5 empty] | TBF04 | 27 | 28 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA001XB11 | 4#给煤机进口电动闸阀全关状态 | 4# coal feeder inlet MOV full closed status | 70CRA07 | FCS0703 | 2 | 3 | 15 | ADV151-P | SI | N | 70HFB40AA001XB11 |  | 70HFB40AA001XB11 |  |  | 4# coal feeder inlet MOV full closed status |  |  |  | %Z023115 | DI |  | 70CRA08 | [5 empty] | TBF04 | 29 | 30 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA001XB21 | 4#给煤机进口电动闸阀远控允许 | 4# coal feeder inlet MOV remote control permitted | 70CRA07 | FCS0703 | 2 | 3 | 16 | ADV151-P | SI | N | 70HFB40AA001XB21 |  | 70HFB40AA001XB21 |  |  | 4# coal feeder inlet MOV remote control permitted |  |  |  | %Z023116 | DI |  | 70CRA08 | [5 empty] | TBF04 | 31 | 32 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA001XB31 | 4#给煤机进口电动闸阀故障 | 4# coal feeder inlet MOV fault | 70CRA07 | FCS0703 | 2 | 3 | 17 | ADV151-P | SI | N | 70HFB40AA001XB31 |  | 70HFB40AA001XB31 |  |  | 4# coal feeder inlet MOV fault |  |  |  | %Z023117 | DI |  | 70CRA08 | [5 empty] | TBF04 | 33 | 34 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA002XB01 | 4#给煤机出口气动阀全开状态 | 4# coal feeder outlet PV full opened status | 70CRA07 | FCS0703 | 2 | 3 | 18 | ADV151-P | SI | N | 70HFB40AA002XB01 |  | 70HFB40AA002XB01 |  |  | 4# coal feeder outlet PV full opened status |  |  |  | %Z023118 | DI |  | 70CRA08 | [5 empty] | TBF04 | 35 | 36 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA002XB11 | 4#给煤机出口气动阀全关状态 | 4# coal feeder outlet PV full closed status | 70CRA07 | FCS0703 | 2 | 3 | 19 | ADV151-P | SI | N | 70HFB40AA002XB11 |  | 70HFB40AA002XB11 |  |  | 4# coal feeder outlet PV full closed status |  |  |  | %Z023119 | DI |  | 70CRA08 | [5 empty] | TBF04 | 37 | 38 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA002XB21 | 4#给煤机出口气动阀远控允许 | 4# coal feeder outlet PV remote control permitted | 70CRA07 | FCS0703 | 2 | 3 | 20 | ADV151-P | SI | N | 70HFB40AA002XB21 |  | 70HFB40AA002XB21 |  |  | 4# coal feeder outlet PV remote control permitted |  |  |  | %Z023120 | DI |  | 70CRA08 | [5 empty] | TBF04 | 39 | 40 |  |  | 70HFB40GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HBB10CP001AHH | 锅炉炉膛出口压力高高1 | Boiler furnace outlet pressure HH 1 | 70CRA07 | FCS0703 | 2 | 3 | 21 | ADV151-P | SI | N | 70HBB10CP001AHH |  | 70HBB10CP001AHH |  |  | Boiler furnace outlet pressure HH 1 | 2.5 |  | Kpa | %Z023121 | DI |  | 70CRA08 | [5 empty] | TBF04 | 41 | 42 |  |  | 70HBB10CP001A | NO | DI |  | √ | [6 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CP001BHH | 锅炉炉膛出口压力高高2 | Boiler furnace outlet pressure HH 2 | 70CRA07 | FCS0703 | 2 | 3 | 22 | ADV151-P | SI | N | 70HBB10CP001BHH |  | 70HBB10CP001BHH |  |  | Boiler furnace outlet pressure HH 2 | 2.5 |  | Kpa | %Z023122 | DI |  | 70CRA08 | [5 empty] | TBF04 | 43 | 44 |  |  | 70HBB10CP001B | NO | DI |  | √ | [6 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CP001CHH | 锅炉炉膛出口压力高高3 | Boiler furnace outlet pressure HH 3 | 70CRA07 | FCS0703 | 2 | 3 | 23 | ADV151-P | SI | N | 70HBB10CP001CHH |  | 70HBB10CP001CHH |  |  | Boiler furnace outlet pressure HH 3 | 2.5 |  | Kpa | %Z023123 | DI |  | 70CRA08 | [5 empty] | TBF04 | 45 | 46 |  |  | 70HBB10CP001C | NO | DI |  | √ | [6 empty] | FSSS | D |  | K0202-005
|  | 70HBB10CP002ALL | 锅炉炉膛出口压力低低1 | Boiler furnace outlet pressure LL 1 | 70CRA07 | FCS0703 | 2 | 3 | 24 | ADV151-P | SI | N | 70HBB10CP002ALL |  | 70HBB10CP002ALL |  |  | Boiler furnace outlet pressure LL 1 | -2.5 |  | Kpa | %Z023124 | DI |  | 70CRA08 | [5 empty] | TBF04 | 47 | 48 |  |  | 70HBB10CP002A | NO | DI |  |  |  |  | √ |  |  |  | FSSS | D |  | K0202-005
|  | 70HBB10CP002BLL | 锅炉炉膛出口压力低低2 | Boiler furnace outlet pressure LL 2 | 70CRA07 | FCS0703 | 2 | 3 | 25 | ADV151-P | SI | N | 70HBB10CP002BLL |  | 70HBB10CP002BLL |  |  | Boiler furnace outlet pressure LL 2 | -2.5 |  | Kpa | %Z023125 | DI |  | 70CRA08 | [5 empty] | TBF04 | 49 | 50 |  |  | 70HBB10CP002 | NO | DI |  |  |  |  | √ |  |  |  | FSSS | D |  | K0202-005
|  | 70HBB10CP002CLL | 锅炉炉膛出口压力低低3 | Boiler furnace outlet pressure LL 3 | 70CRA07 | FCS0703 | 2 | 3 | 26 | ADV151-P | SI | N | 70HBB10CP002CLL |  | 70HBB10CP002CLL |  |  | Boiler furnace outlet pressure LL 3 | -2.5 |  | Kpa | %Z023126 | DI |  | 70CRA08 | [5 empty] | TBF04 | 51 | 52 |  |  | 70HBB10CP002C | NO | DI |  |  |  |  | √ |  |  |  | FSSS | D |  | K0202-005
[5 empty] | 70CRA07 | FCS0703 | 2 | 3 | 27 | ADV151-P | SI | N | [9 empty] | %Z023127 | DI |  | 70CRA08 | [5 empty] | TBF04 | 53 | 54
[5 empty] | 70CRA07 | FCS0703 | 2 | 3 | 28 | ADV151-P | SI | N | [9 empty] | %Z023128 | DI |  | 70CRA08 | [5 empty] | TBF04 | 55 | 56
[5 empty] | 70CRA07 | FCS0703 | 2 | 3 | 29 | ADV151-P | SI | N | [9 empty] | %Z023129 | DI |  | 70CRA08 | [5 empty] | TBF04 | 57 | 58
[5 empty] | 70CRA07 | FCS0703 | 2 | 3 | 30 | ADV151-P | SI | N | [9 empty] | %Z023130 | DI |  | 70CRA08 | [5 empty] | TBF04 | 59 | 60
[5 empty] | 70CRA07 | FCS0703 | 2 | 3 | 31 | ADV151-P | SI | N | [9 empty] | %Z023131 | DI |  | 70CRA08 | [5 empty] | TBF04 | 61 | 62
[5 empty] | 70CRA07 | FCS0703 | 2 | 3 | 32 | ADV151-P | SI | N | [9 empty] | %Z023132 | DI |  | 70CRA08 | [5 empty] | TBF04 | 63 | 64
|  | 70HFB50AF001XB01 | 5#给煤机运行 | 5# coal feeder running | 70CRA07 | FCS0703 | 3 | 2 | 1 | ADV151-P | SI | N | 70HFB50AF001XB01 |  | 70HFB50AF001XB01 |  |  | 5# coal feeder running |  |  |  | %Z032101 | DI |  | 70CRA08 | [5 empty] | TBC02 | 1 | 2 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB02 | 5#给煤机清扫运行 | 5# coal feeder sweeper running | 70CRA07 | FCS0703 | 3 | 2 | 2 | ADV151-P | SI | N | 70HFB50AF001XB02 |  | 70HFB50AF001XB02 |  |  | 5# coal feeder sweeper running |  |  |  | %Z032102 | DI |  | 70CRA08 | [5 empty] | TBC02 | 3 | 4 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB03 | 5#给煤机容积输出显示 | 5# coal feeder volume output display | 70CRA07 | FCS0703 | 3 | 2 | 3 | ADV151-P | SI | N | 70HFB50AF001XB03 |  | 70HFB50AF001XB03 |  |  | 5# coal feeder volume output display |  |  |  | %Z032103 | DI |  | 70CRA08 | [5 empty] | TBC02 | 5 | 6 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB11 | 5#给煤机停止信号 | 5# coal feeder stopped signal | 70CRA07 | FCS0703 | 3 | 2 | 4 | ADV151-P | SI | N | 70HFB50AF001XB11 |  | 70HFB50AF001XB11 |  |  | 5# coal feeder stopped signal |  |  |  | %Z032104 | DI |  | 70CRA08 | [5 empty] | TBC02 | 7 | 8 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB21 | 5#给煤机远控备妥 | 5# coal feeder remote control already | 70CRA07 | FCS0703 | 3 | 2 | 5 | ADV151-P | SI | N | 70HFB50AF001XB21 |  | 70HFB50AF001XB21 |  |  | 5# coal feeder remote control already |  |  |  | %Z032105 | DI |  | 70CRA08 | [5 empty] | TBC02 | 9 | 10 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB31 | 5#给煤机电机故障 | 5# coal feeder motor fault | 70CRA07 | FCS0703 | 3 | 2 | 6 | ADV151-P | SI | N | 70HFB50AF001XB31 |  | 70HFB50AF001XB31 |  |  | 5# coal feeder motor fault |  |  |  | %Z032106 | DI |  | 70CRA08 | [5 empty] | TBC02 | 11 | 12 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB32 | 5#给煤机清扫电机故障 | 5# coal feeder sweeper motor fault | 70CRA07 | FCS0703 | 3 | 2 | 7 | ADV151-P | SI | N | 70HFB50AF001XB32 |  | 70HFB50AF001XB32 |  |  | 5# coal feeder sweeper motor fault |  |  |  | %Z032107 | DI |  | 70CRA08 | [5 empty] | TBC02 | 13 | 14 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB33 | 5#给煤机跑偏报警 | 5# coal feeder offset alarm | 70CRA07 | FCS0703 | 3 | 2 | 8 | ADV151-P | SI | N | 70HFB50AF001XB33 |  | 70HFB50AF001XB33 |  |  | 5# coal feeder offset alarm |  |  |  | %Z032108 | DI |  | 70CRA08 | [5 empty] | TBC02 | 15 | 16 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB34 | 5#给煤机出口堵料故障 | 5# coal feeder exit blockage fault | 70CRA07 | FCS0703 | 3 | 2 | 9 | ADV151-P | SI | N | 70HFB50AF001XB34 |  | 70HFB50AF001XB34 |  |  | 5# coal feeder exit blockage fault |  |  |  | %Z032109 | DI |  | 70CRA08 | [5 empty] | TBC02 | 17 | 18 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB35 | 5#给煤机断料故障 | 5# coal feeder material-shortage | 70CRA07 | FCS0703 | 3 | 2 | 10 | ADV151-P | SI | N | 70HFB50AF001XB35 |  | 70HFB50AF001XB35 |  |  | 5# coal feeder material-shortage |  |  |  | %Z032110 | DI |  | 70CRA08 | [5 empty] | TBC02 | 19 | 20 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB36 | 5#给煤机给料偏差报警 | 5# coal feeder feed rate error | 70CRA07 | FCS0703 | 3 | 2 | 11 | ADV151-P | SI | N | 70HFB50AF001XB36 |  | 70HFB50AF001XB36 |  |  | 5# coal feeder feed rate error |  |  |  | %Z032111 | DI |  | 70CRA08 | [5 empty] | TBC02 | 21 | 22 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB37 | 5#给煤机超温故障 | 5# coal feeder over-temperature fault | 70CRA07 | FCS0703 | 3 | 2 | 12 | ADV151-P | SI | N | 70HFB50AF001XB37 |  | 70HFB50AF001XB37 |  |  | 5# coal feeder over-temperature fault |  |  |  | %Z032112 | DI |  | 70CRA08 | [5 empty] | TBC02 | 23 | 24 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001XB38 | 5#给煤机进口煤流报警 | 5# coal feeder coal flow monitor alarm | 70CRA07 | FCS0703 | 3 | 2 | 13 | ADV151-P | SI | N | 70HFB50AF001XB38 |  | 70HFB50AF001XB38 |  |  | 5# coal feeder coal flow monitor alarm |  |  |  | %Z032113 | DI |  | 70CRA08 | [5 empty] | TBC02 | 25 | 26 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AA001XB01 | 5#给煤机进口电动闸阀全开状态 | 5# coal feeder inlet MOV full opened status | 70CRA07 | FCS0703 | 3 | 2 | 14 | ADV151-P | SI | N | 70HFB50AA001XB01 |  | 70HFB50AA001XB01 |  |  | 5# coal feeder inlet MOV full opened status |  |  |  | %Z032114 | DI |  | 70CRA08 | [5 empty] | TBC02 | 27 | 28 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AA001XB11 | 5#给煤机进口电动闸阀全关状态 | 5# coal feeder inlet MOV full closed status | 70CRA07 | FCS0703 | 3 | 2 | 15 | ADV151-P | SI | N | 70HFB50AA001XB11 |  | 70HFB50AA001XB11 |  |  | 5# coal feeder inlet MOV full closed status |  |  |  | %Z032115 | DI |  | 70CRA08 | [5 empty] | TBC02 | 29 | 30 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AA001XB21 | 5#给煤机进口电动闸阀远控允许 | 5# coal feeder inlet MOV remote control permitted | 70CRA07 | FCS0703 | 3 | 2 | 16 | ADV151-P | SI | N | 70HFB50AA001XB21 |  | 70HFB50AA001XB21 |  |  | 5# coal feeder inlet MOV remote control permitted |  |  |  | %Z032116 | DI |  | 70CRA08 | [5 empty] | TBC02 | 31 | 32 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AA001XB31 | 5#给煤机进口电动闸阀故障 | 5# coal feeder inlet MOV fault | 70CRA07 | FCS0703 | 3 | 2 | 17 | ADV151-P | SI | N | 70HFB50AA001XB31 |  | 70HFB50AA001XB31 |  |  | 5# coal feeder inlet MOV fault |  |  |  | %Z032117 | DI |  | 70CRA08 | [5 empty] | TBC02 | 33 | 34 |  |  | 70HFB50GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HJF10AA001XB12 | 燃油系统供油气动主油阀全关状态2 | Fuel oil system main oil supply PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 2 | 18 | ADV151-P | SI | N | 70HJF10AA001XB12 |  | 70HJF10AA001XB12 |  |  | Fuel oil system main oil supply PV full closed status 2 |  |  |  | %Z032118 | DI |  | 70CRA08 | [5 empty] | TBC02 | 35 | 36 |  |  | 70HJF10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
|  | 70HJF21AA001XB12 | 1#油点火燃烧器气动回油阀全关状态2 | 1# oil ignition burner oil return PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 2 | 19 | ADV151-P | SI | N | 70HJF21AA001XB12 |  | 70HJF21AA001XB12 |  |  | 1# oil ignition burner oil return PV full closed status 2 |  |  |  | %Z032119 | DI |  | 70CRA08 | [5 empty] | TBC02 | 37 | 38 |  |  | 70HJF10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
|  | 70HJF22AA001XB12 | 2#油点火燃烧器气动回油阀全关状态2 | 2# oil ignition burner oil return PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 2 | 20 | ADV151-P | SI | N | 70HJF22AA001XB12 |  | 70HJF22AA001XB12 |  |  | 2# oil ignition burner oil return PV full closed status 2 |  |  |  | %Z032120 | DI |  | 70CRA08 | [5 empty] | TBC02 | 39 | 40 |  |  | 70HJF10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
|  | 70HJF23AA001XB12 | 3#油点火燃烧器气动回油阀全关状态2 | 3# oil ignition burner oil return PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 2 | 21 | ADV151-P | SI | N | 70HJF23AA001XB12 |  | 70HJF23AA001XB12 |  |  | 3# oil ignition burner oil return PV full closed status 2 |  |  |  | %Z032121 | DI |  | 70CRA08 | [5 empty] | TBC02 | 41 | 42 |  |  | 70HJF10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
|  | 70HJF24AA001XB12 | 4#油点火燃烧器气动回油阀全关状态2 | 4# oil ignition burner oil return PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 2 | 22 | ADV151-P | SI | N | 70HJF24AA001XB12 |  | 70HJF24AA001XB12 |  |  | 4# oil ignition burner oil return PV full closed status 2 |  |  |  | %Z032122 | DI |  | 70CRA08 | [5 empty] | TBC02 | 43 | 44 |  |  | 70HJF10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
|  | 70HJF25AA001XB12 | 5#油点火燃烧器气动回油阀全关状态2 | 5# oil ignition burner oil return PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 2 | 23 | ADV151-P | SI | N | 70HJF25AA001XB12 |  | 70HJF25AA001XB12 |  |  | 5# oil ignition burner oil return PV full closed status 2 |  |  |  | %Z032123 | DI |  | 70CRA08 | [5 empty] | TBC02 | 45 | 46 |  |  | 70HJF10GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
[5 empty] | 70CRA07 | FCS0703 | 3 | 2 | 24 | ADV151-P | SI | N | [9 empty] | %Z032124 | DI |  | 70CRA08 | [5 empty] | TBC02 | 47 | 48
[5 empty] | 70CRA07 | FCS0703 | 3 | 2 | 25 | ADV151-P | SI | N | [9 empty] | %Z032125 | DI |  | 70CRA08 | [5 empty] | TBC02 | 49 | 50
[5 empty] | 70CRA07 | FCS0703 | 3 | 2 | 26 | ADV151-P | SI | N | [9 empty] | %Z032126 | DI |  | 70CRA08 | [5 empty] | TBC02 | 51 | 52
[5 empty] | 70CRA07 | FCS0703 | 3 | 2 | 27 | ADV151-P | SI | N | [9 empty] | %Z032127 | DI |  | 70CRA08 | [5 empty] | TBC02 | 53 | 54
[5 empty] | 70CRA07 | FCS0703 | 3 | 2 | 28 | ADV151-P | SI | N | [9 empty] | %Z032128 | DI |  | 70CRA08 | [5 empty] | TBC02 | 55 | 56
[5 empty] | 70CRA07 | FCS0703 | 3 | 2 | 29 | ADV151-P | SI | N | [9 empty] | %Z032129 | DI |  | 70CRA08 | [5 empty] | TBC02 | 57 | 58
[5 empty] | 70CRA07 | FCS0703 | 3 | 2 | 30 | ADV151-P | SI | N | [9 empty] | %Z032130 | DI |  | 70CRA08 | [5 empty] | TBC02 | 59 | 60
[5 empty] | 70CRA07 | FCS0703 | 3 | 2 | 31 | ADV151-P | SI | N | [9 empty] | %Z032131 | DI |  | 70CRA08 | [5 empty] | TBC02 | 61 | 62
[5 empty] | 70CRA07 | FCS0703 | 3 | 2 | 32 | ADV151-P | SI | N | [9 empty] | %Z032132 | DI |  | 70CRA08 | [5 empty] | TBC02 | 63 | 64
|  | 70HFB70AF001XB01 | 埋刮板输送机运行 | Embed belt coal conveyor running | 70CRA07 | FCS0703 | 3 | 3 | 1 | ADV151-P | SI | N | 70HFB70AF001XB01 |  | 70HFB70AF001XB01 |  |  | Embed belt coal conveyor running |  |  |  | %Z033101 | DI |  | 70CRA08 | [5 empty] | TBC03 | 1 | 2 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB70AF001XB21 | 埋刮板输送机远控备妥 | Embed belt coal conveyor remote control already | 70CRA07 | FCS0703 | 3 | 3 | 2 | ADV151-P | SI | N | 70HFB70AF001XB21 |  | 70HFB70AF001XB21 |  |  | Embed belt coal conveyor remote control already |  |  |  | %Z033102 | DI |  | 70CRA08 | [5 empty] | TBC03 | 3 | 4 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB70AF001XB31 | 埋刮板输送机故障 | Embed belt coal conveyor fault | 70CRA07 | FCS0703 | 3 | 3 | 3 | ADV151-P | SI | N | 70HFB70AF001XB31 |  | 70HFB70AF001XB31 |  |  | Embed belt coal conveyor fault |  |  |  | %Z033103 | DI |  | 70CRA08 | [5 empty] | TBC03 | 5 | 6 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB70AF001XB32 | 埋刮板输送机断料报警 | Embed belt coal conveyor material-shortage alarm | 70CRA07 | FCS0703 | 3 | 3 | 4 | ADV151-P | SI | N | 70HFB70AF001XB32 |  | 70HFB70AF001XB32 |  |  | Embed belt coal conveyor material-shortage alarm |  |  |  | %Z033104 | DI |  | 70CRA08 | [5 empty] | TBC03 | 7 | 8 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB71AF001XB01 | 1#螺旋给料机运行 | 1# screw feeder running | 70CRA07 | FCS0703 | 3 | 3 | 5 | ADV151-P | SI | N | 70HFB71AF001XB01 |  | 70HFB71AF001XB01 |  |  | 1# screw feeder running |  |  |  | %Z033105 | DI |  | 70CRA08 | [5 empty] | TBC03 | 9 | 10 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB71AF001XB21 | 1#螺旋给料机远控备妥 | 1# screw feeder remote control already | 70CRA07 | FCS0703 | 3 | 3 | 6 | ADV151-P | SI | N | 70HFB71AF001XB21 |  | 70HFB71AF001XB21 |  |  | 1# screw feeder remote control already |  |  |  | %Z033106 | DI |  | 70CRA08 | [5 empty] | TBC03 | 11 | 12 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB71AF001XB31 | 1#螺旋给料机故障 | 1# screw feeder fault | 70CRA07 | FCS0703 | 3 | 3 | 7 | ADV151-P | SI | N | 70HFB71AF001XB31 |  | 70HFB71AF001XB31 |  |  | 1# screw feeder fault |  |  |  | %Z033107 | DI |  | 70CRA08 | [5 empty] | TBC03 | 13 | 14 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB72AF001XB01 | 2#螺旋给料机运行 | 2# screw feeder running | 70CRA07 | FCS0703 | 3 | 3 | 8 | ADV151-P | SI | N | 70HFB72AF001XB01 |  | 70HFB72AF001XB01 |  |  | 2# screw feeder running |  |  |  | %Z033108 | DI |  | 70CRA08 | [5 empty] | TBC03 | 15 | 16 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB72AF001XB21 | 2#螺旋给料机远控备妥 | 2# screw feeder remote control already | 70CRA07 | FCS0703 | 3 | 3 | 9 | ADV151-P | SI | N | 70HFB72AF001XB21 |  | 70HFB72AF001XB21 |  |  | 2# screw feeder remote control already |  |  |  | %Z033109 | DI |  | 70CRA08 | [5 empty] | TBC03 | 17 | 18 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB72AF001XB31 | 2#螺旋给料机故障 | 2# screw feeder fault | 70CRA07 | FCS0703 | 3 | 3 | 10 | ADV151-P | SI | N | 70HFB72AF001XB31 |  | 70HFB72AF001XB31 |  |  | 2# screw feeder fault |  |  |  | %Z033110 | DI |  | 70CRA08 | [5 empty] | TBC03 | 19 | 20 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB71AA001XB01 | 1#螺旋给料机出口气动阀全开状态 | 1# screw feeder outlet PV full opened status | 70CRA07 | FCS0703 | 3 | 3 | 11 | ADV151-P | SI | N | 70HFB71AA001XB01 |  | 70HFB71AA001XB01 |  |  | 1# screw feeder outlet PV full opened status |  |  |  | %Z033111 | DI |  | 70CRA08 | [5 empty] | TBC03 | 21 | 22 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB71AA001XB11 | 1#螺旋给料机出口气动阀全关状态 | 1# screw feeder outlet PV full closed status | 70CRA07 | FCS0703 | 3 | 3 | 12 | ADV151-P | SI | N | 70HFB71AA001XB11 |  | 70HFB71AA001XB11 |  |  | 1# screw feeder outlet PV full closed status |  |  |  | %Z033112 | DI |  | 70CRA08 | [5 empty] | TBC03 | 23 | 24 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB71AA001XB21 | 1#螺旋给料机出口气动阀远控允许 | 1# screw feeder outlet PV remote control permitted | 70CRA07 | FCS0703 | 3 | 3 | 13 | ADV151-P | SI | N | 70HFB71AA001XB21 |  | 70HFB71AA001XB21 |  |  | 1# screw feeder outlet PV remote control permitted |  |  |  | %Z033113 | DI |  | 70CRA08 | [5 empty] | TBC03 | 25 | 26 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB72AA001XB01 | 2#螺旋给料机出口气动阀全开状态 | 2# screw feeder outlet PV full opened status | 70CRA07 | FCS0703 | 3 | 3 | 14 | ADV151-P | SI | N | 70HFB72AA001XB01 |  | 70HFB72AA001XB01 |  |  | 2# screw feeder outlet PV full opened status |  |  |  | %Z033114 | DI |  | 70CRA08 | [5 empty] | TBC03 | 27 | 28 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB72AA001XB11 | 2#螺旋给料机出口气动阀全关状态 | 2# screw feeder outlet PV full closed status | 70CRA07 | FCS0703 | 3 | 3 | 15 | ADV151-P | SI | N | 70HFB72AA001XB11 |  | 70HFB72AA001XB11 |  |  | 2# screw feeder outlet PV full closed status |  |  |  | %Z033115 | DI |  | 70CRA08 | [5 empty] | TBC03 | 29 | 30 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB72AA001XB21 | 2#螺旋给料机出口气动阀远控允许 | 2# screw feeder outlet PV remote control permitted | 70CRA07 | FCS0703 | 3 | 3 | 16 | ADV151-P | SI | N | 70HFB72AA001XB21 |  | 70HFB72AA001XB21 |  |  | 2# screw feeder outlet PV remote control permitted |  |  |  | %Z033116 | DI |  | 70CRA08 | [5 empty] | TBC03 | 31 | 32 |  |  | 70HFB70GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HJF10GH003YB01 | 1#油点火燃烧器启动允许 | 1# oil ignition burner start permitted | 70CRA07 | FCS0703 | 3 | 3 | 17 | ADV151-P | SI | N | 70HJF10GH003YB01 |  | 70HJF10GH003YB01 |  |  | 1# oil ignition burner start permitted |  |  |  | %Z033117 | DI |  | 70CRA08 | [5 empty] | TBC03 | 33 | 34 |  |  | 70HJF10GH003 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
|  | 70HJF10GH003YB02 | 1#油点火燃烧器灭火报警 | 1# oil ignition burner fire alarm | 70CRA07 | FCS0703 | 3 | 3 | 18 | ADV151-P | SI | N | 70HJF10GH003YB02 |  | 70HJF10GH003YB02 |  |  | 1# oil ignition burner fire alarm |  |  |  | %Z033118 | DI |  | 70CRA08 | [5 empty] | TBC03 | 35 | 36 |  |  | 70HJF10GH003 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
|  | 70HJF10GH003YB03 | 2#油点火燃烧器启动允许 | 2# oil ignition burner start permitted | 70CRA07 | FCS0703 | 3 | 3 | 19 | ADV151-P | SI | N | 70HJF10GH003YB03 |  | 70HJF10GH003YB03 |  |  | 2# oil ignition burner start permitted |  |  |  | %Z033119 | DI |  | 70CRA08 | [5 empty] | TBC03 | 37 | 38 |  |  | 70HJF10GH003 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
|  | 70HJF10GH003YB04 | 2#油点火燃烧器灭火报警 | 2# oil ignition burner fire alarm | 70CRA07 | FCS0703 | 3 | 3 | 20 | ADV151-P | SI | N | 70HJF10GH003YB04 |  | 70HJF10GH003YB04 |  |  | 2# oil ignition burner fire alarm |  |  |  | %Z033120 | DI |  | 70CRA08 | [5 empty] | TBC03 | 39 | 40 |  |  | 70HJF10GH003 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
|  | 70HJF10GH003YB05 | 3#油点火燃烧器启动允许 | 3# oil ignition burner start permitted | 70CRA07 | FCS0703 | 3 | 3 | 21 | ADV151-P | SI | N | 70HJF10GH003YB05 |  | 70HJF10GH003YB05 |  |  | 3# oil ignition burner start permitted |  |  |  | %Z033121 | DI |  | 70CRA08 | [5 empty] | TBC03 | 41 | 42 |  |  | 70HJF10GH003 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
|  | 70HJF10GH003YB06 | 3#油点火燃烧器灭火报警 | 3# oil ignition burner fire alarm | 70CRA07 | FCS0703 | 3 | 3 | 22 | ADV151-P | SI | N | 70HJF10GH003YB06 |  | 70HJF10GH003YB06 |  |  | 3# oil ignition burner fire alarm |  |  |  | %Z033122 | DI |  | 70CRA08 | [5 empty] | TBC03 | 43 | 44 |  |  | 70HJF10GH003 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
|  | 70HJF10GH003YB07 | 4#油点火燃烧器启动允许 | 4# oil ignition burner start permitted | 70CRA07 | FCS0703 | 3 | 3 | 23 | ADV151-P | SI | N | 70HJF10GH003YB07 |  | 70HJF10GH003YB07 |  |  | 4# oil ignition burner start permitted |  |  |  | %Z033123 | DI |  | 70CRA08 | [5 empty] | TBC03 | 45 | 46 |  |  | 70HJF10GH003 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
|  | 70HJF10GH003YB08 | 4#油点火燃烧器灭火报警 | 4# oil ignition burner fire alarm | 70CRA07 | FCS0703 | 3 | 3 | 24 | ADV151-P | SI | N | 70HJF10GH003YB08 |  | 70HJF10GH003YB08 |  |  | 4# oil ignition burner fire alarm |  |  |  | %Z033124 | DI |  | 70CRA08 | [5 empty] | TBC03 | 47 | 48 |  |  | 70HJF10GH003 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
|  | 70HJF10GH003YB09 | 5#油点火燃烧器启动允许 | 5# oil ignition burner start permitted | 70CRA07 | FCS0703 | 3 | 3 | 25 | ADV151-P | SI | N | 70HJF10GH003YB09 |  | 70HJF10GH003YB09 |  |  | 5# oil ignition burner start permitted |  |  |  | %Z033125 | DI |  | 70CRA08 | [5 empty] | TBC03 | 49 | 50 |  |  | 70HJF10GH003 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
|  | 70HJF10GH003YB10 | 5#油点火燃烧器灭火报警 | 5# oil ignition burner fire alarm | 70CRA07 | FCS0703 | 3 | 3 | 26 | ADV151-P | SI | N | 70HJF10GH003YB10 |  | 70HJF10GH003YB10 |  |  | 5# oil ignition burner fire alarm |  |  |  | %Z033126 | DI |  | 70CRA08 | [5 empty] | TBC03 | 51 | 52 |  |  | 70HJF10GH003 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
[5 empty] | 70CRA07 | FCS0703 | 3 | 3 | 27 | ADV151-P | SI | N | [9 empty] | %Z033127 | DI |  | 70CRA08 | [5 empty] | TBC03 | 53 | 54
[5 empty] | 70CRA07 | FCS0703 | 3 | 3 | 28 | ADV151-P | SI | N | [9 empty] | %Z033128 | DI |  | 70CRA08 | [5 empty] | TBC03 | 55 | 56
[5 empty] | 70CRA07 | FCS0703 | 3 | 3 | 29 | ADV151-P | SI | N | [9 empty] | %Z033129 | DI |  | 70CRA08 | [5 empty] | TBC03 | 57 | 58
[5 empty] | 70CRA07 | FCS0703 | 3 | 3 | 30 | ADV151-P | SI | N | [9 empty] | %Z033130 | DI |  | 70CRA08 | [5 empty] | TBC03 | 59 | 60
[5 empty] | 70CRA07 | FCS0703 | 3 | 3 | 31 | ADV151-P | SI | N | [9 empty] | %Z033131 | DI |  | 70CRA08 | [5 empty] | TBC03 | 61 | 62
[5 empty] | 70CRA07 | FCS0703 | 3 | 3 | 32 | ADV151-P | SI | N | [9 empty] | %Z033132 | DI |  | 70CRA08 | [5 empty] | TBC03 | 63 | 64
|  | 70HJF11AA001XB12 | 1#油点火燃烧器1#气动油阀全关状态2 | 1# oil ignition burner 1# oil PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 4 | 1 | ADV151-P | SI | N | 70HJF11AA001XB12 |  | 70HJF11AA001XB12 |  |  | 1# oil ignition burner 1# oil PV full closed status 2 |  |  |  | %Z034101 | DI |  | 70CRA08 | [5 empty] | TBC04 | 1 | 2 |  |  | 70HJF11GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 1#油点火燃烧器控制柜 | 1# oil ignition burnercontrol cabinet
|  | 70HJF11AA002XB12 | 1#油点火燃烧器2#气动油阀全关状态2 | 1# oil ignition burner 2# oil PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 4 | 2 | ADV151-P | SI | N | 70HJF11AA002XB12 |  | 70HJF11AA002XB12 |  |  | 1# oil ignition burner 2# oil PV full closed status 2 |  |  |  | %Z034102 | DI |  | 70CRA08 | [5 empty] | TBC04 | 3 | 4 |  |  | 70HJF11GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 1#油点火燃烧器控制柜 | 1# oil ignition burnercontrol cabinet
|  | 70HJF11CB101XB02 | 1#油点火燃烧器火焰信号2 | 1# oil ignition burner flame signal 2 | 70CRA07 | FCS0703 | 3 | 4 | 3 | ADV151-P | SI | N | 70HJF11CB101XB02 |  | 70HJF11CB101XB02 |  |  | 1# oil ignition burner flame signal 2 |  |  |  | %Z034103 | DI |  | 70CRA08 | [5 empty] | TBC04 | 5 | 6 |  |  | 70HJF11GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 1#油点火燃烧器控制柜 | 1# oil ignition burnercontrol cabinet
|  | 70HJF12AA001XB12 | 2#油点火燃烧器1#气动油阀全关状态2 | 2# oil ignition burner 1# oil PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 4 | 4 | ADV151-P | SI | N | 70HJF12AA001XB12 |  | 70HJF12AA001XB12 |  |  | 2# oil ignition burner 1# oil PV full closed status 2 |  |  |  | %Z034104 | DI |  | 70CRA08 | [5 empty] | TBC04 | 7 | 8 |  |  | 70HJF12GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 2#油点火燃烧器控制柜 | 2# oil ignition burnercontrol cabinet
|  | 70HJF12AA002XB12 | 2#油点火燃烧器2#气动油阀全关状态2 | 2# oil ignition burner 2# oil PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 4 | 5 | ADV151-P | SI | N | 70HJF12AA002XB12 |  | 70HJF12AA002XB12 |  |  | 2# oil ignition burner 2# oil PV full closed status 2 |  |  |  | %Z034105 | DI |  | 70CRA08 | [5 empty] | TBC04 | 9 | 10 |  |  | 70HJF12GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 2#油点火燃烧器控制柜 | 2# oil ignition burnercontrol cabinet
|  | 70HJF12CB101XB02 | 2#油点火燃烧器火焰信号2 | 2# oil ignition burner flame signal 2 | 70CRA07 | FCS0703 | 3 | 4 | 6 | ADV151-P | SI | N | 70HJF12CB101XB02 |  | 70HJF12CB101XB02 |  |  | 2# oil ignition burner flame signal 2 |  |  |  | %Z034106 | DI |  | 70CRA08 | [5 empty] | TBC04 | 11 | 12 |  |  | 70HJF12GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 2#油点火燃烧器控制柜 | 2# oil ignition burnercontrol cabinet
|  | 70HJF13AA001XB12 | 3#油点火燃烧器1#气动油阀全关状态2 | 3# oil ignition burner 1# oil PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 4 | 7 | ADV151-P | SI | N | 70HJF13AA001XB12 |  | 70HJF13AA001XB12 |  |  | 3# oil ignition burner 1# oil PV full closed status 2 |  |  |  | %Z034107 | DI |  | 70CRA08 | [5 empty] | TBC04 | 13 | 14 |  |  | 70HJF13GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 3#油点火燃烧器控制柜 | 3# oil ignition burnercontrol cabinet
|  | 70HJF13AA002XB12 | 3#油点火燃烧器2#气动油阀全关状态2 | 3# oil ignition burner 2# oil PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 4 | 8 | ADV151-P | SI | N | 70HJF13AA002XB12 |  | 70HJF13AA002XB12 |  |  | 3# oil ignition burner 2# oil PV full closed status 2 |  |  |  | %Z034108 | DI |  | 70CRA08 | [5 empty] | TBC04 | 15 | 16 |  |  | 70HJF13GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 3#油点火燃烧器控制柜 | 3# oil ignition burnercontrol cabinet
|  | 70HJF13CB101XB02 | 3#油点火燃烧器火焰信号2 | 3# oil ignition burner flame signal 2 | 70CRA07 | FCS0703 | 3 | 4 | 9 | ADV151-P | SI | N | 70HJF13CB101XB02 |  | 70HJF13CB101XB02 |  |  | 3# oil ignition burner flame signal 2 |  |  |  | %Z034109 | DI |  | 70CRA08 | [5 empty] | TBC04 | 17 | 18 |  |  | 70HJF13GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 3#油点火燃烧器控制柜 | 3# oil ignition burnercontrol cabinet
|  | 70HJF14AA001XB12 | 4#油点火燃烧器1#气动油阀全关状态2 | 4# oil ignition burner 1# oil PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 4 | 10 | ADV151-P | SI | N | 70HJF14AA001XB12 |  | 70HJF14AA001XB12 |  |  | 4# oil ignition burner 1# oil PV full closed status 2 |  |  |  | %Z034110 | DI |  | 70CRA08 | [5 empty] | TBC04 | 19 | 20 |  |  | 70HJF14GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 4#油点火燃烧器控制柜 | 4# oil ignition burnercontrol cabinet
|  | 70HJF14AA002XB12 | 4#油点火燃烧器2#气动油阀全关状态2 | 4# oil ignition burner 2# oil PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 4 | 11 | ADV151-P | SI | N | 70HJF14AA002XB12 |  | 70HJF14AA002XB12 |  |  | 4# oil ignition burner 2# oil PV full closed status 2 |  |  |  | %Z034111 | DI |  | 70CRA08 | [5 empty] | TBC04 | 21 | 22 |  |  | 70HJF14GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 4#油点火燃烧器控制柜 | 4# oil ignition burnercontrol cabinet
|  | 70HJF14CB101XB02 | 4#油点火燃烧器火焰信号2 | 4# oil ignition burner flame signal 2 | 70CRA07 | FCS0703 | 3 | 4 | 12 | ADV151-P | SI | N | 70HJF14CB101XB02 |  | 70HJF14CB101XB02 |  |  | 4# oil ignition burner flame signal 2 |  |  |  | %Z034112 | DI |  | 70CRA08 | [5 empty] | TBC04 | 23 | 24 |  |  | 70HJF14GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 4#油点火燃烧器控制柜 | 4# oil ignition burnercontrol cabinet
|  | 70HJF15AA001XB12 | 5#油点火燃烧器1#气动油阀全关状态2 | 5# oil ignition burner 1# oil PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 4 | 13 | ADV151-P | SI | N | 70HJF15AA001XB12 |  | 70HJF15AA001XB12 |  |  | 5# oil ignition burner 1# oil PV full closed status 2 |  |  |  | %Z034113 | DI |  | 70CRA08 | [5 empty] | TBC04 | 25 | 26 |  |  | 70HJF15GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 5#油点火燃烧器控制柜 | 5# oil ignition burnercontrol cabinet
|  | 70HJF15AA002XB12 | 5#油点火燃烧器2#气动油阀全关状态2 | 5# oil ignition burner 2# oil PV full closed status 2 | 70CRA07 | FCS0703 | 3 | 4 | 14 | ADV151-P | SI | N | 70HJF15AA002XB12 |  | 70HJF15AA002XB12 |  |  | 5# oil ignition burner 2# oil PV full closed status 2 |  |  |  | %Z034114 | DI |  | 70CRA08 | [5 empty] | TBC04 | 27 | 28 |  |  | 70HJF15GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 5#油点火燃烧器控制柜 | 5# oil ignition burnercontrol cabinet
|  | 70HJF15CB101XB02 | 5#油点火燃烧器火焰信号2 | 5# oil ignition burner flame signal 2 | 70CRA07 | FCS0703 | 3 | 4 | 15 | ADV151-P | SI | N | 70HJF15CB101XB02 |  | 70HJF15CB101XB02 |  |  | 5# oil ignition burner flame signal 2 |  |  |  | %Z034115 | DI |  | 70CRA08 | [5 empty] | TBC04 | 29 | 30 |  |  | 70HJF15GH001 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 5#油点火燃烧器控制柜 | 5# oil ignition burnercontrol cabinet
|  | 70HJF11CB101XB03 | 1#油点火燃烧器火检准备信号 | 1# oil ignition burner flame ready signal | 70CRA07 | FCS0703 | 3 | 4 | 16 | ADV151-P | SI | N | 70HJF11CB101XB03 |  | 70HJF11CB101XB03 |  |  | 1# oil ignition burner flame ready signal |  |  |  | %Z034116 | DI |  | 70CRA08 | [5 empty] | TBC04 | 31 | 32 |  |  | 70HJF10GH002 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
|  | 70HJF12CB101XB03 | 2#油点火燃烧器火检准备信号 | 2# oil ignition burner flame ready signal | 70CRA07 | FCS0703 | 3 | 4 | 17 | ADV151-P | SI | N | 70HJF12CB101XB03 |  | 70HJF12CB101XB03 |  |  | 2# oil ignition burner flame ready signal |  |  |  | %Z034117 | DI |  | 70CRA08 | [5 empty] | TBC04 | 33 | 34 |  |  | 70HJF10GH002 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
|  | 70HJF13CB101XB03 | 3#油点火燃烧器火检准备信号 | 3# oil ignition burner flame ready signal | 70CRA07 | FCS0703 | 3 | 4 | 18 | ADV151-P | SI | N | 70HJF13CB101XB03 |  | 70HJF13CB101XB03 |  |  | 3# oil ignition burner flame ready signal |  |  |  | %Z034118 | DI |  | 70CRA08 | [5 empty] | TBC04 | 35 | 36 |  |  | 70HJF10GH002 | NO | DI | [8 empty] | FSSS | D |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
|  | 70HJF14CB101XB03 | 4#油点火燃烧器火检准备信号 | 4# oil ignition burner flame ready signal | 70CRA07 | FCS0703 | 3 | 4 | 19 | ADV151-P | SI | N | 70HJF14CB101XB03 |  | 70HJF14CB101XB03 |  |  | 4# oil ignition burner flame ready signal |  |  |  | %Z034119 | DI |  | 70CRA08 | [5 empty] | TBC04 | 37 | 38 |  |  | 70HJF10GH002 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 火检电源柜 | Flame detection power cabinet
|  | 70HJF15CB101XB03 | 5#油点火燃烧器火检准备信号 | 5# oil ignition burner flame ready signal | 70CRA07 | FCS0703 | 3 | 4 | 20 | ADV151-P | SI | N | 70HJF15CB101XB03 |  | 70HJF15CB101XB03 |  |  | 5# oil ignition burner flame ready signal |  |  |  | %Z034120 | DI |  | 70CRA08 | [5 empty] | TBC04 | 39 | 40 |  |  | 70HJF10GH002 | NO | DI | [8 empty] | FSSS | D |  | K0202-003 | 火检电源柜 | Flame detection power cabinet
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 21 | ADV151-P | SI | N | [9 empty] | %Z034121 | DI |  | 70CRA08 | [5 empty] | TBC04 | 41 | 42
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 22 | ADV151-P | SI | N | [9 empty] | %Z034122 | DI |  | 70CRA08 | [5 empty] | TBC04 | 43 | 44
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 23 | ADV151-P | SI | N | [9 empty] | %Z034123 | DI |  | 70CRA08 | [5 empty] | TBC04 | 45 | 46
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 24 | ADV151-P | SI | N | [9 empty] | %Z034124 | DI |  | 70CRA08 | [5 empty] | TBC04 | 47 | 48
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 25 | ADV151-P | SI | N | [9 empty] | %Z034125 | DI |  | 70CRA08 | [5 empty] | TBC04 | 49 | 50
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 26 | ADV151-P | SI | N | [9 empty] | %Z034126 | DI |  | 70CRA08 | [5 empty] | TBC04 | 51 | 52
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 27 | ADV151-P | SI | N | [9 empty] | %Z034127 | DI |  | 70CRA08 | [5 empty] | TBC04 | 53 | 54
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 28 | ADV151-P | SI | N | [9 empty] | %Z034128 | DI |  | 70CRA08 | [5 empty] | TBC04 | 55 | 56
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 29 | ADV151-P | SI | N | [9 empty] | %Z034129 | DI |  | 70CRA08 | [5 empty] | TBC04 | 57 | 58
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 30 | ADV151-P | SI | N | [9 empty] | %Z034130 | DI |  | 70CRA08 | [5 empty] | TBC04 | 59 | 60
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 31 | ADV151-P | SI | N | [9 empty] | %Z034131 | DI |  | 70CRA08 | [5 empty] | TBC04 | 61 | 62
[5 empty] | 70CRA07 | FCS0703 | 3 | 4 | 32 | ADV151-P | SI | N | [9 empty] | %Z034132 | DI |  | 70CRA08 | [5 empty] | TBC04 | 63 | 64
|  | 70HFB10AF001YB01 | 1#给煤机启动指令 | 1# coal feeder start command | 70CRC01 | FCS0706 | 1 | 4 | 1 | ADV551-P | SO | N | 70HFB10AF001YB01 |  | 70HFB10AF001YB01 |  |  | 1# coal feeder start command |  |  |  | %Z014101 | DO |  | 70CRA08 | [5 empty] | TBE01 | 1 | 2 |  | 220VAC | 70HFB10GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AF001YB11 | 1#给煤机停止指令 | 1# coal feeder stop command | 70CRC01 | FCS0706 | 1 | 4 | 2 | ADV551-P | SO | N | 70HFB10AF001YB11 |  | 70HFB10AF001YB11 |  |  | 1# coal feeder stop command |  |  |  | %Z014102 | DO |  | 70CRA08 | [5 empty] | TBE01 | 3 | 4 |  | 220VAC | 70HFB10GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA001YB01 | 1#给煤机进口电动闸阀打开指令 | 1# coal feeder inlet MOV open command | 70CRC01 | FCS0706 | 1 | 4 | 3 | ADV551-P | SO | N | 70HFB10AA001YB01 |  | 70HFB10AA001YB01 |  |  | 1# coal feeder inlet MOV open command |  |  |  | %Z014103 | DO |  | 70CRA08 | [5 empty] | TBE01 | 5 | 6 |  | 220VAC | 70HFB10GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA001YB11 | 1#给煤机进口电动闸阀关闭指令 | 1# coal feeder inlet MOV close command | 70CRC01 | FCS0706 | 1 | 4 | 4 | ADV551-P | SO | N | 70HFB10AA001YB11 |  | 70HFB10AA001YB11 |  |  | 1# coal feeder inlet MOV close command |  |  |  | %Z014104 | DO |  | 70CRA08 | [5 empty] | TBE01 | 7 | 8 |  | 220VAC | 70HFB10GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA002YB01 | 1#给煤机出口气动阀打开指令 | 1# coal feeder outlet PV open command | 70CRC01 | FCS0706 | 1 | 4 | 5 | ADV551-P | SO | N | 70HFB10AA002YB01 |  | 70HFB10AA002YB01 |  |  | 1# coal feeder outlet PV open command |  |  |  | %Z014105 | DO |  | 70CRA08 | [5 empty] | TBE01 | 9 | 10 |  | 220VAC | 70HFB10GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB10AA002YB11 | 1#给煤机出口气动阀关闭指令 | 1# coal feeder outlet PV close command | 70CRC01 | FCS0706 | 1 | 4 | 6 | ADV551-P | SO | N | 70HFB10AA002YB11 |  | 70HFB10AA002YB11 |  |  | 1# coal feeder outlet PV close command |  |  |  | %Z014106 | DO |  | 70CRA08 | [5 empty] | TBE01 | 11 | 12 |  | 220VAC | 70HFB10GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
|  | 70HFB20AF001YB01 | 2#给煤机启动指令 | 2# coal feeder start command | 70CRC01 | FCS0706 | 1 | 4 | 7 | ADV551-P | SO | N | 70HFB20AF001YB01 |  | 70HFB20AF001YB01 |  |  | 2# coal feeder start command |  |  |  | %Z014107 | DO |  | 70CRA08 | [5 empty] | TBE01 | 13 | 14 |  | 220VAC | 70HFB20GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AF001YB11 | 2#给煤机停止指令 | 2# coal feeder stop command | 70CRC01 | FCS0706 | 1 | 4 | 8 | ADV551-P | SO | N | 70HFB20AF001YB11 |  | 70HFB20AF001YB11 |  |  | 2# coal feeder stop command |  |  |  | %Z014108 | DO |  | 70CRA08 | [5 empty] | TBE01 | 15 | 16 |  | 220VAC | 70HFB20GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA001YB01 | 2#给煤机进口电动闸阀打开指令 | 2# coal feeder inlet MOV open command | 70CRC01 | FCS0706 | 1 | 4 | 9 | ADV551-P | SO | N | 70HFB20AA001YB01 |  | 70HFB20AA001YB01 |  |  | 2# coal feeder inlet MOV open command |  |  |  | %Z014109 | DO |  | 70CRA08 | [5 empty] | TBE01 | 17 | 18 |  | 220VAC | 70HFB20GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA001YB11 | 2#给煤机进口电动闸阀关闭指令 | 2# coal feeder inlet MOV close command | 70CRC01 | FCS0706 | 1 | 4 | 10 | ADV551-P | SO | N | 70HFB20AA001YB11 |  | 70HFB20AA001YB11 |  |  | 2# coal feeder inlet MOV close command |  |  |  | %Z014110 | DO |  | 70CRA08 | [5 empty] | TBE01 | 19 | 20 |  | 220VAC | 70HFB20GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA002YB01 | 2#给煤机出口气动阀打开指令 | 2# coal feeder outlet PV open command | 70CRC01 | FCS0706 | 1 | 4 | 11 | ADV551-P | SO | N | 70HFB20AA002YB01 |  | 70HFB20AA002YB01 |  |  | 2# coal feeder outlet PV open command |  |  |  | %Z014111 | DO |  | 70CRA08 | [5 empty] | TBE01 | 21 | 22 |  | 220VAC | 70HFB20GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB20AA002YB11 | 2#给煤机出口气动阀关闭指令 | 2# coal feeder outlet PV close command | 70CRC01 | FCS0706 | 1 | 4 | 12 | ADV551-P | SO | N | 70HFB20AA002YB11 |  | 70HFB20AA002YB11 |  |  | 2# coal feeder outlet PV close command |  |  |  | %Z014112 | DO |  | 70CRA08 | [5 empty] | TBE01 | 23 | 24 |  | 220VAC | 70HFB20GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
|  | 70HFB60AF001YB01 | 污泥给料机启动指令 | Sludge feeder start command | 70CRC01 | FCS0706 | 1 | 4 | 13 | ADV551-P | SO | N | 70HFB60AF001YB01 |  | 70HFB60AF001YB01 |  |  | Sludge feeder start command |  |  |  | %Z014113 | DO |  | 70CRA08 | [5 empty] | TBE01 | 25 | 26 |  | 220VAC | 70HFB60GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
|  | 70HFB60AF001YB11 | 污泥给料机停止指令 | Sludge feeder stop command | 70CRC01 | FCS0706 | 1 | 4 | 14 | ADV551-P | SO | N | 70HFB60AF001YB11 |  | 70HFB60AF001YB11 |  |  | Sludge feeder stop command |  |  |  | %Z014114 | DO |  | 70CRA08 | [5 empty] | TBE01 | 27 | 28 |  | 220VAC | 70HFB60GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 15 | ADV551-P | SO | N | [9 empty] | %Z014115 | DO |  | 70CRA08 | [5 empty] | TBE01 | 29 | 30
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 16 | ADV551-P | SO | N | [9 empty] | %Z014116 | DO |  | 70CRA08 | [5 empty] | TBE01 | 31 | 32
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 17 | ADV551-P | SO | N | [9 empty] | %Z014117 | DO |  | 70CRA08 | [5 empty] | TBE01 | 33 | 34
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 18 | ADV551-P | SO | N | [9 empty] | %Z014118 | DO |  | 70CRA08 | [5 empty] | TBE01 | 35 | 36
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 19 | ADV551-P | SO | N | [9 empty] | %Z014119 | DO |  | 70CRA08 | [5 empty] | TBE01 | 37 | 38
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 20 | ADV551-P | SO | N | [9 empty] | %Z014120 | DO |  | 70CRA08 | [5 empty] | TBE01 | 39 | 40
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 21 | ADV551-P | SO | N | [9 empty] | %Z014121 | DO |  | 70CRA08 | [5 empty] | TBE01 | 41 | 42
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 22 | ADV551-P | SO | N | [9 empty] | %Z014122 | DO |  | 70CRA08 | [5 empty] | TBE01 | 43 | 44
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 23 | ADV551-P | SO | N | [9 empty] | %Z014123 | DO |  | 70CRA08 | [5 empty] | TBE01 | 45 | 46
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 24 | ADV551-P | SO | N | [9 empty] | %Z014124 | DO |  | 70CRA08 | [5 empty] | TBE01 | 47 | 48
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 25 | ADV551-P | SO | N | [9 empty] | %Z014125 | DO |  | 70CRA08 | [5 empty] | TBE01 | 49 | 50
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 26 | ADV551-P | SO | N | [9 empty] | %Z014126 | DO |  | 70CRA08 | [5 empty] | TBE01 | 51 | 52
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 27 | ADV551-P | SO | N | [9 empty] | %Z014127 | DO |  | 70CRA08 | [5 empty] | TBE01 | 53 | 54
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 28 | ADV551-P | SO | N | [9 empty] | %Z014128 | DO |  | 70CRA08 | [5 empty] | TBE01 | 55 | 56
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 29 | ADV551-P | SO | N | [9 empty] | %Z014129 | DO |  | 70CRA08 | [5 empty] | TBE01 | 57 | 58
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 30 | ADV551-P | SO | N | [9 empty] | %Z014130 | DO |  | 70CRA08 | [5 empty] | TBE01 | 59 | 60
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 31 | ADV551-P | SO | N | [9 empty] | %Z014131 | DO |  | 70CRA08 | [5 empty] | TBE01 | 61 | 62
[5 empty] | 70CRC01 | FCS0706 | 1 | 4 | 32 | ADV551-P | SO | N | [9 empty] | %Z014132 | DO |  | 70CRA08 | [5 empty] | TBE01 | 63 | 64
|  | 70HFB30AF001YB01 | 3#给煤机启动指令 | 3# coal feeder start command | 70CRC01 | FCS0706 | 2 | 4 | 1 | ADV551-P | SO | N | 70HFB30AF001YB01 |  | 70HFB30AF001YB01 |  |  | 3# coal feeder start command |  |  |  | %Z024101 | DO |  | 70CRA08 | [5 empty] | TBH01 | 1 | 2 |  | 220VAC | 70HFB30GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AF001YB11 | 3#给煤机停止指令 | 3# coal feeder stop command | 70CRC01 | FCS0706 | 2 | 4 | 2 | ADV551-P | SO | N | 70HFB30AF001YB11 |  | 70HFB30AF001YB11 |  |  | 3# coal feeder stop command |  |  |  | %Z024102 | DO |  | 70CRA08 | [5 empty] | TBH01 | 3 | 4 |  | 220VAC | 70HFB30GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA001YB01 | 3#给煤机进口电动闸阀打开指令 | 3# coal feeder inlet MOV open command | 70CRC01 | FCS0706 | 2 | 4 | 3 | ADV551-P | SO | N | 70HFB30AA001YB01 |  | 70HFB30AA001YB01 |  |  | 3# coal feeder inlet MOV open command |  |  |  | %Z024103 | DO |  | 70CRA08 | [5 empty] | TBH01 | 5 | 6 |  | 220VAC | 70HFB30GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA001YB11 | 3#给煤机进口电动闸阀关闭指令 | 3# coal feeder inlet MOV close command | 70CRC01 | FCS0706 | 2 | 4 | 4 | ADV551-P | SO | N | 70HFB30AA001YB11 |  | 70HFB30AA001YB11 |  |  | 3# coal feeder inlet MOV close command |  |  |  | %Z024104 | DO |  | 70CRA08 | [5 empty] | TBH01 | 7 | 8 |  | 220VAC | 70HFB30GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA002YB01 | 3#给煤机出口气动阀打开指令 | 3# coal feeder outlet PV open command | 70CRC01 | FCS0706 | 2 | 4 | 5 | ADV551-P | SO | N | 70HFB30AA002YB01 |  | 70HFB30AA002YB01 |  |  | 3# coal feeder outlet PV open command |  |  |  | %Z024105 | DO |  | 70CRA08 | [5 empty] | TBH01 | 9 | 10 |  | 220VAC | 70HFB30GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB30AA002YB11 | 3#给煤机出口气动阀关闭指令 | 3# coal feeder outlet PV close command | 70CRC01 | FCS0706 | 2 | 4 | 6 | ADV551-P | SO | N | 70HFB30AA002YB11 |  | 70HFB30AA002YB11 |  |  | 3# coal feeder outlet PV close command |  |  |  | %Z024106 | DO |  | 70CRA08 | [5 empty] | TBH01 | 11 | 12 |  | 220VAC | 70HFB30GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
|  | 70HFB40AF001YB01 | 4#给煤机启动指令 | 4# coal feeder start command | 70CRC01 | FCS0706 | 2 | 4 | 7 | ADV551-P | SO | N | 70HFB40AF001YB01 |  | 70HFB40AF001YB01 |  |  | 4# coal feeder start command |  |  |  | %Z024107 | DO |  | 70CRA08 | [5 empty] | TBH01 | 13 | 14 |  | 220VAC | 70HFB40GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AF001YB11 | 4#给煤机停止指令 | 4# coal feeder stop command | 70CRC01 | FCS0706 | 2 | 4 | 8 | ADV551-P | SO | N | 70HFB40AF001YB11 |  | 70HFB40AF001YB11 |  |  | 4# coal feeder stop command |  |  |  | %Z024108 | DO |  | 70CRA08 | [5 empty] | TBH01 | 15 | 16 |  | 220VAC | 70HFB40GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA001YB01 | 4#给煤机进口电动闸阀打开指令 | 4# coal feeder inlet MOV open command | 70CRC01 | FCS0706 | 2 | 4 | 9 | ADV551-P | SO | N | 70HFB40AA001YB01 |  | 70HFB40AA001YB01 |  |  | 4# coal feeder inlet MOV open command |  |  |  | %Z024109 | DO |  | 70CRA08 | [5 empty] | TBH01 | 17 | 18 |  | 220VAC | 70HFB40GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA001YB11 | 4#给煤机进口电动闸阀关闭指令 | 4# coal feeder inlet MOV close command | 70CRC01 | FCS0706 | 2 | 4 | 10 | ADV551-P | SO | N | 70HFB40AA001YB11 |  | 70HFB40AA001YB11 |  |  | 4# coal feeder inlet MOV close command |  |  |  | %Z024110 | DO |  | 70CRA08 | [5 empty] | TBH01 | 19 | 20 |  | 220VAC | 70HFB40GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA002YB01 | 4#给煤机出口气动阀打开指令 | 4# coal feeder outlet PV open command | 70CRC01 | FCS0706 | 2 | 4 | 11 | ADV551-P | SO | N | 70HFB40AA002YB01 |  | 70HFB40AA002YB01 |  |  | 4# coal feeder outlet PV open command |  |  |  | %Z024111 | DO |  | 70CRA08 | [5 empty] | TBH01 | 21 | 22 |  | 220VAC | 70HFB40GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB40AA002YB11 | 4#给煤机出口气动阀关闭指令 | 4# coal feeder outlet PV close command | 70CRC01 | FCS0706 | 2 | 4 | 12 | ADV551-P | SO | N | 70HFB40AA002YB11 |  | 70HFB40AA002YB11 |  |  | 4# coal feeder outlet PV close command |  |  |  | %Z024112 | DO |  | 70CRA08 | [5 empty] | TBH01 | 23 | 24 |  | 220VAC | 70HFB40GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
|  | 70HFB60AA001YB01 | 污泥给料机入口电动插板阀打开指令 | Sludge feeder inlet MOV open command | 70CRC01 | FCS0706 | 2 | 4 | 13 | ADV551-P | SO | N | 70HFB60AA001YB01 |  | 70HFB60AA001YB01 |  |  | Sludge feeder inlet MOV open command |  |  |  | %Z024113 | DO |  | 70CRA08 | [5 empty] | TBH01 | 25 | 26 |  | 220VAC | 70HFB60AA001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013
|  | 70HFB60AA001YB11 | 污泥给料机入口电动插板阀关闭指令 | Sludge feeder inlet MOV close command | 70CRC01 | FCS0706 | 2 | 4 | 14 | ADV551-P | SO | N | 70HFB60AA001YB11 |  | 70HFB60AA001YB11 |  |  | Sludge feeder inlet MOV close command |  |  |  | %Z024114 | DO |  | 70CRA08 | [5 empty] | TBH01 | 27 | 28 |  | 220VAC | 70HFB60AA001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 15 | ADV551-P | SO | N | [9 empty] | %Z024115 | DO |  | 70CRA08 | [5 empty] | TBH01 | 29 | 30
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 16 | ADV551-P | SO | N | [9 empty] | %Z024116 | DO |  | 70CRA08 | [5 empty] | TBH01 | 31 | 32
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 17 | ADV551-P | SO | N | [9 empty] | %Z024117 | DO |  | 70CRA08 | [5 empty] | TBH01 | 33 | 34
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 18 | ADV551-P | SO | N | [9 empty] | %Z024118 | DO |  | 70CRA08 | [5 empty] | TBH01 | 35 | 36
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 19 | ADV551-P | SO | N | [9 empty] | %Z024119 | DO |  | 70CRA08 | [5 empty] | TBH01 | 37 | 38
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 20 | ADV551-P | SO | N | [9 empty] | %Z024120 | DO |  | 70CRA08 | [5 empty] | TBH01 | 39 | 40
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 21 | ADV551-P | SO | N | [9 empty] | %Z024121 | DO |  | 70CRA08 | [5 empty] | TBH01 | 41 | 42
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 22 | ADV551-P | SO | N | [9 empty] | %Z024122 | DO |  | 70CRA08 | [5 empty] | TBH01 | 43 | 44
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 23 | ADV551-P | SO | N | [9 empty] | %Z024123 | DO |  | 70CRA08 | [5 empty] | TBH01 | 45 | 46
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 24 | ADV551-P | SO | N | [9 empty] | %Z024124 | DO |  | 70CRA08 | [5 empty] | TBH01 | 47 | 48
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 25 | ADV551-P | SO | N | [9 empty] | %Z024125 | DO |  | 70CRA08 | [5 empty] | TBH01 | 49 | 50
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 26 | ADV551-P | SO | N | [9 empty] | %Z024126 | DO |  | 70CRA08 | [5 empty] | TBH01 | 51 | 52
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 27 | ADV551-P | SO | N | [9 empty] | %Z024127 | DO |  | 70CRA08 | [5 empty] | TBH01 | 53 | 54
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 28 | ADV551-P | SO | N | [9 empty] | %Z024128 | DO |  | 70CRA08 | [5 empty] | TBH01 | 55 | 56
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 29 | ADV551-P | SO | N | [9 empty] | %Z024129 | DO |  | 70CRA08 | [5 empty] | TBH01 | 57 | 58
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 30 | ADV551-P | SO | N | [9 empty] | %Z024130 | DO |  | 70CRA08 | [5 empty] | TBH01 | 59 | 60
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 31 | ADV551-P | SO | N | [9 empty] | %Z024131 | DO |  | 70CRA08 | [5 empty] | TBH01 | 61 | 62
[5 empty] | 70CRC01 | FCS0706 | 2 | 4 | 32 | ADV551-P | SO | N | [9 empty] | %Z024132 | DO |  | 70CRA08 | [5 empty] | TBH01 | 63 | 64
|  | 70HFB50AF001YB01 | 5#给煤机启动指令 | 5# coal feeder start command | 70CRC01 | FCS0706 | 3 | 5 | 1 | ADV551-P | SO | N | 70HFB50AF001YB01 |  | 70HFB50AF001YB01 |  |  | 5# coal feeder start command |  |  |  | %Z035101 | DO |  | 70CRA08 | [5 empty] | TBC01 | 1 | 2 |  | 220VAC | 70HFB50GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AF001YB11 | 5#给煤机停止指令 | 5# coal feeder stop command | 70CRC01 | FCS0706 | 3 | 5 | 2 | ADV551-P | SO | N | 70HFB50AF001YB11 |  | 70HFB50AF001YB11 |  |  | 5# coal feeder stop command |  |  |  | %Z035102 | DO |  | 70CRA08 | [5 empty] | TBC01 | 3 | 4 |  | 220VAC | 70HFB50GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AA001YB01 | 5#给煤机进口电动闸阀打开指令 | 5# coal feeder inlet MOV open command | 70CRC01 | FCS0706 | 3 | 5 | 3 | ADV551-P | SO | N | 70HFB50AA001YB01 |  | 70HFB50AA001YB01 |  |  | 5# coal feeder inlet MOV open command |  |  |  | %Z035103 | DO |  | 70CRA08 | [5 empty] | TBC01 | 5 | 6 |  | 220VAC | 70HFB50GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB50AA001YB11 | 5#给煤机进口电动闸阀关闭指令 | 5# coal feeder inlet MOV close command | 70CRC01 | FCS0706 | 3 | 5 | 4 | ADV551-P | SO | N | 70HFB50AA001YB11 |  | 70HFB50AA001YB11 |  |  | 5# coal feeder inlet MOV close command |  |  |  | %Z035104 | DO |  | 70CRA08 | [5 empty] | TBC01 | 7 | 8 |  | 220VAC | 70HFB50GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
|  | 70HFB70AF001YB01 | 埋刮板输送机启动指令 | Embed belt coal conveyor start command | 70CRC01 | FCS0706 | 3 | 5 | 5 | ADV551-P | SO | N | 70HFB70AF001YB01 |  | 70HFB70AF001YB01 |  |  | Embed belt coal conveyor start command |  |  |  | %Z035105 | DO |  | 70CRA08 | [5 empty] | TBC01 | 9 | 10 |  | 220VAC | 70HFB70GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB70AF001YB11 | 埋刮板输送机停止指令 | Embed belt coal conveyor stop command | 70CRC01 | FCS0706 | 3 | 5 | 6 | ADV551-P | SO | N | 70HFB70AF001YB11 |  | 70HFB70AF001YB11 |  |  | Embed belt coal conveyor stop command |  |  |  | %Z035106 | DO |  | 70CRA08 | [5 empty] | TBC01 | 11 | 12 |  | 220VAC | 70HFB70GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB71AF001YB01 | 1#螺旋给料机启动指令 | 1# screw feeder start command | 70CRC01 | FCS0706 | 3 | 5 | 7 | ADV551-P | SO | N | 70HFB71AF001YB01 |  | 70HFB71AF001YB01 |  |  | 1# screw feeder start command |  |  |  | %Z035107 | DO |  | 70CRA08 | [5 empty] | TBC01 | 13 | 14 |  | 220VAC | 70HFB70GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB71AF001YB11 | 1#螺旋给料机停止指令 | 1# screw feeder stop command | 70CRC01 | FCS0706 | 3 | 5 | 8 | ADV551-P | SO | N | 70HFB71AF001YB11 |  | 70HFB71AF001YB11 |  |  | 1# screw feeder stop command |  |  |  | %Z035108 | DO |  | 70CRA08 | [5 empty] | TBC01 | 15 | 16 |  | 220VAC | 70HFB70GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB72AF001YB01 | 2#螺旋给料机启动指令 | 2# screw feeder start command | 70CRC01 | FCS0706 | 3 | 5 | 9 | ADV551-P | SO | N | 70HFB72AF001YB01 |  | 70HFB72AF001YB01 |  |  | 2# screw feeder start command |  |  |  | %Z035109 | DO |  | 70CRA08 | [5 empty] | TBC01 | 17 | 18 |  | 220VAC | 70HFB70GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB72AF001YB11 | 2#螺旋给料机停止指令 | 2# screw feeder stop command | 70CRC01 | FCS0706 | 3 | 5 | 10 | ADV551-P | SO | N | 70HFB72AF001YB11 |  | 70HFB72AF001YB11 |  |  | 2# screw feeder stop command |  |  |  | %Z035110 | DO |  | 70CRA08 | [5 empty] | TBC01 | 19 | 20 |  | 220VAC | 70HFB70GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB71AA001YB01 | 1#螺旋给料机出口气动阀打开指令 | 1# screw feeder outlet PV open command | 70CRC01 | FCS0706 | 3 | 5 | 11 | ADV551-P | SO | N | 70HFB71AA001YB01 |  | 70HFB71AA001YB01 |  |  | 1# screw feeder outlet PV open command |  |  |  | %Z035111 | DO |  | 70CRA08 | [5 empty] | TBC01 | 21 | 22 |  | 220VAC | 70HFB70GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB71AA001YB11 | 1#螺旋给料机出口气动阀关闭指令 | 1# screw feeder outlet PV close command | 70CRC01 | FCS0706 | 3 | 5 | 12 | ADV551-P | SO | N | 70HFB71AA001YB11 |  | 70HFB71AA001YB11 |  |  | 1# screw feeder outlet PV close command |  |  |  | %Z035112 | DO |  | 70CRA08 | [5 empty] | TBC01 | 23 | 24 |  | 220VAC | 70HFB70GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB72AA001YB01 | 2#螺旋给料机出口气动阀打开指令 | 2# screw feeder outlet PV open command | 70CRC01 | FCS0706 | 3 | 5 | 13 | ADV551-P | SO | N | 70HFB72AA001YB01 |  | 70HFB72AA001YB01 |  |  | 2# screw feeder outlet PV open command |  |  |  | %Z035113 | DO |  | 70CRA08 | [5 empty] | TBC01 | 25 | 26 |  | 220VAC | 70HFB70GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HFB72AA001YB11 | 2#螺旋给料机出口气动阀关闭指令 | 2# screw feeder outlet PV close command | 70CRC01 | FCS0706 | 3 | 5 | 14 | ADV551-P | SO | N | 70HFB72AA001YB11 |  | 70HFB72AA001YB11 |  |  | 2# screw feeder outlet PV close command |  |  |  | %Z035114 | DO |  | 70CRA08 | [5 empty] | TBC01 | 27 | 28 |  | 220VAC | 70HFB70GH001 | NO | DO | [8 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
|  | 70HJF11GH001YB01 | 1#油点火燃烧器控制柜启动程序 | 1# oil ignition burner control cabinet start program | 70CRC01 | FCS0706 | 3 | 5 | 15 | ADV551-P | SO | N | 70HJF11GH001YB01 |  | 70HJF11GH001YB01 |  |  | 1# oil ignition burner control cabinet start program |  |  |  | %Z035115 | DO |  | 70CRA08 | [5 empty] | TBC01 | 29 | 30 |  | 24VDC | 70HJF11GH001 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-002 | 1#油点火燃烧器控制柜 | 1# oil ignition burnercontrol cabinet
|  | 70HJF11GH001YB11 | 1#油点火燃烧器控制柜停止程序 | 1# oil ignition burner control cabinet stop program | 70CRC01 | FCS0706 | 3 | 5 | 16 | ADV551-P | SO | N | 70HJF11GH001YB11 |  | 70HJF11GH001YB11 |  |  | 1# oil ignition burner control cabinet stop program |  |  |  | %Z035116 | DO |  | 70CRA08 | [5 empty] | TBC01 | 31 | 32 |  | 24VDC | 70HJF11GH001 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-002 | 1#油点火燃烧器控制柜 | 1# oil ignition burnercontrol cabinet
|  | 70HJF12GH001YB01 | 2#油点火燃烧器控制柜启动程序 | 2# oil ignition burner control cabinet start program | 70CRC01 | FCS0706 | 3 | 5 | 17 | ADV551-P | SO | N | 70HJF12GH001YB01 |  | 70HJF12GH001YB01 |  |  | 2# oil ignition burner control cabinet start program |  |  |  | %Z035117 | DO |  | 70CRA08 | [5 empty] | TBC01 | 33 | 34 |  | 24VDC | 70HJF12GH001 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-002 | 2#油点火燃烧器控制柜 | 2# oil ignition burnercontrol cabinet
|  | 70HJF12GH001YB11 | 2#油点火燃烧器控制柜停止程序 | 2# oil ignition burner control cabinet stop program | 70CRC01 | FCS0706 | 3 | 5 | 18 | ADV551-P | SO | N | 70HJF12GH001YB11 |  | 70HJF12GH001YB11 |  |  | 2# oil ignition burner control cabinet stop program |  |  |  | %Z035118 | DO |  | 70CRA08 | [5 empty] | TBC01 | 35 | 36 |  | 24VDC | 70HJF12GH001 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-002 | 2#油点火燃烧器控制柜 | 2# oil ignition burnercontrol cabinet
|  | 70HJF13GH001YB01 | 3#油点火燃烧器控制柜启动程序 | 3# oil ignition burner control cabinet start program | 70CRC01 | FCS0706 | 3 | 5 | 19 | ADV551-P | SO | N | 70HJF13GH001YB01 |  | 70HJF13GH001YB01 |  |  | 3# oil ignition burner control cabinet start program |  |  |  | %Z035119 | DO |  | 70CRA08 | [5 empty] | TBC01 | 37 | 38 |  | 24VDC | 70HJF13GH001 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-002 | 3#油点火燃烧器控制柜 | 3# oil ignition burnercontrol cabinet
|  | 70HJF13GH001YB11 | 3#油点火燃烧器控制柜停止程序 | 3# oil ignition burner control cabinet stop program | 70CRC01 | FCS0706 | 3 | 5 | 20 | ADV551-P | SO | N | 70HJF13GH001YB11 |  | 70HJF13GH001YB11 |  |  | 3# oil ignition burner control cabinet stop program |  |  |  | %Z035120 | DO |  | 70CRA08 | [5 empty] | TBC01 | 39 | 40 |  | 24VDC | 70HJF13GH001 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-002 | 3#油点火燃烧器控制柜 | 3# oil ignition burnercontrol cabinet
|  | 70HJF14GH001YB01 | 4#油点火燃烧器控制柜启动程序 | 4# oil ignition burner control cabinet start program | 70CRC01 | FCS0706 | 3 | 5 | 21 | ADV551-P | SO | N | 70HJF14GH001YB01 |  | 70HJF14GH001YB01 |  |  | 4# oil ignition burner control cabinet start program |  |  |  | %Z035121 | DO |  | 70CRA08 | [5 empty] | TBC01 | 41 | 42 |  | 24VDC | 70HJF14GH001 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-003 | 4#油点火燃烧器控制柜 | 4# oil ignition burnercontrol cabinet
|  | 70HJF14GH001YB11 | 4#油点火燃烧器控制柜停止程序 | 4# oil ignition burner control cabinet stop program | 70CRC01 | FCS0706 | 3 | 5 | 22 | ADV551-P | SO | N | 70HJF14GH001YB11 |  | 70HJF14GH001YB11 |  |  | 4# oil ignition burner control cabinet stop program |  |  |  | %Z035122 | DO |  | 70CRA08 | [5 empty] | TBC01 | 43 | 44 |  | 24VDC | 70HJF14GH001 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-003 | 4#油点火燃烧器控制柜 | 4# oil ignition burnercontrol cabinet
|  | 70HJF15GH001YB01 | 5#油点火燃烧器控制柜启动程序 | 5# oil ignition burner control cabinet start program | 70CRC01 | FCS0706 | 3 | 5 | 23 | ADV551-P | SO | N | 70HJF15GH001YB01 |  | 70HJF15GH001YB01 |  |  | 5# oil ignition burner control cabinet start program |  |  |  | %Z035123 | DO |  | 70CRA08 | [5 empty] | TBC01 | 45 | 46 |  | 24VDC | 70HJF15GH001 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-003 | 5#油点火燃烧器控制柜 | 5# oil ignition burnercontrol cabinet
|  | 70HJF15GH001YB11 | 5#油点火燃烧器控制柜停止程序 | 5# oil ignition burner control cabinet stop program | 70CRC01 | FCS0706 | 3 | 5 | 24 | ADV551-P | SO | N | 70HJF15GH001YB11 |  | 70HJF15GH001YB11 |  |  | 5# oil ignition burner control cabinet stop program |  |  |  | %Z035124 | DO |  | 70CRA08 | [5 empty] | TBC01 | 47 | 48 |  | 24VDC | 70HJF15GH001 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-003 | 5#油点火燃烧器控制柜 | 5# oil ignition burnercontrol cabinet
|  | 70HJF10GH003XB02 | 点火燃烧器允许启动指令 | Ignition burner allows start command | 70CRC01 | FCS0706 | 3 | 5 | 25 | ADV551-P | SO | N | 70HJF10GH003XB02 |  | 70HJF10GH003XB02 |  |  | Ignition burner allows start command |  |  |  | %Z035125 | DO |  | 70CRA08 | [5 empty] | TBC01 | 49 | 50 |  | 24VDC | 70HJF10GH003 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
|  | 70HJF10GH003XB03 | 点火燃烧器故障复位 | Ignition burner fault reset | 70CRC01 | FCS0706 | 3 | 5 | 26 | ADV551-P | SO | N | 70HJF10GH003XB03 |  | 70HJF10GH003XB03 |  |  | Ignition burner fault reset |  |  |  | %Z035126 | DO |  | 70CRA08 | [5 empty] | TBC01 | 51 | 52 |  | 24VDC | 70HJF10GH003 | NO | DO | [8 empty] | FSSS | U | 24VDC | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
[5 empty] | 70CRC01 | FCS0706 | 3 | 5 | 27 | ADV551-P | SO | N | [9 empty] | %Z035127 | DO |  | 70CRA08 | [5 empty] | TBC01 | 53 | 54
[5 empty] | 70CRC01 | FCS0706 | 3 | 5 | 28 | ADV551-P | SO | N | [9 empty] | %Z035128 | DO |  | 70CRA08 | [5 empty] | TBC01 | 55 | 56
[5 empty] | 70CRC01 | FCS0706 | 3 | 5 | 29 | ADV551-P | SO | N | [9 empty] | %Z035129 | DO |  | 70CRA08 | [5 empty] | TBC01 | 57 | 58
[5 empty] | 70CRC01 | FCS0706 | 3 | 5 | 30 | ADV551-P | SO | N | [9 empty] | %Z035130 | DO |  | 70CRA08 | [5 empty] | TBC01 | 59 | 60
[5 empty] | 70CRC01 | FCS0706 | 3 | 5 | 31 | ADV551-P | SO | N | [9 empty] | %Z035131 | DO |  | 70CRA08 | [5 empty] | TBC01 | 61 | 62
[5 empty] | 70CRC01 | FCS0706 | 3 | 5 | 32 | ADV551-P | SO | N | [9 empty] | %Z035132 | DO |  | 70CRA08 | [5 empty] | TBC01 | 63 | 64
Note on AD1: 作者: Surge arrester(SA) model

## IOlsit
| PID_TAG | COMMENT(Chinese) | COMMENT | Source | Type | I/O | ENG_LO | ENG_UNITS | HHH | HH | H | L | LL | LLL | LOG | SOE | DCS Subfunction | Power Supply | Excitation Voltage | Drawing No. | Chinese Remark | English Remark
160 | 70HJF10CP101 | 油点火燃烧器供油母管压力 | Oil ignition burner oli supply main pipe pressure | 70HJF10CP101 | 4~20mA | AI | 0~2.5 | Mpa | [8 empty] | FSSS | D |  | K0202-001
161 | 70HJF20CP101 | 油点火燃烧器回油母管压力 | Oil ignition burner oli return main pipe pressure | 70HJF20CP101 | 4~20mA | AI | 0~2.5 | Mpa | [8 empty] | FSSS | D |  | K0202-001
162 | 70HJF20CF101 | 油点火燃烧器回油母管流量 | Oil ignition burner oli return main pipe flow | 70HJF20CF101 | 4~20mA | AI | 0~10 | t/h | [8 empty] | FSSS | U |  | K0202-001
163 | 70HJF10AA001XB12 | 燃油系统供油气动主油阀全关状态2 | Fuel oil system main oil supply PV full closed status 2 | 70HJF10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
164 | 70HJF21AA001XB12 | 1#油点火燃烧器气动回油阀全关状态2 | 1# oil ignition burner oil return PV full closed status 2 | 70HJF10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
165 | 70HJF22AA001XB12 | 2#油点火燃烧器气动回油阀全关状态2 | 2# oil ignition burner oil return PV full closed status 2 | 70HJF10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
166 | 70HJF23AA001XB12 | 3#油点火燃烧器气动回油阀全关状态2 | 3# oil ignition burner oil return PV full closed status 2 | 70HJF10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
167 | 70HJF24AA001XB12 | 4#油点火燃烧器气动回油阀全关状态2 | 4# oil ignition burner oil return PV full closed status 2 | 70HJF10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
168 | 70HJF25AA001XB12 | 5#油点火燃烧器气动回油阀全关状态2 | 5# oil ignition burner oil return PV full closed status 2 | 70HJF10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-001 | 点火控制柜 | Ignition control cabinet
172 | 70HJF11AA001XB12 | 1#油点火燃烧器1#气动油阀全关状态2 | 1# oil ignition burner 1# oil PV full closed status 2 | 70HJF11GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 1#油点火燃烧器控制柜 | 1# oil ignition burnercontrol cabinet
173 | 70HJF11AA002XB12 | 1#油点火燃烧器2#气动油阀全关状态2 | 1# oil ignition burner 2# oil PV full closed status 2 | 70HJF11GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 1#油点火燃烧器控制柜 | 1# oil ignition burnercontrol cabinet
174 | 70HJF11CB101XB02 | 1#油点火燃烧器火焰信号2 | 1# oil ignition burner flame signal 2 | 70HJF11GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 1#油点火燃烧器控制柜 | 1# oil ignition burnercontrol cabinet
175 | 70HJF11GH001YB01 | 1#油点火燃烧器控制柜启动程序 | 1# oil ignition burner control cabinet start program | 70HJF11GH001 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-002 | 1#油点火燃烧器控制柜 | 1# oil ignition burnercontrol cabinet
176 | 70HJF11GH001YB11 | 1#油点火燃烧器控制柜停止程序 | 1# oil ignition burner control cabinet stop program | 70HJF11GH001 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-002 | 1#油点火燃烧器控制柜 | 1# oil ignition burnercontrol cabinet
177 | 70HJF12AA001XB12 | 2#油点火燃烧器1#气动油阀全关状态2 | 2# oil ignition burner 1# oil PV full closed status 2 | 70HJF12GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 2#油点火燃烧器控制柜 | 2# oil ignition burnercontrol cabinet
178 | 70HJF12AA002XB12 | 2#油点火燃烧器2#气动油阀全关状态2 | 2# oil ignition burner 2# oil PV full closed status 2 | 70HJF12GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 2#油点火燃烧器控制柜 | 2# oil ignition burnercontrol cabinet
179 | 70HJF12CB101XB02 | 2#油点火燃烧器火焰信号2 | 2# oil ignition burner flame signal 2 | 70HJF12GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 2#油点火燃烧器控制柜 | 2# oil ignition burnercontrol cabinet
180 | 70HJF12GH001YB01 | 2#油点火燃烧器控制柜启动程序 | 2# oil ignition burner control cabinet start program | 70HJF12GH001 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-002 | 2#油点火燃烧器控制柜 | 2# oil ignition burnercontrol cabinet
181 | 70HJF12GH001YB11 | 2#油点火燃烧器控制柜停止程序 | 2# oil ignition burner control cabinet stop program | 70HJF12GH001 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-002 | 2#油点火燃烧器控制柜 | 2# oil ignition burnercontrol cabinet
182 | 70HJF13AA001XB12 | 3#油点火燃烧器1#气动油阀全关状态2 | 3# oil ignition burner 1# oil PV full closed status 2 | 70HJF13GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 3#油点火燃烧器控制柜 | 3# oil ignition burnercontrol cabinet
183 | 70HJF13AA002XB12 | 3#油点火燃烧器2#气动油阀全关状态2 | 3# oil ignition burner 2# oil PV full closed status 2 | 70HJF13GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 3#油点火燃烧器控制柜 | 3# oil ignition burnercontrol cabinet
184 | 70HJF13CB101XB02 | 3#油点火燃烧器火焰信号2 | 3# oil ignition burner flame signal 2 | 70HJF13GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 3#油点火燃烧器控制柜 | 3# oil ignition burnercontrol cabinet
185 | 70HJF13GH001YB01 | 3#油点火燃烧器控制柜启动程序 | 3# oil ignition burner control cabinet start program | 70HJF13GH001 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-002 | 3#油点火燃烧器控制柜 | 3# oil ignition burnercontrol cabinet
186 | 70HJF13GH001YB11 | 3#油点火燃烧器控制柜停止程序 | 3# oil ignition burner control cabinet stop program | 70HJF13GH001 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-002 | 3#油点火燃烧器控制柜 | 3# oil ignition burnercontrol cabinet
187 | 70HJF11CB101XQ01 | 1#油点火燃烧器火焰强度 | 1# oil ignition burner flame strength | 70HJF10GH002 | 4~20mA | AI | [10 empty] | FSSS | U |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
188 | 70HJF11CB101XB03 | 1#油点火燃烧器火检准备信号 | 1# oil ignition burner flame ready signal | 70HJF10GH002 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
189 | 70HJF12CB101XQ01 | 2#油点火燃烧器火焰强度 | 2# oil ignition burner flame strength | 70HJF10GH002 | 4~20mA | AI | [10 empty] | FSSS | U |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
190 | 70HJF12CB101XB03 | 2#油点火燃烧器火检准备信号 | 2# oil ignition burner flame ready signal | 70HJF10GH002 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
191 | 70HJF13CB101XQ01 | 3#油点火燃烧器火焰强度 | 3# oil ignition burner flame strength | 70HJF10GH002 | 4~20mA | AI | [10 empty] | FSSS | U |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
192 | 70HJF13CB101XB03 | 3#油点火燃烧器火检准备信号 | 3# oil ignition burner flame ready signal | 70HJF10GH002 | NO | DI | [10 empty] | FSSS | D |  | K0202-002 | 火检电源柜 | Flame detection power cabinet
193 | 70HJF14AA001XB12 | 4#油点火燃烧器1#气动油阀全关状态2 | 4# oil ignition burner 1# oil PV full closed status 2 | 70HJF14GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 4#油点火燃烧器控制柜 | 4# oil ignition burnercontrol cabinet
194 | 70HJF14AA002XB12 | 4#油点火燃烧器2#气动油阀全关状态2 | 4# oil ignition burner 2# oil PV full closed status 2 | 70HJF14GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 4#油点火燃烧器控制柜 | 4# oil ignition burnercontrol cabinet
195 | 70HJF14CB101XB02 | 4#油点火燃烧器火焰信号2 | 4# oil ignition burner flame signal 2 | 70HJF14GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 4#油点火燃烧器控制柜 | 4# oil ignition burnercontrol cabinet
196 | 70HJF14GH001YB01 | 4#油点火燃烧器控制柜启动程序 | 4# oil ignition burner control cabinet start program | 70HJF14GH001 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-003 | 4#油点火燃烧器控制柜 | 4# oil ignition burnercontrol cabinet
197 | 70HJF14GH001YB11 | 4#油点火燃烧器控制柜停止程序 | 4# oil ignition burner control cabinet stop program | 70HJF14GH001 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-003 | 4#油点火燃烧器控制柜 | 4# oil ignition burnercontrol cabinet
198 | 70HJF15AA001XB12 | 5#油点火燃烧器1#气动油阀全关状态2 | 5# oil ignition burner 1# oil PV full closed status 2 | 70HJF15GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 5#油点火燃烧器控制柜 | 5# oil ignition burnercontrol cabinet
199 | 70HJF15AA002XB12 | 5#油点火燃烧器2#气动油阀全关状态2 | 5# oil ignition burner 2# oil PV full closed status 2 | 70HJF15GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 5#油点火燃烧器控制柜 | 5# oil ignition burnercontrol cabinet
200 | 70HJF15CB101XB02 | 5#油点火燃烧器火焰信号2 | 5# oil ignition burner flame signal 2 | 70HJF15GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 5#油点火燃烧器控制柜 | 5# oil ignition burnercontrol cabinet
201 | 70HJF15GH001YB01 | 5#油点火燃烧器控制柜启动程序 | 5# oil ignition burner control cabinet start program | 70HJF15GH001 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-003 | 5#油点火燃烧器控制柜 | 5# oil ignition burnercontrol cabinet
202 | 70HJF15GH001YB11 | 5#油点火燃烧器控制柜停止程序 | 5# oil ignition burner control cabinet stop program | 70HJF15GH001 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-003 | 5#油点火燃烧器控制柜 | 5# oil ignition burnercontrol cabinet
203 | 70HJF14CB101XQ01 | 4#油点火燃烧器火焰强度 | 4# oil ignition burner flame strength | 70HJF10GH002 | 4~20mA | AI | [10 empty] | FSSS | U |  | K0202-003 | 火检电源柜 | Flame detection power cabinet
204 | 70HJF14CB101XB03 | 4#油点火燃烧器火检准备信号 | 4# oil ignition burner flame ready signal | 70HJF10GH002 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 火检电源柜 | Flame detection power cabinet
205 | 70HJF15CB101XQ01 | 5#油点火燃烧器火焰强度 | 5# oil ignition burner flame strength | 70HJF10GH002 | 4~20mA | AI | [10 empty] | FSSS | D |  | K0202-003 | 火检电源柜 | Flame detection power cabinet
206 | 70HJF15CB101XB03 | 5#油点火燃烧器火检准备信号 | 5# oil ignition burner flame ready signal | 70HJF10GH002 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 火检电源柜 | Flame detection power cabinet
207 | 70HJF10GH003XB02 | 点火燃烧器允许启动指令 | Ignition burner allows start command | 70HJF10GH003 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
208 | 70HJF10GH003XB03 | 点火燃烧器故障复位 | Ignition burner fault reset | 70HJF10GH003 | NO | DO | [10 empty] | FSSS | U | 24VDC | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
209 | 70HJF10GH003YB01 | 1#油点火燃烧器启动允许 | 1# oil ignition burner start permitted | 70HJF10GH003 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
210 | 70HJF10GH003YB02 | 1#油点火燃烧器灭火报警 | 1# oil ignition burner fire alarm | 70HJF10GH003 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
211 | 70HJF10GH003YB03 | 2#油点火燃烧器启动允许 | 2# oil ignition burner start permitted | 70HJF10GH003 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
212 | 70HJF10GH003YB04 | 2#油点火燃烧器灭火报警 | 2# oil ignition burner fire alarm | 70HJF10GH003 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
213 | 70HJF10GH003YB05 | 3#油点火燃烧器启动允许 | 3# oil ignition burner start permitted | 70HJF10GH003 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
214 | 70HJF10GH003YB06 | 3#油点火燃烧器灭火报警 | 3# oil ignition burner fire alarm | 70HJF10GH003 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
215 | 70HJF10GH003YB07 | 4#油点火燃烧器启动允许 | 4# oil ignition burner start permitted | 70HJF10GH003 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
216 | 70HJF10GH003YB08 | 4#油点火燃烧器灭火报警 | 4# oil ignition burner fire alarm | 70HJF10GH003 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
217 | 70HJF10GH003YB09 | 5#油点火燃烧器启动允许 | 5# oil ignition burner start permitted | 70HJF10GH003 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
218 | 70HJF10GH003YB10 | 5#油点火燃烧器灭火报警 | 5# oil ignition burner fire alarm | 70HJF10GH003 | NO | DI | [10 empty] | FSSS | D |  | K0202-003 | 点火PLC柜 | Ignition PLC cabinet
226 | 70HBB10CT101A | 锅炉炉膛床温1 | Boiler furnace bed temperature 1 | 70HBB10CT101A | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
227 | 70HBB10CT101B | 锅炉炉膛床温2 | Boiler furnace bed temperature 2 | 70HBB10CT101B | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
228 | 70HBB10CT101C | 锅炉炉膛床温3 | Boiler furnace bed temperature 3 | 70HBB10CT101C | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
229 | 70HBB10CT101D | 锅炉炉膛床温4 | Boiler furnace bed temperature 4 | 70HBB10CT101D | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
230 | 70HBB10CT101E | 锅炉炉膛床温5 | Boiler furnace bed temperature 5 | 70HBB10CT101E | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
231 | 70HBB10CT101F | 锅炉炉膛床温6 | Boiler furnace bed temperature 6 | 70HBB10CT101F | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
232 | 70HBB10CT101G | 锅炉炉膛床温7 | Boiler furnace bed temperature 7 | 70HBB10CT101G | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
233 | 70HBB10CT101H | 锅炉炉膛床温8 | Boiler furnace bed temperature 8 | 70HBB10CT101H | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
242 | 70HBB10CT104A | 锅炉炉膛出口烟气温度左1 | Boiler furnace outlet flue gas temperature left 1 | 70HBB10CT104A | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
243 | 70HBB10CT104B | 锅炉炉膛出口烟气温度左2 | Boiler furnace outlet flue gas temperature left 2 | 70HBB10CT104B | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
244 | 70HBB10CT104C | 锅炉炉膛出口烟气温度左3 | Boiler furnace outlet flue gas temperature left 3 | 70HBB10CT104C | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
245 | 70HBB10CT105A | 锅炉炉膛出口烟气温度右1 | Boiler furnace outlet flue gas temperature right 1 | 70HBB10CT105A | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
246 | 70HBB10CT105B | 锅炉炉膛出口烟气温度右2 | Boiler furnace outlet flue gas temperature right 2 | 70HBB10CT105B | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
247 | 70HBB10CT105C | 锅炉炉膛出口烟气温度右3 | Boiler furnace outlet flue gas temperature right 3 | 70HBB10CT105C | 4~20mA | AI | 0~1200 | ℃ | [8 empty] | FSSS | D |  | K0202-005
253 | 70HBB10CP001AHH | 锅炉炉膛出口压力高高1 | Boiler furnace outlet pressure HH 1 | 70HBB10CP001A | NO | DI | 2.5 | Kpa | [8 empty] | FSSS | D |  | K0202-005 | bar: HH
254 | 70HBB10CP001BHH | 锅炉炉膛出口压力高高2 | Boiler furnace outlet pressure HH 2 | 70HBB10CP001B | NO | DI | 2.5 | Kpa | [8 empty] | FSSS | D |  | K0202-005 | bar: HH
255 | 70HBB10CP001CHH | 锅炉炉膛出口压力高高3 | Boiler furnace outlet pressure HH 3 | 70HBB10CP001C | NO | DI | 2.5 | Kpa | [8 empty] | FSSS | D |  | K0202-005 | bar: HH
256 | 70HBB10CP002ALL | 锅炉炉膛出口压力低低1 | Boiler furnace outlet pressure LL 1 | 70HBB10CP002A | NO | DI | -2.5 | Kpa | [8 empty] | FSSS | D |  | K0202-005 | bar: LL
257 | 70HBB10CP002BLL | 锅炉炉膛出口压力低低2 | Boiler furnace outlet pressure LL 2 | 70HBB10CP002 | NO | DI | -2.5 | Kpa | [8 empty] | FSSS | D |  | K0202-005 | bar: LL
258 | 70HBB10CP002CLL | 锅炉炉膛出口压力低低3 | Boiler furnace outlet pressure LL 3 | 70HBB10CP002C | NO | DI | -2.5 | Kpa | [8 empty] | FSSS | D |  | K0202-005 | bar: LL
371 | 70HLA40CP101A | 1#风室热一次风压力1 | 1# wind box hot primary air pressure 1 | 70HLA40CP101A | 4~20mA | AI | 0~30 | KPa | [8 empty] | FSSS | D |  | K0202-008
372 | 70HLA40CP101B | 1#风室热一次风压力2 | 1# wind box hot primary air pressure 2 | 70HLA40CP101B | 4~20mA | AI | 0~30 | KPa | [8 empty] | FSSS | D |  | K0202-008
373 | 70HLA40CP101C | 1#风室热一次风压力3 | 1# wind box hot primary air pressure 3 | 70HLA40CP101C | 4~20mA | AI | 0~30 | KPa | [8 empty] | FSSS | D |  | K0202-008
374 | 70HLA50CP101A | 2#风室热一次风压力1 | 2# wind box hot primary air pressure 1 | 70HLA50CP101A | 4~20mA | AI | 0~30 | KPa | [8 empty] | FSSS | D |  | K0202-008
375 | 70HLA50CP101B | 2#风室热一次风压力2 | 2# wind box hot primary air pressure 2 | 70HLA50CP101B | 4~20mA | AI | 0~30 | KPa | [8 empty] | FSSS | D |  | K0202-008
376 | 70HLA50CP101C | 2#风室热一次风压力3 | 2# wind box hot primary air pressure 3 | 70HLA50CP101C | 4~20mA | AI | 0~30 | KPa | [8 empty] | FSSS | D |  | K0202-008
590 | 70HHL40CP002LL | 高压流化风机出口母管压力低低1 | High pressure fludized fan outlet main pipe pressure LL1 | 70HHL40CP002 | NO | DI | 20 | kPa | [8 empty] | FSSS | D |  | K0202-012 | bar: LL
591 | 70HHL40CP003LL | 高压流化风机出口母管压力低低2 | High pressure fludized fan outlet main pipe pressure LL2 | 70HHL40CP003 | NO | DI | 20 | kPa | [8 empty] | FSSS | D |  | K0202-012 | bar: LL
592 | 70HHL40CP004LL | 高压流化风机出口母管压力低低3 | High pressure fludized fan outlet main pipe pressure LL3 | 70HHL40CP004 | NO | DI | 20 | kPa | [8 empty] | FSSS | D |  | K0202-012 | bar: LL
647 | 70HFB60AF001YB01 | 污泥给料机启动指令 | Sludge feeder start command | 70HFB60GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
648 | 70HFB60AF001YB11 | 污泥给料机停止指令 | Sludge feeder stop command | 70HFB60GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
649 | 70HFB60AF001XB01 | 污泥给料机运行 | Sludge feeder running | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
650 | 70HFB60AF001XB02 | 污泥给料机清扫运行 | Sludge feeder sweeper running | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
651 | 70HFB60AF001XB03 | 污泥给料机容积输出显示 | Sludge feeder volume output display | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
652 | 70HFB60AF001XB11 | 污泥给料机停止信号 | Sludge feeder stopped signal | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
653 | 70HFB60AF001XB21 | 污泥给料机远控备妥 | Sludge feeder remote control already | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
654 | 70HFB60AF001XB31 | 污泥给料机电机故障 | Sludge feeder motor fault | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
655 | 70HFB60AF001XB32 | 污泥给料机清扫电机故障 | Sludge feeder sweeper motor fault | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
656 | 70HFB60AF001XB33 | 污泥给料机跑偏报警 | Sludge feeder offset alarm | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
657 | 70HFB60AF001XB34 | 污泥给料机出口堵料故障 | Sludge feeder exit blockage fault | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
658 | 70HFB60AF001XB35 | 污泥给料机断料故障 | Sludge feeder material-shortage | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
659 | 70HFB60AF001XB36 | 污泥给料机给料偏差报警 | Sludge feeder feed rate error | 70HFB60GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 污泥给料机控制柜 | Sludge feeder control cabinet
675 | 70HFB60AA001YB01 | 污泥给料机入口电动插板阀打开指令 | Sludge feeder inlet MOV open command | 70HFB60AA001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013
676 | 70HFB60AA001YB11 | 污泥给料机入口电动插板阀关闭指令 | Sludge feeder inlet MOV close command | 70HFB60AA001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013
677 | 70HFB60AA001XB01 | 污泥给料机入口电动插板阀全开状态 | Sludge feeder inlet MOV full opened status | 70HFB60AA001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013
678 | 70HFB60AA001XB11 | 污泥给料机入口电动插板阀全关 | Sludge feeder inlet MOV full closed status | 70HFB60AA001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013
679 | 70HFB60AA001XB21 | 污泥给料机入口电动插板阀远控允许 | Sludge feeder inlet MOV remote control permitted | 70HFB60AA001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013
680 | 70HFB60AA001XB31 | 污泥给料机入口电动插板阀故障 | Sludge feeder inlet MOV fault | 70HFB60AA001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013
681 | 70HFB10AF001YB01 | 1#给煤机启动指令 | 1# coal feeder start command | 70HFB10GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
682 | 70HFB10AF001YB11 | 1#给煤机停止指令 | 1# coal feeder stop command | 70HFB10GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
683 | 70HFB10AF001XB01 | 1#给煤机运行 | 1# coal feeder running | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
684 | 70HFB10AF001XB02 | 1#给煤机清扫运行 | 1# coal feeder sweeper running | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
685 | 70HFB10AF001XB03 | 1#给煤机容积输出显示 | 1# coal feeder volume output display | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
686 | 70HFB10AF001XB11 | 1#给煤机停止信号 | 1# coal feeder stopped signal | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
687 | 70HFB10AF001XB21 | 1#给煤机远控备妥 | 1# coal feeder remote control already | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
688 | 70HFB10AF001XB31 | 1#给煤机电机故障 | 1# coal feeder motor fault | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
689 | 70HFB10AF001XB32 | 1#给煤机清扫电机故障 | 1# coal feeder sweeper motor fault | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
690 | 70HFB10AF001XB33 | 1#给煤机跑偏报警 | 1# coal feeder offset alarm | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
691 | 70HFB10AF001XB34 | 1#给煤机出口堵料故障 | 1# coal feeder exit blockage fault | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
692 | 70HFB10AF001XB35 | 1#给煤机断料故障 | 1# coal feeder material-shortage | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
693 | 70HFB10AF001XB36 | 1#给煤机给料偏差报警 | 1# coal feeder feed rate error | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
694 | 70HFB10AF001XB37 | 1#给煤机超温故障 | 1# coal feeder over-temperature fault | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
695 | 70HFB10AF001XB38 | 1#给煤机进口煤流报警 | 1# coal feeder coal flow monitor alarm | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
700 | 70HFB10AA001YB01 | 1#给煤机进口电动闸阀打开指令 | 1# coal feeder inlet MOV open command | 70HFB10GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
701 | 70HFB10AA001YB11 | 1#给煤机进口电动闸阀关闭指令 | 1# coal feeder inlet MOV close command | 70HFB10GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
702 | 70HFB10AA001XB01 | 1#给煤机进口电动闸阀全开状态 | 1# coal feeder inlet MOV full opened status | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
703 | 70HFB10AA001XB11 | 1#给煤机进口电动闸阀全关状态 | 1# coal feeder inlet MOV full closed status | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
704 | 70HFB10AA001XB21 | 1#给煤机进口电动闸阀远控允许 | 1# coal feeder inlet MOV remote control permitted | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
705 | 70HFB10AA001XB31 | 1#给煤机进口电动闸阀故障 | 1# coal feeder inlet MOV fault | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
706 | 70HFB10AA002YB01 | 1#给煤机出口气动阀打开指令 | 1# coal feeder outlet PV open command | 70HFB10GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
707 | 70HFB10AA002YB11 | 1#给煤机出口气动阀关闭指令 | 1# coal feeder outlet PV close command | 70HFB10GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
708 | 70HFB10AA002XB01 | 1#给煤机出口气动阀全开状态 | 1# coal feeder outlet PV full opened status | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
709 | 70HFB10AA002XB11 | 1#给煤机出口气动阀全关状态 | 1# coal feeder outlet PV full closed status | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
710 | 70HFB10AA002XB21 | 1#给煤机出口气动阀远控允许 | 1# coal feeder outlet PV remote control permitted | 70HFB10GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 1#给煤机控制柜 | 1# coal feeder control cabinet
711 | 70HFB20AF001YB01 | 2#给煤机启动指令 | 2# coal feeder start command | 70HFB20GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
712 | 70HFB20AF001YB11 | 2#给煤机停止指令 | 2# coal feeder stop command | 70HFB20GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
713 | 70HFB20AF001XB01 | 2#给煤机运行 | 2# coal feeder running | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
714 | 70HFB20AF001XB02 | 2#给煤机清扫运行 | 2# coal feeder sweeper running | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
715 | 70HFB20AF001XB03 | 2#给煤机容积输出显示 | 2# coal feeder volume output display | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
716 | 70HFB20AF001XB11 | 2#给煤机停止信号 | 2# coal feeder stopped signal | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
717 | 70HFB20AF001XB21 | 2#给煤机远控备妥 | 2# coal feeder remote control already | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
718 | 70HFB20AF001XB31 | 2#给煤机电机故障 | 2# coal feeder motor fault | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
719 | 70HFB20AF001XB32 | 2#给煤机清扫电机故障 | 2# coal feeder sweeper motor fault | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
720 | 70HFB20AF001XB33 | 2#给煤机跑偏报警 | 2# coal feeder offset alarm | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
721 | 70HFB20AF001XB34 | 2#给煤机出口堵料故障 | 2# coal feeder exit blockage fault | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
722 | 70HFB20AF001XB35 | 2#给煤机断料故障 | 2# coal feeder material-shortage | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
723 | 70HFB20AF001XB36 | 2#给煤机给料偏差报警 | 2# coal feeder feed rate error | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
724 | 70HFB20AF001XB37 | 2#给煤机超温故障 | 2# coal feeder over-temperature fault | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
725 | 70HFB20AF001XB38 | 2#给煤机进口煤流报警 | 2# coal feeder coal flow monitor alarm | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
730 | 70HFB20AA001YB01 | 2#给煤机进口电动闸阀打开指令 | 2# coal feeder inlet MOV open command | 70HFB20GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
731 | 70HFB20AA001YB11 | 2#给煤机进口电动闸阀关闭指令 | 2# coal feeder inlet MOV close command | 70HFB20GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
732 | 70HFB20AA001XB01 | 2#给煤机进口电动闸阀全开状态 | 2# coal feeder inlet MOV full opened status | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
733 | 70HFB20AA001XB11 | 2#给煤机进口电动闸阀全关状态 | 2# coal feeder inlet MOV full closed status | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
734 | 70HFB20AA001XB21 | 2#给煤机进口电动闸阀远控允许 | 2# coal feeder inlet MOV remote control permitted | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
735 | 70HFB20AA001XB31 | 2#给煤机进口电动闸阀故障 | 2# coal feeder inlet MOV fault | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
736 | 70HFB20AA002YB01 | 2#给煤机出口气动阀打开指令 | 2# coal feeder outlet PV open command | 70HFB20GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
737 | 70HFB20AA002YB11 | 2#给煤机出口气动阀关闭指令 | 2# coal feeder outlet PV close command | 70HFB20GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
738 | 70HFB20AA002XB01 | 2#给煤机出口气动阀全开状态 | 2# coal feeder outlet PV full opened status | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
739 | 70HFB20AA002XB11 | 2#给煤机出口气动阀全关状态 | 2# coal feeder outlet PV full closed status | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
740 | 70HFB20AA002XB21 | 2#给煤机出口气动阀远控允许 | 2# coal feeder outlet PV remote control permitted | 70HFB20GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 2#给煤机控制柜 | 2# coal feeder control cabinet
741 | 70HFB30AF001YB01 | 3#给煤机启动指令 | 3# coal feeder start command | 70HFB30GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
742 | 70HFB30AF001YB11 | 3#给煤机停止指令 | 3# coal feeder stop command | 70HFB30GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
743 | 70HFB30AF001XB01 | 3#给煤机运行 | 3# coal feeder running | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
744 | 70HFB30AF001XB02 | 3#给煤机清扫运行 | 3# coal feeder sweeper running | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
745 | 70HFB30AF001XB03 | 3#给煤机容积输出显示 | 3# coal feeder volume output display | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
746 | 70HFB30AF001XB11 | 3#给煤机停止信号 | 3# coal feeder stopped signal | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
747 | 70HFB30AF001XB21 | 3#给煤机远控备妥 | 3# coal feeder remote control already | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
748 | 70HFB30AF001XB31 | 3#给煤机电机故障 | 3# coal feeder motor fault | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
749 | 70HFB30AF001XB32 | 3#给煤机清扫电机故障 | 3# coal feeder sweeper motor fault | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
750 | 70HFB30AF001XB33 | 3#给煤机跑偏报警 | 3# coal feeder offset alarm | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
751 | 70HFB30AF001XB34 | 3#给煤机出口堵料故障 | 3# coal feeder exit blockage fault | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
752 | 70HFB30AF001XB35 | 3#给煤机断料故障 | 3# coal feeder material-shortage | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
753 | 70HFB30AF001XB36 | 3#给煤机给料偏差报警 | 3# coal feeder feed rate error | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
754 | 70HFB30AF001XB37 | 3#给煤机超温故障 | 3# coal feeder over-temperature fault | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
755 | 70HFB30AF001XB38 | 3#给煤机进口煤流报警 | 3# coal feeder coal flow monitor alarm | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
760 | 70HFB30AA001YB01 | 3#给煤机进口电动闸阀打开指令 | 3# coal feeder inlet MOV open command | 70HFB30GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
761 | 70HFB30AA001YB11 | 3#给煤机进口电动闸阀关闭指令 | 3# coal feeder inlet MOV close command | 70HFB30GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
762 | 70HFB30AA001XB01 | 3#给煤机进口电动闸阀全开状态 | 3# coal feeder inlet MOV full opened status | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
763 | 70HFB30AA001XB11 | 3#给煤机进口电动闸阀全关状态 | 3# coal feeder inlet MOV full closed status | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
764 | 70HFB30AA001XB21 | 3#给煤机进口电动闸阀远控允许 | 3# coal feeder inlet MOV remote control permitted | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
765 | 70HFB30AA001XB31 | 3#给煤机进口电动闸阀故障 | 3# coal feeder inlet MOV fault | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
766 | 70HFB30AA002YB01 | 3#给煤机出口气动阀打开指令 | 3# coal feeder outlet PV open command | 70HFB30GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
767 | 70HFB30AA002YB11 | 3#给煤机出口气动阀关闭指令 | 3# coal feeder outlet PV close command | 70HFB30GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
768 | 70HFB30AA002XB01 | 3#给煤机出口气动阀全开状态 | 3# coal feeder outlet PV full opened status | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
769 | 70HFB30AA002XB11 | 3#给煤机出口气动阀全关状态 | 3# coal feeder outlet PV full closed status | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
770 | 70HFB30AA002XB21 | 3#给煤机出口气动阀远控允许 | 3# coal feeder outlet PV remote control permitted | 70HFB30GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 3#给煤机控制柜 | 3# coal feeder control cabinet
771 | 70HFB40AF001YB01 | 4#给煤机启动指令 | 4# coal feeder start command | 70HFB40GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
772 | 70HFB40AF001YB11 | 4#给煤机停止指令 | 4# coal feeder stop command | 70HFB40GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
773 | 70HFB40AF001XB01 | 4#给煤机运行 | 4# coal feeder running | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
774 | 70HFB40AF001XB02 | 4#给煤机清扫运行 | 4# coal feeder sweeper running | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
775 | 70HFB40AF001XB03 | 4#给煤机容积输出显示 | 4# coal feeder volume output display | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
776 | 70HFB40AF001XB11 | 4#给煤机停止信号 | 4# coal feeder stopped signal | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
777 | 70HFB40AF001XB21 | 4#给煤机远控备妥 | 4# coal feeder remote control already | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
778 | 70HFB40AF001XB31 | 4#给煤机电机故障 | 4# coal feeder motor fault | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
779 | 70HFB40AF001XB32 | 4#给煤机清扫电机故障 | 4# coal feeder sweeper motor fault | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
780 | 70HFB40AF001XB33 | 4#给煤机跑偏报警 | 4# coal feeder offset alarm | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
781 | 70HFB40AF001XB34 | 4#给煤机出口堵料故障 | 4# coal feeder exit blockage fault | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
782 | 70HFB40AF001XB35 | 4#给煤机断料故障 | 4# coal feeder material-shortage | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
783 | 70HFB40AF001XB36 | 4#给煤机给料偏差报警 | 4# coal feeder feed rate error | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
784 | 70HFB40AF001XB37 | 4#给煤机超温故障 | 4# coal feeder over-temperature fault | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
785 | 70HFB40AF001XB38 | 4#给煤机进口煤流报警 | 4# coal feeder coal flow monitor alarm | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
790 | 70HFB40AA001YB01 | 4#给煤机进口电动闸阀打开指令 | 4# coal feeder inlet MOV open command | 70HFB40GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
791 | 70HFB40AA001YB11 | 4#给煤机进口电动闸阀关闭指令 | 4# coal feeder inlet MOV close command | 70HFB40GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
792 | 70HFB40AA001XB01 | 4#给煤机进口电动闸阀全开状态 | 4# coal feeder inlet MOV full opened status | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
793 | 70HFB40AA001XB11 | 4#给煤机进口电动闸阀全关状态 | 4# coal feeder inlet MOV full closed status | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
794 | 70HFB40AA001XB21 | 4#给煤机进口电动闸阀远控允许 | 4# coal feeder inlet MOV remote control permitted | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
795 | 70HFB40AA001XB31 | 4#给煤机进口电动闸阀故障 | 4# coal feeder inlet MOV fault | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
796 | 70HFB40AA002YB01 | 4#给煤机出口气动阀打开指令 | 4# coal feeder outlet PV open command | 70HFB40GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
797 | 70HFB40AA002YB11 | 4#给煤机出口气动阀关闭指令 | 4# coal feeder outlet PV close command | 70HFB40GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
798 | 70HFB40AA002XB01 | 4#给煤机出口气动阀全开状态 | 4# coal feeder outlet PV full opened status | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
799 | 70HFB40AA002XB11 | 4#给煤机出口气动阀全关状态 | 4# coal feeder outlet PV full closed status | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
800 | 70HFB40AA002XB21 | 4#给煤机出口气动阀远控允许 | 4# coal feeder outlet PV remote control permitted | 70HFB40GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 4#给煤机控制柜 | 4# coal feeder control cabinet
801 | 70HFB50AF001YB01 | 5#给煤机启动指令 | 5# coal feeder start command | 70HFB50GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
802 | 70HFB50AF001YB11 | 5#给煤机停止指令 | 5# coal feeder stop command | 70HFB50GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
803 | 70HFB50AF001XB01 | 5#给煤机运行 | 5# coal feeder running | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
804 | 70HFB50AF001XB02 | 5#给煤机清扫运行 | 5# coal feeder sweeper running | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
805 | 70HFB50AF001XB03 | 5#给煤机容积输出显示 | 5# coal feeder volume output display | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
806 | 70HFB50AF001XB11 | 5#给煤机停止信号 | 5# coal feeder stopped signal | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
807 | 70HFB50AF001XB21 | 5#给煤机远控备妥 | 5# coal feeder remote control already | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
808 | 70HFB50AF001XB31 | 5#给煤机电机故障 | 5# coal feeder motor fault | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
809 | 70HFB50AF001XB32 | 5#给煤机清扫电机故障 | 5# coal feeder sweeper motor fault | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
810 | 70HFB50AF001XB33 | 5#给煤机跑偏报警 | 5# coal feeder offset alarm | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
811 | 70HFB50AF001XB34 | 5#给煤机出口堵料故障 | 5# coal feeder exit blockage fault | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
812 | 70HFB50AF001XB35 | 5#给煤机断料故障 | 5# coal feeder material-shortage | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
813 | 70HFB50AF001XB36 | 5#给煤机给料偏差报警 | 5# coal feeder feed rate error | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
814 | 70HFB50AF001XB37 | 5#给煤机超温故障 | 5# coal feeder over-temperature fault | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
815 | 70HFB50AF001XB38 | 5#给煤机进口煤流报警 | 5# coal feeder coal flow monitor alarm | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
820 | 70HFB50AA001YB01 | 5#给煤机进口电动闸阀打开指令 | 5# coal feeder inlet MOV open command | 70HFB50GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
821 | 70HFB50AA001YB11 | 5#给煤机进口电动闸阀关闭指令 | 5# coal feeder inlet MOV close command | 70HFB50GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
822 | 70HFB50AA001XB01 | 5#给煤机进口电动闸阀全开状态 | 5# coal feeder inlet MOV full opened status | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
823 | 70HFB50AA001XB11 | 5#给煤机进口电动闸阀全关状态 | 5# coal feeder inlet MOV full closed status | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
824 | 70HFB50AA001XB21 | 5#给煤机进口电动闸阀远控允许 | 5# coal feeder inlet MOV remote control permitted | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
825 | 70HFB50AA001XB31 | 5#给煤机进口电动闸阀故障 | 5# coal feeder inlet MOV fault | 70HFB50GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 5#给煤机控制柜 | 5# coal feeder control cabinet
826 | 70HFB70AF001YB01 | 埋刮板输送机启动指令 | Embed belt coal conveyor start command | 70HFB70GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
827 | 70HFB70AF001YB11 | 埋刮板输送机停止指令 | Embed belt coal conveyor stop command | 70HFB70GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
828 | 70HFB70AF001XB01 | 埋刮板输送机运行 | Embed belt coal conveyor running | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
829 | 70HFB70AF001XB21 | 埋刮板输送机远控备妥 | Embed belt coal conveyor remote control already | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
830 | 70HFB70AF001XB31 | 埋刮板输送机故障 | Embed belt coal conveyor fault | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
831 | 70HFB70AF001XB32 | 埋刮板输送机断料报警 | Embed belt coal conveyor material-shortage alarm | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
832 | 70HFB71AF001YB01 | 1#螺旋给料机启动指令 | 1# screw feeder start command | 70HFB70GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
833 | 70HFB71AF001YB11 | 1#螺旋给料机停止指令 | 1# screw feeder stop command | 70HFB70GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
834 | 70HFB71AF001XB01 | 1#螺旋给料机运行 | 1# screw feeder running | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
835 | 70HFB71AF001XB21 | 1#螺旋给料机远控备妥 | 1# screw feeder remote control already | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
836 | 70HFB71AF001XB31 | 1#螺旋给料机故障 | 1# screw feeder fault | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
837 | 70HFB72AF001YB01 | 2#螺旋给料机启动指令 | 2# screw feeder start command | 70HFB70GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
838 | 70HFB72AF001YB11 | 2#螺旋给料机停止指令 | 2# screw feeder stop command | 70HFB70GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
839 | 70HFB72AF001XB01 | 2#螺旋给料机运行 | 2# screw feeder running | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
840 | 70HFB72AF001XB21 | 2#螺旋给料机远控备妥 | 2# screw feeder remote control already | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
841 | 70HFB72AF001XB31 | 2#螺旋给料机故障 | 2# screw feeder fault | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
842 | 70HFB71AA001YB01 | 1#螺旋给料机出口气动阀打开指令 | 1# screw feeder outlet PV open command | 70HFB70GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
843 | 70HFB71AA001YB11 | 1#螺旋给料机出口气动阀关闭指令 | 1# screw feeder outlet PV close command | 70HFB70GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
844 | 70HFB71AA001XB01 | 1#螺旋给料机出口气动阀全开状态 | 1# screw feeder outlet PV full opened status | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
845 | 70HFB71AA001XB11 | 1#螺旋给料机出口气动阀全关状态 | 1# screw feeder outlet PV full closed status | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
846 | 70HFB71AA001XB21 | 1#螺旋给料机出口气动阀远控允许 | 1# screw feeder outlet PV remote control permitted | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
847 | 70HFB72AA001YB01 | 2#螺旋给料机出口气动阀打开指令 | 2# screw feeder outlet PV open command | 70HFB70GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
848 | 70HFB72AA001YB11 | 2#螺旋给料机出口气动阀关闭指令 | 2# screw feeder outlet PV close command | 70HFB70GH001 | NO | DO | [10 empty] | FSSS | U | 220VAC | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
849 | 70HFB72AA001XB01 | 2#螺旋给料机出口气动阀全开状态 | 2# screw feeder outlet PV full opened status | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
850 | 70HFB72AA001XB11 | 2#螺旋给料机出口气动阀全关状态 | 2# screw feeder outlet PV full closed status | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet
851 | 70HFB72AA001XB21 | 2#螺旋给料机出口气动阀远控允许 | 2# screw feeder outlet PV remote control permitted | 70HFB70GH001 | NO | DI | [10 empty] | FSSS | D |  | K0202-013 | 埋刮板输送机控制柜 | Embed belt coal conveyor control cabinet

## IO分配表
| N1S1 | N2S1 | N3S1 | N1S4 | N2S4 | N1S2 | N1S3 | N2S2 | N2S3
1 | 70HJF10CP101 | 70HJF20CP101 | 70HJF20CF101 | 70HFB10AF001YB01 | 70HFB30AF001YB01 | 70HFB10AF001XB01 | 70HFB20AF001XB01 | 70HFB30AF001XB01 | 70HFB40AF001XB01
2 | 70HBB10CT101A | 70HBB10CT101B | 70HBB10CT101C | 70HFB10AF001YB11 | 70HFB30AF001YB11 | 70HFB10AF001XB02 | 70HFB20AF001XB02 | 70HFB30AF001XB02 | 70HFB40AF001XB02
3 | 70HBB10CT101D | 70HBB10CT101E | 70HBB10CT101F | 70HFB10AA001YB01 | 70HFB30AA001YB01 | 70HFB10AF001XB03 | 70HFB20AF001XB03 | 70HFB30AF001XB03 | 70HFB40AF001XB03
4 | 70HBB10CT101G | 70HBB10CT101H |  | 70HFB10AA001YB11 | 70HFB30AA001YB11 | 70HFB10AF001XB11 | 70HFB20AF001XB11 | 70HFB30AF001XB11 | 70HFB40AF001XB11
5 | 70HBB10CT104A | 70HBB10CT104B | 70HBB10CT104C | 70HFB10AA002YB01 | 70HFB30AA002YB01 | 70HFB10AF001XB21 | 70HFB20AF001XB21 | 70HFB30AF001XB21 | 70HFB40AF001XB21
6 | 70HBB10CT105A | 70HBB10CT105B | 70HBB10CT105C | 70HFB10AA002YB11 | 70HFB30AA002YB11 | 70HFB10AF001XB31 | 70HFB20AF001XB31 | 70HFB30AF001XB31 | 70HFB40AF001XB31
7 | 70HLA40CP101A | 70HLA40CP101B | 70HLA40CP101C | 70HFB20AF001YB01 | 70HFB40AF001YB01 | 70HFB10AF001XB32 | 70HFB20AF001XB32 | 70HFB30AF001XB32 | 70HFB40AF001XB32
8 | 70HLA50CP101A | 70HLA50CP101B | 70HLA50CP101C | 70HFB20AF001YB11 | 70HFB40AF001YB11 | 70HFB10AF001XB33 | 70HFB20AF001XB33 | 70HFB30AF001XB33 | 70HFB40AF001XB33
9 | 70HJF11CB101XQ01 | 70HJF13CB101XQ01 | 70HJF15CB101XQ01 | 70HFB20AA001YB01 | 70HFB40AA001YB01 | 70HFB10AF001XB34 | 70HFB20AF001XB34 | 70HFB30AF001XB34 | 70HFB40AF001XB34
10 | 70HJF12CB101XQ01 | 70HJF14CB101XQ01 |  | 70HFB20AA001YB11 | 70HFB40AA001YB11 | 70HFB10AF001XB35 | 70HFB20AF001XB35 | 70HFB30AF001XB35 | 70HFB40AF001XB35
11 |  |  |  | 70HFB20AA002YB01 | 70HFB40AA002YB01 | 70HFB10AF001XB36 | 70HFB20AF001XB36 | 70HFB30AF001XB36 | 70HFB40AF001XB36
12 |  |  |  | 70HFB20AA002YB11 | 70HFB40AA002YB11 | 70HFB10AF001XB37 | 70HFB20AF001XB37 | 70HFB30AF001XB37 | 70HFB40AF001XB37
13 |  |  |  | 70HFB60AF001YB01 | 70HFB60AA001YB01 | 70HFB10AF001XB38 | 70HFB20AF001XB38 | 70HFB30AF001XB38 | 70HFB40AF001XB38
14 |  |  |  | 70HFB60AF001YB11 | 70HFB60AA001YB11 | 70HFB10AA001XB01 | 70HFB20AA001XB01 | 70HFB30AA001XB01 | 70HFB40AA001XB01
15 | [5 empty] | 70HFB10AA001XB11 | 70HFB20AA001XB11 | 70HFB30AA001XB11 | 70HFB40AA001XB11
16 | [5 empty] | 70HFB10AA001XB21 | 70HFB20AA001XB21 | 70HFB30AA001XB21 | 70HFB40AA001XB21
17 | [5 empty] | 70HFB10AA001XB31 | 70HFB20AA001XB31 | 70HFB30AA001XB31 | 70HFB40AA001XB31
18 | [5 empty] | 70HFB10AA002XB01 | 70HFB20AA002XB01 | 70HFB30AA002XB01 | 70HFB40AA002XB01
19 | [5 empty] | 70HFB10AA002XB11 | 70HFB20AA002XB11 | 70HFB30AA002XB11 | 70HFB40AA002XB11
20 | [5 empty] | 70HFB10AA002XB21 | 70HFB20AA002XB21 | 70HFB30AA002XB21 | 70HFB40AA002XB21
21 | [5 empty] | 70HFB60AF001XB01 | 70HFB60AF001XB31 | 70HFB60AA001XB01 | 70HBB10CP001AHH
22 | [5 empty] | 70HFB60AF001XB02 | 70HFB60AF001XB32 | 70HFB60AA001XB11 | 70HBB10CP001BHH
23 | [5 empty] | 70HFB60AF001XB03 | 70HFB60AF001XB33 | 70HFB60AA001XB21 | 70HBB10CP001CHH
24 | [5 empty] | 70HFB60AF001XB11 | 70HFB60AF001XB34 | 70HFB60AA001XB31 | 70HBB10CP002ALL
25 | [5 empty] | 70HFB60AF001XB21 | 70HFB60AF001XB35 | 70HHL40CP002LL | 70HBB10CP002BLL
26 | [6 empty] | 70HFB60AF001XB36 | 70HHL40CP003LL | 70HBB10CP002CLL
27 | [7 empty] | 70HHL40CP004LL
28
29
30
31
32
|  |  |  | N3S5 |  |  | N3S2 | N3S3 | N3S4
|  |  |  | 70HFB50AF001YB01 |  |  | 70HFB50AF001XB01 | 70HFB70AF001XB01 | 70HJF11AA001XB12
|  |  |  | 70HFB50AF001YB11 |  |  | 70HFB50AF001XB02 | 70HFB70AF001XB21 | 70HJF11AA002XB12
|  |  |  | 70HFB50AA001YB01 |  |  | 70HFB50AF001XB03 | 70HFB70AF001XB31 | 70HJF11CB101XB02
|  |  |  | 70HFB50AA001YB11 |  |  | 70HFB50AF001XB11 | 70HFB70AF001XB32 | 70HJF12AA001XB12
|  |  |  | 70HFB70AF001YB01 |  |  | 70HFB50AF001XB21 | 70HFB71AF001XB01 | 70HJF12AA002XB12
|  |  |  | 70HFB70AF001YB11 |  |  | 70HFB50AF001XB31 | 70HFB71AF001XB21 | 70HJF12CB101XB02
|  |  |  | 70HFB71AF001YB01 |  |  | 70HFB50AF001XB32 | 70HFB71AF001XB31 | 70HJF13AA001XB12
|  |  |  | 70HFB71AF001YB11 |  |  | 70HFB50AF001XB33 | 70HFB72AF001XB01 | 70HJF13AA002XB12
|  |  |  | 70HFB72AF001YB01 |  |  | 70HFB50AF001XB34 | 70HFB72AF001XB21 | 70HJF13CB101XB02
|  |  |  | 70HFB72AF001YB11 |  |  | 70HFB50AF001XB35 | 70HFB72AF001XB31 | 70HJF14AA001XB12
|  |  |  | 70HFB71AA001YB01 |  |  | 70HFB50AF001XB36 | 70HFB71AA001XB01 | 70HJF14AA002XB12
|  |  |  | 70HFB71AA001YB11 |  |  | 70HFB50AF001XB37 | 70HFB71AA001XB11 | 70HJF14CB101XB02
|  |  |  | 70HFB72AA001YB01 |  |  | 70HFB50AF001XB38 | 70HFB71AA001XB21 | 70HJF15AA001XB12
|  |  |  | 70HFB72AA001YB11 |  |  | 70HFB50AA001XB01 | 70HFB72AA001XB01 | 70HJF15AA002XB12
|  |  |  | 70HJF11GH001YB01 |  |  | 70HFB50AA001XB11 | 70HFB72AA001XB11 | 70HJF15CB101XB02
|  |  |  | 70HJF11GH001YB11 |  |  | 70HFB50AA001XB21 | 70HFB72AA001XB21 | 70HJF11CB101XB03
|  |  |  | 70HJF12GH001YB01 |  |  | 70HFB50AA001XB31 | 70HJF10GH003YB01 | 70HJF12CB101XB03
|  |  |  | 70HJF12GH001YB11 |  |  | 70HJF10AA001XB12 | 70HJF10GH003YB02 | 70HJF13CB101XB03
|  |  |  | 70HJF13GH001YB01 |  |  | 70HJF21AA001XB12 | 70HJF10GH003YB03 | 70HJF14CB101XB03
|  |  |  | 70HJF13GH001YB11 |  |  | 70HJF22AA001XB12 | 70HJF10GH003YB04 | 70HJF15CB101XB03
|  |  |  | 70HJF14GH001YB01 |  |  | 70HJF23AA001XB12 | 70HJF10GH003YB05
|  |  |  | 70HJF14GH001YB11 |  |  | 70HJF24AA001XB12 | 70HJF10GH003YB06
|  |  |  | 70HJF15GH001YB01 |  |  | 70HJF25AA001XB12 | 70HJF10GH003YB07
|  |  |  | 70HJF15GH001YB11 |  |  |  | 70HJF10GH003YB08
|  |  |  | 70HJF10GH003XB02 |  |  |  | 70HJF10GH003YB09
|  |  |  | 70HJF10GH003XB03 |  |  |  | 70HJF10GH003YB10

## 卡件布置
| Node | Slot
AAI143 | 1 | 1
ADV151 | 1 | 2
ADV151 | 1 | 3
ADV551 | 1 | 4
AAI143 | 2 | 1
ADV151 | 2 | 2
ADV151 | 2 | 3
ADV551 | 2 | 4
ALP121 | 2 | 7 | Y
AAI143 | 3 | 1
ADV151 | 3 | 2
ADV151 | 3 | 3
ADV151 | 3 | 4
ADV551 | 3 | 5
ALE111 | 3 | 7 | Y