## SE5
PJT Doc. No. PJ-ZHYXSY-CN20NSA0702-C15-01 SE5 Checklist - Internal Test
Template Revision History
| Rev. Nr. | Date | By | Approved |  |  |  | Description
| R00.01 | 2011-08-25 | N.Senga / YHQ | EP Network
| R01.00 | 2011-12-01 | K.Maeda / YEF | EP Network |  |  |  | Reviewed and revised with the latest information
| R02.00 | 2012-02-15 | K.Maeda / YEF | EP Network |  |  |  | Added Revision History
| R03.00 | 2013-04-16 | GH. Tan /CEC-S | EP Network |  |  |  | Incorporated YCA and CEC-S comments
(added item 1.3.2, 1.3.3, 1.3.7, 2.3.5, section 2.2,
added section 4.5 for CAMS, section 5 for batch,
section 6.2 to 6.4 for subsystem interface test (moved from SE6),
section 7 for non-DCS items,, section 8.3 to 8.5 for FAT reporting (moved from SE6))
| R03.01 | 2013-06-10 | Ramprasad B/ YMA | EP Network |  |  |  | Incorporated YEF-GB & YMA comments
(added item 2.1.11, 2.7.4, 4.4.7)
| R03.02 | 2013-11-04 | M.Latocha / YEF-G |  |  |  |  | Incorporated YEF-G & YMQ comments
(added item 5.1.11, 5.1.12, 5.1.13, 5.1.14)
| R03.03 | 2013-11-13 | M.Latocha / YEF-G |  |  |  |  | Incorporated YEF-G & YMQ comments
(added item 5.1.15 and modified section 5.1 grammatically)
| R03.04 | 2014-03-20 | D. Christie / YCA AEC | Batch G-SME Ozaku |  |  |  | Added Items 5.1.9 and 5.1.10. Moved remaining items in Section 5.1 down accordingly
| R03.05 | 2014-11-26 | H.Usami / YHQ | EP & Batch GSME |  |  |  | The items for batch ( Section 5 ) was divided into another sheet by YEF's comment.
Corrected mistake 4.2.7 ,
Modified item 2.1.6 , 2.2.2 , 3.2.2 , 7.1.1 , 7.2.1 , 7.3.1 , 7.4.1 , 7.5.1 , 7.6.1
Deleted 3.3.1 ( Move to SE4 3.1.23 ) , 3.2.1 ( Move to SE4-3.1.24)
| R03.06 | 2016-03-28 | Y.Yamada/CEC-T | N/A |  |  |  | Updated the old link in 1.1.3, 1.2.1.
| ENDUSER | :有行鲨鱼（珠海）新材料科技有限公司
| CUSTOMER | :有行鲨鱼（珠海）新材料科技有限公司
| CONSULTANT | :
| PROJECT NAME | : 有行鲨鱼珠海新材料科技有限公司化学胶粘剂DCS项目
| PROJECT NUMBER | :CN20NSA0702
| Name of Participants | :
| Reviewed by / date | :
| Approved by / date | :
Number of Failure Items
Number of Attention Items
Number of OK Items
Number of NA Items
Note : The number mentioned above is the sum of this sheet and batch sheet if your project uses batch sheet.
Outline
This phase starts from staging of the system to prepare for the FAT till the commencement of FAT.
The main task of this phase is to ensure that the hardware staged and software engineered is ready for FAT in all respects and the documentation for commencing the FAT is also in place.
This phase is not intended to 100% test all software applications but rather focus on modular integration test. Individual loops shall be debugged and fully tested during the Implementation Phase.
Participants
- Project Manager / Engineering Manager
- Technical Reviewer
- Lead System Engineer(s)
- System Engineers(s)
- QA Manager
Usage
The check items in this checklist provide general guidance for system design and project execution.
The questions associated with each check item are intended to guide the user towards details that may be applicable for the project.
The project team shall report the evaluation of each check item, comments pertaining to this (if any), and follow-up action (if any).
The completed check list is an indication that the project team has carried out the recommended checks for this milestone.
Project documentation that is used during the check shall be mentioned in the remarks or comments field (Title and Revision).
Meeting Initiation
Project Manager / Engineering Manager shall schedule and initiate this milestone check.
Evaluation of check items
Each check item should result in one of the following evaluation results:
Fail (FL)
The check item is not satisfactory. Follow up action is required.
Follow up actions shall include what needs to be done, who is to do it,
and when it must be completed. The Project Manager / Engineering Manager is ultimately responsible for the closure of follow up actions. Add comments if any.
Attention (AT)
This item needs some attention. Add comments if any.
Satisfactory (OK)
The check item is satisfactory. Add comments if any.
Not Applicable (NA)
The check item is not applicable. Add comments if any.
a
a
a | SE5
a
a
a
a | -5 | ARCHITECTURE
a | 1899-12-31 02:24 | Visual Inspection
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 1.1.1 | Will you be staging all the PCs for HIS, EWS, PRM, advanced controls, PIMS, EXAOPC etc. shown in the system configuration? |  |  |  | 1
a | 1.1.2 | Are Operating Systems newly installed to all the target PCs properly? Pre- installed OS is not acceptable. i Refer to "Selection web". (http://globalcyber.jp.ykgw.net/PMK/Selection-e/selection-e.htm) |  |  |  | 1
a | 1.1.3 | Have you used correct version of service pack and confirmed the current MS patches for the PCs?. i Tested MS patches can be obtained through the following website. (http://adm402-sitc001.gbl.ykgw.net/sites/security2012/avos/AVOS%20Download%20Center/Download_AVOS.html) * The latest tested MS patches are listed in section 03 "Validation Reports". |  |  |  | 1
a | 1.1.4 | Have you checked if the service pack of the OS is compatible with the application software? Refer software installation manual for revision. |  |  |  | 1
a | 1.1.5 | Is the OS media available along with the PC hardware? |  |  |  | 1
a | 1.1.6 | Is their any hard disk partitioning philosophy worked out for all the PCs? |  |  |  | 1
a | 1.1.7 | Have you determined the PCI slot for installing the Vnet / Vnet/IP card and installed with proper DIP switch setting? |  |  |  | 1
a | 1.1.8 | Are computer names for the PCs on the network as per design? HIS shall have HISddss as computer name. All other PCs shall preferably have STNddss as computer name. |  |  |  | 1
a | 1.1.9 | Does the Windows OS require activation and have you kept the record of activation code? |  |  |  | 1
a | 1.1.10 | Have you checked the event log for any error messages or abnormalities during OS installation? | No |  |  | 1
a | 1.1.11 | Have you made a ghost image of the hard disk to save time/effort during re-installation of OS? |  |  |  | 1
a
a
a | 1899-12-31 04:48 | Network Address
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 1.2.1 | Have you installed the Open Bus and Control Bus drivers from the proper revision system installation media? The drivers should not be installed from the New hardware wizard appearing when the PC is restarted after installation of VF/ VI card. If a separate Ethernet for Information Network is used, Vnet/IP open should be disabled. Refer the Vnet /IP construction guideline section 1.5 and 1.6 for more details. (http://inquiry.gbl.ykgw.net/sys-inq-en/pdf/CENTUM/VP%20R5/TI/TI30A10A05-01E_003.pdf) |  |  |  | 1
a | 1.2.2 | Have you configured higher access priority to Open Bus than Control bus in the advanced settings? |  |  |  | 1
a | 1.2.3 | Have you configured the IP address / Subnet mask / Default Gateway address for the open bus as per the FDS? |  |  |  | 1
a | 1.2.4 | Have you configured the IP address / Subnet mask / Default Gateway address for the control bus as per the FDS? |  |  |  | 1
a | 1.2.5 | Is the network adaptor name for the Open bus and control bus mentioned as per the FDS? |  |  |  | 1
a | 1.2.6 | Have the L2 and L3 switches been configured as per the requirement of Vnet/IP? Even though the out of the box manufacturer configuration works, the switches must be examined to comply to the Vnet/IP requirement? |  |  |  | 1
a
a
a | 1899-12-31 07:12 | System Protection and Backup
| S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 1.3.1 | Have you set the password for the internal test system in order to protect it from unauthorized access? |  |  |  | 1
a | 1.3.2 | Have you installed the Antivirus software on all the HIS’s, PC’s, servers? | No |  |  |  | 1
a | 1.3.3 | Have you taken the following measures to prevent virus attack? * Download the latest virus definition file and OS patches. * Scan the target and in-house system for virus. *Document the virus scan result.  Log book shall be signed and kept for audit | No |  |  |  | 1
| 1.3.4 | Is the PC scanned for virus regularly with updates? | No |  |  |  | 1
a | 1.3.5 | Have you planned a daily backup for the project database? This backup should be located in the hard disk of another PC and not the PC where the project DB exists. |  |  |  | 1
a | 1.3.6 | Have you done weekly backup on removable media such as DAT tape and stored them at a separate place from staging area? Some projects have contractual requirement to protect the project database at an offsite location for security and fire protection. Verify if this is required. |  |  |  | 1
a | 1.3.7 | If project supply Access Control package, is it being used to manage the access of engineering database? (Engineering builder, Report package, Batch recipe package) |  |  |  |  | 1
a
a
a | 1900-01-01 | SYSTEM
a | 1900-01-01 02:24 | DCS Software Installation/Verification
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 2.1.1 | Will you be conducting the FAT using the target software packages? It is preferable to conduct the FAT with target keycodes in order to avoid using functions eventually not available to customer. |  |  |  | 1
a | 2.1.2 | Have you studied the installation manual and taken note of all the precautions before the installation? |  |  |  | 1
a | 2.1.3 | Have you checked the installation log of each HIS to ensure that there are no system installation errors? |  |  |  | 1
a | 2.1.4 | Have you specified correct master database reference HIS during system installation?. |  |  |  | 1
a | 2.1.5 | Have you setup the multiple monitors and its display properties properly? |  |  |  | 1
a | 2.1.6 | Is resolution of target PC monitor in line with the graphic window resolution? |  |  |  | 1
a | 2.1.7 | Is the maximum number of tag handling in the HIS as per requirement? |  |  |  | 1
a | 2.1.8 | Has the Username and Password for PC Administrator and other user account been defined? |  |  |  | 1
| 2.1.9 | Is there a plan to transfer the above administration information to the customer in the as-built documentation? |  |  |  | 1
| 2.1.10 | For revamp or upgrade project, is the system revision the same as the existing project? This is important because if the engineering is carried out on a higher revision of system then it cannot be opened on a lower revision. |  |  |  |  | 1
a | 2.1.11 | Have separate PCs (not target PCs) considered for installation of engineering tools , yGet etc ? Tools are not allowed to be installed in target machines. If so, machines are required to be formatted, reinstalled before shipment. |  |  |  | 1
a
a
a | 1900-01-01 04:48 | Software Revision and Patch Record
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 2.2.1 | Have you installed the software revision as per the requirement?  Ensure consistency of software revision on all stations and take note of the compatibility of software revision for interfacing different system. |  |  |  | 1
a | 2.2.2 | Is there any patch software that has been loaded? If so, has it been applied uniformly across all the stations that require it?  Please check YHQ website for patch requirement. < http://globalcyber.jp.ykgw.net/qa/sps/CENTUM_VP_Patch_list.xls > Please maintain a log or record of all the software revisions and patch revision that has been installed. |  |  |  | 1
a
a
a | 1900-01-01 07:12 | 3rd Party Software Installation/verification
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 2.3.1 | Are you clear about all deliverable third party software to be installed on the PC? 3rd party software refer to those non-Yokogawa software such as Excel, Anti-virus, Acrobat, Oracle Database, Printer Configuration s/w etc. |  |  |  |  | 1
| 2.3.2 | Do you have official licenses to install the 3rd party software? If target licenses are not available, temporary licenses shall be arranged by project team. |  |  |  |  | 1
| 2.3.3 | Do you have all the 3rd party hardware drivers available? Sometimes separate drivers are required in addition to those in Windows O/S for printer, network card, SCSI adapter, RS485 adapter, etc. You shall deliver these driver software media to customer. |  |  |  |  | 1
a | 2.3.4 | Have you installed patches if Microsoft O/S or any other applications require patch to work with Yokogawa application? |  |  |  | 1
a | 2.3.5 | Have all the USB ports and removable media drives being disabled in all the PC’s? |  |  |  | 1
a
a
a | 1900-01-01 09:36 | FCS Loading Measurement
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 2.4.1 | Are all the target FCS connected to the network and powered on? |  |  |  | 1
a | 2.4.2 | Have you compiled & downloaded the FCS application Software? This is mandatory to activate inter station communication link. |  |  |  | 1
a | 2.4.3 | Is the CPU idle time in line with the CPU load calculated during the detailed engineering phase?  For the purpose of recording the FCS idle time ,Please carry out the following steps: • The FCS under review should not have test function activated. • No download operation must be performed. • Open at least 5 graphic pages ( with dense data) in different HIS which belong to the same operation group. • If the subsystem communication is available activate that with all subsystem tags configured in the DCS. • All nodes in the FCS to be powered on. • Ensure that all LC64, ST16 and all blocks are scanned on as per normal conditions. With all these conditions maintained, open the FCS status display window and record the CPU idle time. | No |  |  | 1
a | 2.4.4 | If there is a gross mismatch between the calculated & actual FCS CPU load? Is the actual CPU loading exceeding the limit specified by the customer?  Prepare a report as to what is the reason for this mismatch. This needs to be discussed with client/contractor during FAT. | No |  |  | 1
a
a
a | 1900-01-01 12:00 | FCS Resource
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 2.5.1 | Have you used FCS Resource Information tool to verify the actual FCS resource against the project requirement? |  |  |  | 1
a
a
a | 1900-01-01 14:24 | Vnet and Vnet-IP Loading Measurement
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | Vnet IP
a | 2.6.1 | Are all the L2SW/L3SW configured as per standard engineering guideline? |  |  |  | 1
a | 2.6.2 | Is the password for L2SW/L3SW recorded ? |  |  |  |  | 1
a | 2.6.3 | Is there any philosophy to handle the unused ports in L2SW & L3SW? For example, unused port to be disabled or not. |  |  |  |  | 1
a | 2.6.4 | Is the fiber optic transceiver, cable interconnection between switches tested? |  |  |  |  | 1
a | 2.6.5 | Is there any requirement from customer to prove Vnet/IP network loading by any tools? | No |  |  |  | 1
a | Vnet
a | 2.6.6 | Is the Vnet load measured and is it within the specification requirements? |  |  |  |  | 1
a
a
a | 1900-01-01 16:48 | PC Sizing
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 2.7.1 | Do all the PC’s & Server’s have adequate hard disk capacity after the target software has been loaded? |  |  |  | 1
a | 2.7.2 | Do all the PC’s & server’s have adequate CPU and memory capacity after the target software has been loaded? |  |  |  | 1
| 2.7.3 | Are there any performance issues because of lack of CPU speed / memory usage? If so, please check in the Task manager and report this issue. | No |  |  | 1
a | 2.7.4 | Have the Hard disk partition (drive partition, C, D etc) done as per requirement of respective applications (CENTUM VP, PRM, etc.) |  |  |  | 1
a
a
a | 1900-01-02 | APPLICATION
a | 1900-01-02 02:24 | Typical Loops Verification
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 3.1.1 | Have you checked all the typical loops generated for functionality as per the approved functional specification? |  |  |  | 1
a
a
a | 1900-01-02 04:48 | Application Verification
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 3.2.1 | N/A
a | 3.2.2 | 3.2.2 Have you tested all the complex loops / sequence documented by approved FDS and ensured that there is no discrepancy / doubt against the control narratives / functional spec.? Record the test processes by highlighting on FDS and customer narrative with notes, signature and date. |  |  |  | 1
a | 3.2.3 | Are there any signal exchanges between FCS and has this been tested? |  |  |  | 1
a | 3.2.4 | Is I-Table created to put all the ST16 and LC64 to AUTO? |  |  |  | 1
a | 3.2.5 | For blocks which have automatic function activation like SPLIT block SW=3, Selector switches SW=4,Have these settings been permanently activated in the software? |  |  |  | 1
a | 3.2.6 | Have you activated the test function for all the FCS and checked the alarm history for toggling alarms especially in logics and sequence tables? |  |  |  | 1
a | 3.2.7 | Are all the temporary configuration removed from the control drawing? |  |  |  | 1
a | 3.2.8 | Is the control drawing provided with vital text information mentioning important points to better understand the complex loop? |  |  |  | 1
a | 3.2.9 | Are the logics and interlocks tested with all possible manual intervention and operational errors? |  |  |  | 1
a | 3.2.10 | Have the following tools been executed and have you fixed all issues? i. Element Map ii. IOM Duplication iii. IO Map iv. Engineering Data Consistency Tool output to be attached. |  |  |  | 1
a | 3.2.11 | Have you executed “Tag Count” tool to validate FCS Loading. |  |  |  |  | 1
a
a
a | 1900-01-02 07:12 | Tuning Parameter Setting/Verification
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 3.3.1 | N/A | Move to SE4
a | 3.3.2 | If engineering ranges of tags have changed, have you rectified the previous default alarm setpoints for those tags? |  |  |  | 1
a | 3.3.3 | Is the tuning parameter file saved prior to commencement of FAT with all approved values? |  |  |  | 1
a
a
a | 1900-01-03 | HMI
a | 1900-01-03 02:24 | Document and Record
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 4.1.1 | Is the document basis clear to carry out the internal test? |  |  |  | 1
a | 4.1.2 | Are the items to be checked during the internal test clearly identified in the check sheets? |  |  |  | 1
a | 4.1.3 | Have areas where softcopy or visual inspection checks been carried out clearly marked and stored for ready reference? |  |  |  | 1
a | 4.1.4 | Has the DCS engineer documented these checks and maintained a hard copy? It is recommended that internal check shall not be carried out by the engineer who configured the software. |  |  |  | 1
a | 4.1.5 | Have all software been tested internally prior to FAT? |  |  |  | 1
a | 4.1.6 | Have you executed “Window Count” tool? |  |  |  |  | 1
a
a
a | 1900-01-03 04:48 | Graphic Static/Dynamic Verification
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 4.2.1 | Is the graphic window hierarchy configured properly? |  |  |  | 1
a | 4.2.2 | Are all the Graphic shortcuts created on all the HIS according to the operation philosophy? |  |  |  | 1
a | 4.2.3 | Have all the static graphics been approved ? |  |  |  | 1
a | 4.2.4 | Have you executed the “Graphic Consistency Check” Tool to verify the correctness of dynamic assignment? |  |  |  | 1
a | 4.2.5 | Have you tested each graphic using a checksheet and are you able to show the test record? |  |  |  | 1
a | 4.2.6 | Is proper index sheet available for easy navigation? |  |  |  | 1
a | 4.2.7 | Have you compiled all the pending items in the graphics for retest after getting the required date? Sub-System data and other tag data not clear needs to be .listed for retest. |  |  |  | 1
a
a
a | 1900-01-03 07:12 | Report Test
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 4.3.1 | Are all the reports triggered as per the defined scheduler? |  |  |  |  | 1
a | 4.3.2 | Have you simulated those data that cannot be verified under normal staging environment? |  |  |  |  | 1
a | 4.3.3 | Have you checked whether all values (process data, calculated data, closure data, etc.) in the report are correct? Simulate the required data and check on the report (Daily/hourly Average,max,min etc.,). |  |  |  |  | 1
a
a
a | 1900-01-03 09:36 | CG/TG/Function key Verification
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 4.4.1 | Is there any long term trend recording requirement mentioned in the specification and has the hard disk been sized for this? |  |  |  | 1
a | 4.4.2 | Have you checked the navigation as per the hierarchy from the control group and trend group to respective graphic window ? |  |  |  | 1
a | 4.4.3 | Has the DCS engineer prepared any CG and TG for the purpose of internal test and FAT? These shall be deleted after the FAT in consultation with the customer. |  |  |  | 1
a | 4.4.4 | Is the function key requirement specified for the project? |  |  |  |  | 1
| 4.4.5 | Is the function key labels to be inserted in the operator keyboard finalized and the same prepared? |  |  |  |  | 1
| 4.4.6 | Is the Opecon Grouping properly configured and tested? |  |  |  |  | 1
a | 4.4.7 | Is the function key operation checked for custom facpelates or user defined functions which may require operation key board functions ? |  |  |  |  | 1
a
a
a | 1900-01-03 12:00 | CAMS for HIS
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 4.5.1 | Have CAMS been enabled on HIS? |  |  |  |  | 1
a | 4.5.2 | Have CAMS filters been configured on Download master HIS and verified? |  |  |  |  | 1
a | 4.5.3 | Have CAMS equalization ring been configured and tested? |  |  |  |  | 1
| 4.5.4 | Have customer re-prioritized alarm definition been imported to CAMS database? |  |  |  |  | 1
| 4.5.5 | Have suppression been configured and tested? |  |  |  |  | 1
a
a
a | 1900-01-04 | BATCH
a | Please use 'SE5-Batch' sheet as well if your project uses Batch function.
a
a | 1900-01-05 | SUB-SYSTEMS
a | 1900-01-05 02:24 | Subsystem IO Map Verification
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 6.1.1 | Is the list of subsystems to be integrated during the FAT / IFAT identified and has it been included in the FAT / IFAT procedure? | No |  |  | 1
a | 6.1.2 | Is there any subsystem redundancy check envisaged? | No |  |  |  | 1
a | 6.1.3 | Is the subsystem IO check method clarified for digital and analog signals? For digital we can check the starting bit & ending bit of each word if time is a constraint. |  |  |  | 1
a | 6.1.4 | Is the communication philosophy clear between the DCS and the subsystem? |  |  |  | 1
a | 6.1.5 | Are all the subsystem IO’s mapped to the DCS? |  |  |  | 1
a | 6.1.6 | Are the communication settings done for all the sub-system cards and WW builder . |  |  |  | 1
a | 6.1.7 | Are there adequate spare %WW, %WB as per specification requirements? |  |  |  | 1
| 6.1.8 | Have you specified the gain & bias for analog tags where scaling is required? |  |  |  | 1
a | 6.1.9 | Is there any date/time exchange between the subsystem and the DCS and is this data displayed in the DCS? |  |  |  |  | 1
a | 6.1.10 | Is the display format in line with the requirement? |  |  |  | 1
a | 6.1.11 | Is there any readback function requirement specified for any of the subsystem? |  |  |  |  | 1
a | 6.1.12 | Is there any time synchronization requirement between the DCS and the subsystem? | No |  |  |  | 1
| 6.1.13 | Have the following tools been executed and have you fixed all issues? v. Element Map vi. IOM Duplication vii. IO Map viii. Engineering Data Consistency Tool output to be attached. |  |  |  | 1
| 1900-01-05 04:48 | Serial Interface Test (MODBUS, Profibus, Ethernet, etc.)
| S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 6.2.1 | Has a clear Schedule been drawn up for the various Tests which include internal IFAT? |  |  |  | 1
a | 6.2.2 | Has the Engineer who will be conducting the Test been identified? |  |  |  | 1
a | 6.2.3 | Are you using the latest revision of the Communication List? |  |  |  | 1
a | 6.2.4 | Have you configured & debugged the project database? |  |  |  | 1
a | 6.2.5 | Have the relevant HMI been generated & debugged? |  |  |  | 1
| 6.2.6 | Are the communication cables fabricated as per requirement? For serial interface, different subsystems require different pin configurations |  |  |  | 1
| 1900-01-05 07:12 | OPC Server Interface Test
| S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 6.3.1 | Has a clear Schedule been drawn up for the various Tests which include internal IFAT? |  |  |  |  | 1
a | 6.3.2 | Has the Engineer who will be conducting the Test been identified? |  |  |  |  | 1
a | 6.3.3 | Has the Exaopc Server been Setup for Test? |  |  |  |  | 1
a | 6.3.4 | Have you identified the hub & cables required for the Test? |  |  |  |  | 1
| 6.3.5 | Have the relevant HMI been generated & debugged? |  |  |  |  | 1
| 1900-01-05 09:36 | OPC Client interface Test
| S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 6.4.1 | Has a clear Schedule been drawn up for the various Tests which include internal IFAT? |  |  |  |  | 1
| 6.4.2 | Has the Engineer who will be conducting the Test been identified? |  |  |  |  | 1
| 6.4.3 | Has the GSGW/SIOS/UGS been Setup for Test? |  |  |  |  | 1
a | 6.4.4 | Are you using the latest revision of the Communication List? |  |  |  |  | 1
a | 6.4.5 | Have you configured & debugged the project database? |  |  |  |  | 1
a | 6.4.6 | Have you identified the hub & cables required for Test? |  |  |  |  | 1
a | 6.4.7 | Have the relevant HMI been generated & debugged? |  |  |  |  | 1
a | 1900-01-06 | OTHER NON-DCS ITEMS
a | 1900-01-06 02:24 | Plant Resource Manager
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 7.1.1 | Has the Plant Resource Manager tested? |  |  |  |  | 1
a
a | 1900-01-06 04:48 | Sequence of Events Manager (SEM - SoE for DCS)
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 7.2.1 | Has the SoE for DCS tested? |  |  |  |  | 1
a
a | 1900-01-06 07:12 | EXA Series Packages
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 7.3.1 | Has the EXA packages tested? |  |  |  |  | 1
a
a | 1900-01-06 09:36 | Remote Terminal Service
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 7.4.1 | Has the Remote Terminal Server tested? |  |  |  |  | 1
a
a | 1900-01-06 12:00 | Operating Training System
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 7.5.1 | Has the OTS tested? |  |  |  |  | 1
a
a | 1900-01-06 14:24 | Time Synchronization
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 7.6.1 | Has the Time synchronization tested? |  |  |  |  | 1
a
a
| 1900-01-07 | FAT / IFAT
a | 1900-01-07 02:24 | FAT / IFAT Test Plan
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 8.1.1 | Are the simple loops going to be tested individually or is it a database check? |  |  |  | 1
a | 8.1.2 | Is the subsystem integration test philosophy clearly spelt out? Only simulation in DCS by mapping I/O or requires actual subsystem. |  |  |  | 1
a | 8.1.3 | Are there any identical complex applications and have you defined a methodology to efficiently test these applications? |  |  |  | 1
a
a
a | 1900-01-07 04:48 | FAT /IFAT Test Procedure
| S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 8.2.1 | Has the FAT procedure been approved? |  |  |  | 1
a | 8.2.2 | Is the software test procedure spelt out clearly in the document? |  |  |  | 1
a | 8.2.3 | Is the DCS engineer conversant with loop demonstration procedure? |  |  |  | 1
a | 8.2.4 | Have you configured CG’s, graphics, simulations in order to demonstrate the complex loop of sequence to make it more effective? |  |  |  | 1
a | 8.2.5 | Have you verified the FAT procedure during Internal Test and made updates in the document if necessary? | No |  |  | 1
a
a
| 1900-01-07 07:12 | FAT Report - Punch List Management System
| S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 8.3.1 | Are you using the electronic punch list management or any other means of punch entry in electronic form for easy compilation of data?  In case you are not using please state the reason. |  |  |  | 1
a | 8.3.2 | Have you attached the electronic punch list management system procedure as annexure to the FAT Procedure/Plan? |  |  |  | 1
| 8.3.3 | Has the punch list entry PC been setup?  Should be shown in the Staging layout |  |  |  | 1
| 8.3.4 | During FAT Punch lists are generally created by hand. Have people been identified to key this into the Punch list Server or in electronic form (Excel)? |  |  |  | 1
a
| 1900-01-07 09:36 | FAT Report - Customer Master Documents
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 8.4.1 | Have all the customer documents (basis for FAT) been filed and labeled as FAT-MASTER and kept in a central location? |  |  |  | 1
a | 8.4.2 | Have all the Approved Functional Specifications been filed and labeled as FAT-MASTER and kept in a central location? |  |  |  | 1
a | 8.4.3 | Are all RFI’s and responses been filed and complied?  In some jobs RFI’s (Request For Information) formats are originated by the project team to the customer’s which shall form the basis for engineering and testing. |  |  |  | 1
a
a
| 1900-01-07 12:00 | FAT Report - Documents Change Management
| S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 8.5.1 | Are you clear about how documents change shall be managed during the FAT? |  |  |  | 1 | 1
| 8.5.2 | Have you marked up the changes on Master FAT documents with dates and signature? |  |  |  | 1
Total

## SE5 (2)
a | S.No | Check Items | Check Items CN | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 1.1.1 | Will you be staging all the PCs for HIS, EWS, PRM, advanced controls, PIMS, EXAOPC etc. shown in the system configuration? | 您是否将为系统配置中显示的HIS，EWS，PRM，高级控件，PIMS，EXAOPC等所有PC进行升级？ |  |  |  | 1
a | 1.1.2 | Are Operating Systems newly installed to all the target PCs properly? Pre- installed OS is not acceptable. i Refer to "Selection web". (http://globalcyber.jp.ykgw.net/PMK/Selection-e/selection-e.htm) | 是否已将操作系统重新正确安装到所有目标PC？不接受预安装的OS。 i请参阅“选择网”。 （http://globalcyber.jp.ykgw.net/PMK/Selection-e/selection-e.htm） |  |  |  | 1
a | 1.1.3 | Have you used correct version of service pack and confirmed the current MS patches for the PCs?. i Tested MS patches can be obtained through the following website. (http://adm402-sitc001.gbl.ykgw.net/sites/security2012/avos/AVOS%20Download%20Center/Download_AVOS.html) * The latest tested MS patches are listed in section 03 "Validation Reports". | “您是否使用了正确的Service Pack版本并确认了PC的当前MS补丁？ i可通过以下网站获得经过测试的MS补丁。 （http://adm402-sitc001.gbl.ykgw.net/sites/security2012/avos/AVOS%20Download%20Center/Download_AVOS.html） *最新测试的MS修补程序在第03节““验证报告””中列出。 |  |  |  | 1
a | 1.1.4 | Have you checked if the service pack of the OS is compatible with the application software? Refer software installation manual for revision. | 您是否检查过操作系统的Service Pack是否与应用程序软件兼容？ 请参阅软件安装手册以进行修订。 |  |  |  | 1
a | 1.1.5 | Is the OS media available along with the PC hardware? | OS介质与PC硬件一起可用吗？ |  |  |  | 1
a | 1.1.6 | Is their any hard disk partitioning philosophy worked out for all the PCs? | 他们是否对所有PC都采用了硬盘分区原则？ |  |  |  | 1
a | 1.1.7 | Have you determined the PCI slot for installing the Vnet / Vnet/IP card and installed with proper DIP switch setting? | 您是否确定了用于安装Vnet / Vnet / IP卡的PCI插槽并已使用正确的DIP开关设置进行安装？ |  |  |  | 1
a | 1.1.8 | Are computer names for the PCs on the network as per design? HIS shall have HISddss as computer name. All other PCs shall preferably have STNddss as computer name. | “是否按照设计为网络上的PC提供了计算机名称？ 他应将HISddss作为计算机名。所有其他PC最好将STNddss作为计算机名。 |  |  |  | 1
a | 1.1.9 | Does the Windows OS require activation and have you kept the record of activation code? | Windows操作系统是否需要激活，您是否保留了激活代码的记录？ |  |  |  | 1
a | 1.1.10 | Have you checked the event log for any error messages or abnormalities during OS installation? | 在安装操作系统期间，您是否检查了事件日志中是否有任何错误消息或异常情况？ | No |  |  | 1
a | 1.1.11 | Have you made a ghost image of the hard disk to save time/effort during re-installation of OS? | 您是否制作了硬盘的虚拟映像以节省重新安装OS的时间/精力？ |  |  |  | 1
a
a
a | 1899-12-31 04:48 | Network Address
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 1.2.1 | Have you installed the Open Bus and Control Bus drivers from the proper revision system installation media? The drivers should not be installed from the New hardware wizard appearing when the PC is restarted after installation of VF/ VI card. If a separate Ethernet for Information Network is used, Vnet/IP open should be disabled. Refer the Vnet /IP construction guideline section 1.5 and 1.6 for more details. (http://inquiry.gbl.ykgw.net/sys-inq-en/pdf/CENTUM/VP%20R5/TI/TI30A10A05-01E_003.pdf) | “您是否通过正确的修订系统安装媒体安装了Open Bus和Control Bus驱动程序？ 安装VF / VI卡后重新启动PC时，不应从出现的“新硬件”向导中安装驱动程序。 如果使用单独的信息网络以太网，则应禁用Vnet / IP open。 有关更多详细信息，请参阅Vnet / IP建设指南第1.5和1.6节。 （http://inquiry.gbl.ykgw.net/sys-inq-zh/pdf/CENTUM/VP%20R5/TI/TI30A10A05-01E_003.pdf） |  |  |  | 1
a | 1.2.2 | Have you configured higher access priority to Open Bus than Control bus in the advanced settings? | 在高级设置中，您是否为Open Bus配置了比Control总线更高的访问优先级？ |  |  |  | 1
a | 1.2.3 | Have you configured the IP address / Subnet mask / Default Gateway address for the open bus as per the FDS? | 您是否已按照FDS为开放式总线配置了IP地址/子网掩码/默认网关地址？ |  |  |  | 1
a | 1.2.4 | Have you configured the IP address / Subnet mask / Default Gateway address for the control bus as per the FDS? | 您是否已按照FDS为控制总线配置了IP地址/子网掩码/默认网关地址？ |  |  |  | 1
a | 1.2.5 | Is the network adaptor name for the Open bus and control bus mentioned as per the FDS? | 是否按照FDS提到了Open总线和控制总线的网络适配器名称？ |  |  |  | 1
a | 1.2.6 | Have the L2 and L3 switches been configured as per the requirement of Vnet/IP? Even though the out of the box manufacturer configuration works, the switches must be examined to comply to the Vnet/IP requirement? | 是否已根据Vnet / IP的要求配置了L2和L3交换机？ 即使开箱即用的制造商配置有效，也必须检查交换机是否符合Vnet / IP要求？ |  |  |  | 1
a
a
a | 1899-12-31 07:12 | System Protection and Backup
| S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 1.3.1 | Have you set the password for the internal test system in order to protect it from unauthorized access? | 您是否设置了内部测试系统的密码以防止未经授权的访问？ |  |  |  | 1
a | 1.3.2 | Have you installed the Antivirus software on all the HIS’s, PC’s, servers? | 您是否已在所有HIS，PC和服务器上安装了防病毒软件？ | No |  |  |  | 1
a | 1.3.3 | Have you taken the following measures to prevent virus attack? * Download the latest virus definition file and OS patches. * Scan the target and in-house system for virus. *Document the virus scan result.  Log book shall be signed and kept for audit | 您是否采取了以下措施来防止病毒攻击？ *下载最新的病毒定义文件和操作系统补丁。 *扫描目标系统和内部系统是否有病毒。 *记录病毒扫描结果。 *日志应签名并备查” | No |  |  |  | 1
| 1.3.4 | Is the PC scanned for virus regularly with updates? | PC是否定期通过更新扫描病毒？ | No |  |  |  | 1
a | 1.3.5 | Have you planned a daily backup for the project database? This backup should be located in the hard disk of another PC and not the PC where the project DB exists. | 您是否计划对项目数据库进行每日备份？ 此备份应位于另一台PC的硬盘中，而不是在存在项目DB的PC中。 |  |  |  | 1
a | 1.3.6 | Have you done weekly backup on removable media such as DAT tape and stored them at a separate place from staging area? Some projects have contractual requirement to protect the project database at an offsite location for security and fire protection. Verify if this is required. | 您是否每周对数据磁带等可移动介质进行备份，并将它们存储在暂存区之外的单独位置？ 一些项目具有合同要求，以在非现场位置保护项目数据库，以确保安全和防火。验证是否需要这样做。 |  |  |  | 1
a | 1.3.7 | If project supply Access Control package, is it being used to manage the access of engineering database? (Engineering builder, Report package, Batch recipe package) | 如果项目提供了访问控制软件包，它是否用于管理工程数据库的访问？（工程构建器，报告软件包，批处理配方软件包） |  |  |  |  | 1
a
a
a | 1900-01-01 | SYSTEM
a | 1900-01-01 02:24 | DCS Software Installation/Verification
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 2.1.1 | Will you be conducting the FAT using the target software packages? It is preferable to conduct the FAT with target keycodes in order to avoid using functions eventually not available to customer. | “您将使用目标软件包进行FAT吗？ 为避免最终使用客户无法使用的功能，最好使用目标键代码进行FAT。 |  |  |  | 1
a | 2.1.2 | Have you studied the installation manual and taken note of all the precautions before the installation? | 在安装之前，您是否已阅读安装手册并注意所有注意事项？ |  |  |  | 1
a | 2.1.3 | Have you checked the installation log of each HIS to ensure that there are no system installation errors? | 您是否检查了每个HIS的安装日志以确保没有系统安装错误？ |  |  |  | 1
a | 2.1.4 | Have you specified correct master database reference HIS during system installation?. | 系统安装过程中是否指定了正确的主数据库引用HIS？ |  |  |  | 1
a | 2.1.5 | Have you setup the multiple monitors and its display properties properly? | 您是否正确设置了多台监视器及其显示属性？ |  |  |  | 1
a | 2.1.6 | Is resolution of target PC monitor in line with the graphic window resolution? | 目标PC显示器的分辨率是否与图形窗口分辨率一致？ |  |  |  | 1
a | 2.1.7 | Is the maximum number of tag handling in the HIS as per requirement? | HIS中标签处理的最大数量是否符合要求？ |  |  |  | 1
a | 2.1.8 | Has the Username and Password for PC Administrator and other user account been defined? | 是否已定义PC Administrator和其他用户帐户的用户名和密码？ |  |  |  | 1
| 2.1.9 | Is there a plan to transfer the above administration information to the customer in the as-built documentation? | 是否有计划将上述管理信息在生成的文档中传输给客户？ |  |  |  | 1
| 2.1.10 | For revamp or upgrade project, is the system revision the same as the existing project? This is important because if the engineering is carried out on a higher revision of system then it cannot be opened on a lower revision. | 对于修订或升级项目，系统版本是否与现有项目相同？ 这一点很重要，因为如果工程在较高版本的系统上进行，则无法在较低版本上打开它。 |  |  |  |  | 1
a | 2.1.11 | Have separate PCs (not target PCs) considered for installation of engineering tools , yGet etc ? Tools are not allowed to be installed in target machines. If so, machines are required to be formatted, reinstalled before shipment. | 是否考虑过安装工程工具，yGet等的单独PC（不是目标PC）？ 不允许在目标计算机上安装工具。 如果是这样，则需要格式化机器，然后在装运前重新安装。 |  |  |  | 1
a
a
a | 1900-01-01 04:48 | Software Revision and Patch Record
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 2.2.1 | Have you installed the software revision as per the requirement?  Ensure consistency of software revision on all stations and take note of the compatibility of software revision for interfacing different system. | 您是否已根据要求安装了软件修订版？ 确保所有工作站上软件版本的一致性，并注意用于连接不同系统的软件版本的兼容性。 |  |  |  | 1
a | 2.2.2 | Is there any patch software that has been loaded? If so, has it been applied uniformly across all the stations that require it?  Please check YHQ website for patch requirement. < http://globalcyber.jp.ykgw.net/qa/sps/CENTUM_VP_Patch_list.xls > Please maintain a log or record of all the software revisions and patch revision that has been installed. | 是否已加载任何补丁软件？如果已加载，是否已在需要它的所有站点上统一应用了补丁软件？ patch请检查YHQ网站的补丁程序要求。 <http://globalcyber.jp.ykgw.net/qa/sps/CENTUM_VP_Patch_list.xls> 请保留所有已安装软件版本和补丁程序修订的日志或记录。 |  |  |  | 1
a
a
a | 1900-01-01 07:12 | 3rd Party Software Installation/verification
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 2.3.1 | Are you clear about all deliverable third party software to be installed on the PC? 3rd party software refer to those non-Yokogawa software such as Excel, Anti-virus, Acrobat, Oracle Database, Printer Configuration s/w etc. | 您是否清楚要在PC上安装的所有可交付使用的第三方软件？ 第三方软件是指那些非横河电机的软件，例如Excel，防病毒，Acrobat，Oracle数据库，打印机配置软件等。 |  |  |  |  | 1
| 2.3.2 | Do you have official licenses to install the 3rd party software? If target licenses are not available, temporary licenses shall be arranged by project team. | 您具有安装第三方软件的官方许可证吗？ 如果没有目标许可证，则应由项目团队安排临时许可证。 |  |  |  |  | 1
| 2.3.3 | Do you have all the 3rd party hardware drivers available? Sometimes separate drivers are required in addition to those in Windows O/S for printer, network card, SCSI adapter, RS485 adapter, etc. You shall deliver these driver software media to customer. | 您有所有可用的第三方硬件驱动程序吗？ 有时，除了Windows O / S中的打印机，网卡，SCSI适配器，RS485适配器等驱动程序外，还需要单独的驱动程序。您应将这些驱动程序软件介质交付给客户。 |  |  |  |  | 1
a | 2.3.4 | Have you installed patches if Microsoft O/S or any other applications require patch to work with Yokogawa application? | 如果Microsoft O / S或任何其他应用程序需要补丁才能与Yokogawa应用程序一起使用，您是否已安装补丁？ |  |  |  | 1
a | 2.3.5 | Have all the USB ports and removable media drives being disabled in all the PC’s? | 是否在所有PC上都禁用了所有USB端口和可移动媒体驱动器？ |  |  |  | 1
a
a
a | 1900-01-01 09:36 | FCS Loading Measurement
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 2.4.1 | Are all the target FCS connected to the network and powered on? | 所有目标FCS是否都已连接到网络并通电？ |  |  |  | 1
a | 2.4.2 | Have you compiled & downloaded the FCS application Software? This is mandatory to activate inter station communication link. | 您是否已编译并下载了FCS应用程序软件？ 这是激活站间通信链接所必需的。 |  |  |  | 1
a | 2.4.3 | Is the CPU idle time in line with the CPU load calculated during the detailed engineering phase?  For the purpose of recording the FCS idle time ,Please carry out the following steps: • The FCS under review should not have test function activated. • No download operation must be performed. • Open at least 5 graphic pages ( with dense data) in different HIS which belong to the same operation group. • If the subsystem communication is available activate that with all subsystem tags configured in the DCS. • All nodes in the FCS to be powered on. • Ensure that all LC64, ST16 and all blocks are scanned on as per normal conditions. With all these conditions maintained, open the FCS status display window and record the CPU idle time. | “ CPU空闲时间是否与详细工程阶段计算出的CPU负载一致？ 为了记录FCS空闲时间，请执行以下步骤： •所检查的FCS不应激活测试功能。 •无需执行下载操作。 •在属于同一操作组的不同HIS中至少打开5个图形页面（包含密集数据）。 •如果子系统通讯可用，请使用DCS中配置的所有子系统标签激活该通讯。 •FCS中要打开的所有节点。 •确保按照正常条件扫描所有LC64，ST16和所有块。 在保持所有这些条件的情况下，打开FCS状态显示窗口并记录CPU空闲时间。 | No |  |  | 1
a | 2.4.4 | If there is a gross mismatch between the calculated & actual FCS CPU load? Is the actual CPU loading exceeding the limit specified by the customer?  Prepare a report as to what is the reason for this mismatch. This needs to be discussed with client/contractor during FAT. | 如果计算的FCS与实际的FCS CPU负载之间存在严重不匹配？实际的CPU负载是否超过客户指定的限制？ 准备有关此不匹配的原因的报告。 FAT期间需要与客户/承包商讨论。 | No |  |  | 1
a
a
a | 1900-01-01 12:00 | FCS Resource
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 2.5.1 | Have you used FCS Resource Information tool to verify the actual FCS resource against the project requirement? | 您是否使用FCS资源信息工具根据项目要求验证了实际的FCS资源？ |  |  |  | 1
a
a
a | 1900-01-01 14:24 | Vnet and Vnet-IP Loading Measurement
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | Vnet IP
a | 2.6.1 | Are all the L2SW/L3SW configured as per standard engineering guideline? | 所有的L2SW / L3SW是否都按照标准工程指南进行了配置？ |  |  |  | 1
a | 2.6.2 | Is the password for L2SW/L3SW recorded ? | 是否已记录L2SW / L3SW的密码？ |  |  |  |  | 1
a | 2.6.3 | Is there any philosophy to handle the unused ports in L2SW & L3SW? For example, unused port to be disabled or not. | 是否有处理L2SW和L3SW中未使用端口的哲学？ 例如，是否禁用未使用的端口。 |  |  |  |  | 1
a | 2.6.4 | Is the fiber optic transceiver, cable interconnection between switches tested? | 交换机之间的光纤收发器，电缆互连是否经过测试？ |  |  |  |  | 1
a | 2.6.5 | Is there any requirement from customer to prove Vnet/IP network loading by any tools? | 客户是否有要求通过任何工具证明Vnet / IP网络负载？ | No |  |  |  | 1
a | Vnet
a | 2.6.6 | Is the Vnet load measured and is it within the specification requirements? | Vnet负载是否已测量，是否在规格要求之内？ |  |  |  |  | 1
a
a
a | 1900-01-01 16:48 | PC Sizing
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 2.7.1 | Do all the PC’s & Server’s have adequate hard disk capacity after the target software has been loaded? | 加载目标软件后，所有PC和服务器是否都具有足够的硬盘容量？ |  |  |  | 1
a | 2.7.2 | Do all the PC’s & server’s have adequate CPU and memory capacity after the target software has been loaded? | 加载目标软件后，所有PC和服务器是否都具有足够的CPU和内存容量？ |  |  |  | 1
| 2.7.3 | Are there any performance issues because of lack of CPU speed / memory usage? If so, please check in the Task manager and report this issue. | 由于缺乏CPU速度/内存使用率，是否存在任何性能问题？ 如果是这样，请签入任务管理器并报告此问题。 | No |  |  | 1
a | 2.7.4 | Have the Hard disk partition (drive partition, C, D etc) done as per requirement of respective applications (CENTUM VP, PRM, etc.) | 已按照相应应用程序（CENTUM VP，PRM等）的要求完成了硬盘分区（驱动器分区，C，D等） |  |  |  | 1
a
a
a | 1900-01-02 | APPLICATION
a | 1900-01-02 02:24 | Typical Loops Verification
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 3.1.1 | Have you checked all the typical loops generated for functionality as per the approved functional specification? | 您是否按照批准的功能说明检查了为功能而生成的所有典型循环？ |  |  |  | 1
a
a
a | 1900-01-02 04:48 | Application Verification
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 3.2.1 | N/A
a | 3.2.2 | 3.2.2 Have you tested all the complex loops / sequence documented by approved FDS and ensured that there is no discrepancy / doubt against the control narratives / functional spec.? Record the test processes by highlighting on FDS and customer narrative with notes, signature and date. | 3.2.2您是否已经测试了批准的FDS记录的所有复杂循环/顺序，并确保与控制说明/功能规范之间没有差异/怀疑？” 通过在FDS上突出显示客户说明以及签名，签名和日期来记录测试过程。 |  |  |  | 1
a | 3.2.3 | Are there any signal exchanges between FCS and has this been tested? | FCS之间是否有任何信号交换，是否已经过测试？ |  |  |  | 1
a | 3.2.4 | Is I-Table created to put all the ST16 and LC64 to AUTO? | 是否创建了I-Table，以便将所有ST16和LC64置于AUTO状态？ |  |  |  | 1
a | 3.2.5 | For blocks which have automatic function activation like SPLIT block SW=3, Selector switches SW=4,Have these settings been permanently activated in the software? | 对于具有自动功能激活的块，例如SPLIT块SW = 3，选择开关SW = 4，这些设置是否已在软件中永久激活？ |  |  |  | 1
a | 3.2.6 | Have you activated the test function for all the FCS and checked the alarm history for toggling alarms especially in logics and sequence tables? | 您是否激活了所有FCS的测试功能并检查了警报历史，以切换警报，尤其是在逻辑和顺序表中？ |  |  |  | 1
a | 3.2.7 | Are all the temporary configuration removed from the control drawing? | 是否从控制图中删除了所有临时配置？ |  |  |  | 1
a | 3.2.8 | Is the control drawing provided with vital text information mentioning important points to better understand the complex loop? | 控制图是否提供了重要文本信息，其中提到了要点，以便更好地理解复杂的回路？ |  |  |  | 1
a | 3.2.9 | Are the logics and interlocks tested with all possible manual intervention and operational errors? | 逻辑和联锁是否经过了所有可能的人工干预和操作错误的测试？ |  |  |  | 1
a | 3.2.10 | Have the following tools been executed and have you fixed all issues? i. Element Map ii. IOM Duplication iii. IO Map iv. Engineering Data Consistency Tool output to be attached. | 是否已执行以下工具，您是否已解决所有问题？ i. 元素图 ii. IOM复制 iii. IO地图 iv. 工程数据一致性 附带的工具输出。 |  |  |  | 1
a | 3.2.11 | Have you executed “Tag Count” tool to validate FCS Loading. | 您是否执行了“标签计数”工具来验证FCS加载。 |  |  |  |  | 1
a
a
a | 1900-01-02 07:12 | Tuning Parameter Setting/Verification
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 3.3.1 | N/A |  | Move to SE4
a | 3.3.2 | If engineering ranges of tags have changed, have you rectified the previous default alarm setpoints for those tags? | 如果标签的工程范围已更改，您是否已为这些标签纠正了先前的默认警报设置点？ |  |  |  | 1
a | 3.3.3 | Is the tuning parameter file saved prior to commencement of FAT with all approved values? | 在启动FAT之前，是否使用所有批准的值保存了调整参数文件？ |  |  |  | 1
a
a
a | 1900-01-03 | HMI
a | 1900-01-03 02:24 | Document and Record
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 4.1.1 | Is the document basis clear to carry out the internal test? | 文件依据是否明确进行了内部测试？ |  |  |  | 1
a | 4.1.2 | Are the items to be checked during the internal test clearly identified in the check sheets? | 内部检查过程中要检查的项目在检查表中是否明确标识？ |  |  |  | 1
a | 4.1.3 | Have areas where softcopy or visual inspection checks been carried out clearly marked and stored for ready reference? | 是否对进行软拷贝或目测检查的区域进行了清楚的标记并存储以备参考？ |  |  |  | 1
a | 4.1.4 | Has the DCS engineer documented these checks and maintained a hard copy? It is recommended that internal check shall not be carried out by the engineer who configured the software. | DCS工程师是否记录了这些检查并维护了纸质副本？ 建议不要由配置软件的工程师进行内部检查。 |  |  |  | 1
a | 4.1.5 | Have all software been tested internally prior to FAT? | 在FAT之前，是否已对所有软件进行了内部测试？ |  |  |  | 1
a | 4.1.6 | Have you executed “Window Count” tool? | 您是否执行过“窗口计数”工具？ |  |  |  |  | 1
a
a
a | 1900-01-03 04:48 | Graphic Static/Dynamic Verification
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 4.2.1 | Is the graphic window hierarchy configured properly? | 图形窗口层次结构是否配置正确？ |  |  |  | 1
a | 4.2.2 | Are all the Graphic shortcuts created on all the HIS according to the operation philosophy? | 是否根据操作原理在所有HIS上创建了所有图形快捷方式？ |  |  |  | 1
a | 4.2.3 | Have all the static graphics been approved ? | 是否已批准所有静态图形？ |  |  |  | 1
a | 4.2.4 | Have you executed the “Graphic Consistency Check” Tool to verify the correctness of dynamic assignment? | 您是否执行了“图形一致性检查”工具以验证动态分配的正确性？ |  |  |  | 1
a | 4.2.5 | Have you tested each graphic using a checksheet and are you able to show the test record? | 您是否已使用检查表测试了每个图形，并且能够显示测试记录？ |  |  |  | 1
a | 4.2.6 | Is proper index sheet available for easy navigation? | 是否提供适当的索引表以便于浏览？ |  |  |  | 1
a | 4.2.7 | Have you compiled all the pending items in the graphics for retest after getting the required date? Sub-System data and other tag data not clear needs to be .listed for retest. | 获得所需日期后，您是否已将图形中所有待处理的项目进行了编译以进行重新测试？ 需要列出子系统数据和其他未清除的标签数据以进行重新测试。 |  |  |  | 1
a
a
a | 1900-01-03 07:12 | Report Test
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 4.3.1 | Are all the reports triggered as per the defined scheduler? | 是否按照定义的计划程序触发了所有报告？ |  |  |  |  | 1
a | 4.3.2 | Have you simulated those data that cannot be verified under normal staging environment? | 您是否模拟了在正常登台环境下无法验证的数据？ |  |  |  |  | 1
a | 4.3.3 | Have you checked whether all values (process data, calculated data, closure data, etc.) in the report are correct? Simulate the required data and check on the report (Daily/hourly Average,max,min etc.,). | 您是否检查了报告中的所有值（过程数据，计算数据，关闭数据等）是否正确？ 模拟所需的数据并检查报告（每日/每小时平均值，最大值，最小值等）。 |  |  |  |  | 1
a
a
a | 1900-01-03 09:36 | CG/TG/Function key Verification
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 4.4.1 | Is there any long term trend recording requirement mentioned in the specification and has the hard disk been sized for this? | 规范中是否有任何长期趋势记录要求，硬盘是否已为此调整尺寸？ |  |  |  | 1
a | 4.4.2 | Have you checked the navigation as per the hierarchy from the control group and trend group to respective graphic window ? | 您是否已按照从控件组和趋势组到相应图形窗口的层次结构检查了导航？ |  |  |  | 1
a | 4.4.3 | Has the DCS engineer prepared any CG and TG for the purpose of internal test and FAT? These shall be deleted after the FAT in consultation with the customer. | DCS工程师是否为内部测试和FAT准备了CG和TG？ 在与客户协商后，这些内容应在FAT之后删除。 |  |  |  | 1
a | 4.4.4 | Is the function key requirement specified for the project? | 是否为项目指定了功能键要求？ |  |  |  |  | 1
| 4.4.5 | Is the function key labels to be inserted in the operator keyboard finalized and the same prepared? | 插入操作员键盘的功能键标签是否已确定并准备就绪？ |  |  |  |  | 1
| 4.4.6 | Is the Opecon Grouping properly configured and tested? | Opecon分组是否已正确配置和测试？ |  |  |  |  | 1
a | 4.4.7 | Is the function key operation checked for custom facpelates or user defined functions which may require operation key board functions ? | 是否检查了功能键的操作是否需要定制功能或用户定义的功能，这些功能可能需要操作键盘功能？ |  |  |  |  | 1
a
a
a | 1900-01-03 12:00 | CAMS for HIS
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 4.5.1 | Have CAMS been enabled on HIS? | 是否在HIS上启用了CAMS？ |  |  |  |  | 1
a | 4.5.2 | Have CAMS filters been configured on Download master HIS and verified? | 是否已在下载主HIS上配置了CAMS筛选器并进行了验证？ |  |  |  |  | 1
a | 4.5.3 | Have CAMS equalization ring been configured and tested? | 是否已配置并测试了CAMS均衡环？ |  |  |  |  | 1
| 4.5.4 | Have customer re-prioritized alarm definition been imported to CAMS database? | 是否已将客户重新设置优先级的警报定义导入到CAMS数据库？ |  |  |  |  | 1
| 4.5.5 | Have suppression been configured and tested? | 是否已配置并测试了抑制功能？ |  |  |  |  | 1
a
a
a | 1900-01-04 | BATCH
a | Please use 'SE5-Batch' sheet as well if your project uses Batch function.
a
a | 1900-01-05 | SUB-SYSTEMS
a | 1900-01-05 02:24 | Subsystem IO Map Verification
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 6.1.1 | Is the list of subsystems to be integrated during the FAT / IFAT identified and has it been included in the FAT / IFAT procedure? | 是否确定了在FAT / IFAT过程中要集成的子系统列表，并且该列表是否已包括在FAT / IFAT过程中？ | No |  |  | 1
a | 6.1.2 | Is there any subsystem redundancy check envisaged? | 是否计划进行子系统冗余检查？ | No |  |  |  | 1
a | 6.1.3 | Is the subsystem IO check method clarified for digital and analog signals? For digital we can check the starting bit & ending bit of each word if time is a constraint. | 是否明确了针对数字和模拟信号的子系统IO检查方法？ 对于数字，如果时间有限，我们可以检查每个单词的起始位和结束位。 |  |  |  | 1
a | 6.1.4 | Is the communication philosophy clear between the DCS and the subsystem? | DCS与子系统之间的通信理念是否清晰？ |  |  |  | 1
a | 6.1.5 | Are all the subsystem IO’s mapped to the DCS? | 所有子系统IO是否都已映射到DCS？ |  |  |  | 1
a | 6.1.6 | Are the communication settings done for all the sub-system cards and WW builder . | 所有子系统卡和WW构建器的通信设置是否都已完成？ |  |  |  | 1
a | 6.1.7 | Are there adequate spare %WW, %WB as per specification requirements? | 根据规格要求，是否有足够的备用％WW，％WB？ |  |  |  | 1
| 6.1.8 | Have you specified the gain & bias for analog tags where scaling is required? | 您是否为需要缩放的模拟标签指定了增益和偏置？ |  |  |  | 1
a | 6.1.9 | Is there any date/time exchange between the subsystem and the DCS and is this data displayed in the DCS? | 子系统和DCS之间是否有日期/时间交换，该数据是否显示在DCS中？ |  |  |  |  | 1
a | 6.1.10 | Is the display format in line with the requirement? | 显示格式是否符合要求？ |  |  |  | 1
a | 6.1.11 | Is there any readback function requirement specified for any of the subsystem? | 是否为任何子系统指定了任何回读功能要求？ |  |  |  |  | 1
a | 6.1.12 | Is there any time synchronization requirement between the DCS and the subsystem? | DCS和子系统之间是否有时间同步要求？ | No |  |  |  | 1
| 6.1.13 | Have the following tools been executed and have you fixed all issues? v. Element Map vi. IOM Duplication vii. IO Map viii. Engineering Data Consistency Tool output to be attached. | “是否已执行以下工具，您是否已解决所有问题？ 5。元素图 6。 IOM复制 7。 IO地图 8。工程数据一致性 附带的工具输出。 |  |  |  | 1
| 1900-01-05 04:48 | Serial Interface Test (MODBUS, Profibus, Ethernet, etc.)
| S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 6.2.1 | Has a clear Schedule been drawn up for the various Tests which include internal IFAT? | 是否为包括内部IFAT在内的各种测试制定了明确的时间表？ |  |  |  | 1
a | 6.2.2 | Has the Engineer who will be conducting the Test been identified? | 是否确定了将进行测试的工程师？ |  |  |  | 1
a | 6.2.3 | Are you using the latest revision of the Communication List? | 您使用的是通讯列表的最新版本吗？ |  |  |  | 1
a | 6.2.4 | Have you configured & debugged the project database? | 您是否配置和调试了项目数据库？ |  |  |  | 1
a | 6.2.5 | Have the relevant HMI been generated & debugged? | 相关的HMI是否已生成和调试？ |  |  |  | 1
| 6.2.6 | Are the communication cables fabricated as per requirement? For serial interface, different subsystems require different pin configurations | 通信电缆是否按要求制造？ 对于串行接口，不同的子系统需要不同的引脚配置 |  |  |  | 1
| 1900-01-05 07:12 | OPC Server Interface Test
| S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 6.3.1 | Has a clear Schedule been drawn up for the various Tests which include internal IFAT? | 是否为包括内部IFAT在内的各种测试制定了明确的时间表？ |  |  |  |  | 1
a | 6.3.2 | Has the Engineer who will be conducting the Test been identified? | 是否确定了将进行测试的工程师？ |  |  |  |  | 1
a | 6.3.3 | Has the Exaopc Server been Setup for Test? | 是否已将Exaopc服务器设置为进行测试？ |  |  |  |  | 1
a | 6.3.4 | Have you identified the hub & cables required for the Test? | 您是否确定了测试所需的集线器和电缆？ |  |  |  |  | 1
| 6.3.5 | Have the relevant HMI been generated & debugged? | 相关的HMI是否已生成和调试？ |  |  |  |  | 1
| 1900-01-05 09:36 | OPC Client interface Test
| S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 6.4.1 | Has a clear Schedule been drawn up for the various Tests which include internal IFAT? | 是否为包括内部IFAT在内的各种测试制定了明确的时间表？ |  |  |  |  | 1
| 6.4.2 | Has the Engineer who will be conducting the Test been identified? | 是否确定了将进行测试的工程师？ |  |  |  |  | 1
| 6.4.3 | Has the GSGW/SIOS/UGS been Setup for Test? | 是否已设置GSGW / SIOS / UGS进行测试？ |  |  |  |  | 1
a | 6.4.4 | Are you using the latest revision of the Communication List? | 您使用的是通讯列表的最新版本吗？ |  |  |  |  | 1
a | 6.4.5 | Have you configured & debugged the project database? | 您是否配置和调试了项目数据库？ |  |  |  |  | 1
a | 6.4.6 | Have you identified the hub & cables required for Test? | 您是否确定了测试所需的集线器和电缆？ |  |  |  |  | 1
a | 6.4.7 | Have the relevant HMI been generated & debugged? | 相关的HMI是否已生成和调试？ |  |  |  |  | 1
a | 1900-01-06 | OTHER NON-DCS ITEMS
a | 1900-01-06 02:24 | Plant Resource Manager
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 7.1.1 | Has the Plant Resource Manager tested? | 工厂资源经理是否经过测试？ |  |  |  |  | 1
a
a | 1900-01-06 04:48 | Sequence of Events Manager (SEM - SoE for DCS)
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 7.2.1 | Has the SoE for DCS tested? | DCS的SoE是否经过测试？ |  |  |  |  | 1
a
a | 1900-01-06 07:12 | EXA Series Packages
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 7.3.1 | Has the EXA packages tested? | EXA包装是否经过测试？ |  |  |  |  | 1
a
a | 1900-01-06 09:36 | Remote Terminal Service
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 7.4.1 | Has the Remote Terminal Server tested? | 远程终端服务器是否经过测试？ |  |  |  |  | 1
a
a | 1900-01-06 12:00 | Operating Training System
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 7.5.1 | Has the OTS tested? | OTS是否经过测试？ |  |  |  |  | 1
a
a | 1900-01-06 14:24 | Time Synchronization
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 7.6.1 | Has the Time synchronization tested? | 时间同步是否经过测试？ |  |  |  |  | 1
a
a
| 1900-01-07 | FAT / IFAT
a | 1900-01-07 02:24 | FAT / IFAT Test Plan
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 8.1.1 | Are the simple loops going to be tested individually or is it a database check? | 简单的循环是要单独测试还是数据库检查？ |  |  |  | 1
a | 8.1.2 | Is the subsystem integration test philosophy clearly spelt out? Only simulation in DCS by mapping I/O or requires actual subsystem. | 子系统集成测试理念是否明确阐明？ 仅在DCS中通过映射I / O进行仿真或需要实际的子系统。 |  |  |  | 1
a | 8.1.3 | Are there any identical complex applications and have you defined a methodology to efficiently test these applications? | 是否有相同的复杂应用程序，您是否定义了有效测试这些应用程序的方法？ |  |  |  | 1
a
a
a | 1900-01-07 04:48 | FAT /IFAT Test Procedure
| S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 8.2.1 | Has the FAT procedure been approved? | FAT程序是否已获批准？ |  |  |  | 1
a | 8.2.2 | Is the software test procedure spelt out clearly in the document? | 文件中是否明确阐明了软件测试程序？ |  |  |  | 1
a | 8.2.3 | Is the DCS engineer conversant with loop demonstration procedure? | DCS工程师是否熟悉环路演示程序？ |  |  |  | 1
a | 8.2.4 | Have you configured CG’s, graphics, simulations in order to demonstrate the complex loop of sequence to make it more effective? | 您是否配置了CG，图形和模拟以演示复杂的序列循环以使其更有效？ |  |  |  | 1
a | 8.2.5 | Have you verified the FAT procedure during Internal Test and made updates in the document if necessary? | 您是否在内部测试期间验证了FAT程序，并在必要时对文档进行了更新？ | No |  |  | 1
a
a
| 1900-01-07 07:12 | FAT Report - Punch List Management System
| S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 8.3.1 | Are you using the electronic punch list management or any other means of punch entry in electronic form for easy compilation of data?  In case you are not using please state the reason. | 您是否正在使用电子打孔清单管理或任何其他电子形式的打孔录入方式来简化数据编辑？如果您不使用，请说明原因。 |  |  |  | 1
a | 8.3.2 | Have you attached the electronic punch list management system procedure as annexure to the FAT Procedure/Plan? | 您是否已将电子打孔清单管理系统程序作为FAT程序/计划的附件？ |  |  |  | 1
| 8.3.3 | Has the punch list entry PC been setup?  Should be shown in the Staging layout | 是否已设置打孔清单输入PC？ 应该显示在暂存布局中 |  |  |  | 1
| 8.3.4 | During FAT Punch lists are generally created by hand. Have people been identified to key this into the Punch list Server or in electronic form (Excel)? | 在FAT打孔列表期间，通常是手动创建的。是否已确定有人将其键入打孔列表服务器或电子形式（Excel）？ |  |  |  | 1
a
| 1900-01-07 09:36 | FAT Report - Customer Master Documents
a | S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 8.4.1 | Have all the customer documents (basis for FAT) been filed and labeled as FAT-MASTER and kept in a central location? | 是否已将所有客户文档（以FAT为基础）归档并标记为FAT-MASTER，并保存在中央位置？ |  |  |  | 1
a | 8.4.2 | Have all the Approved Functional Specifications been filed and labeled as FAT-MASTER and kept in a central location? | 是否已将所有批准的功能规格归档并标记为FAT-MASTER并保存在中央位置？ |  |  |  | 1
a | 8.4.3 | Are all RFI’s and responses been filed and complied?  In some jobs RFI’s (Request For Information) formats are originated by the project team to the customer’s which shall form the basis for engineering and testing. | 是否已提交并遵守了所有RFI和答复？ 在某些工作中，RFI（信息请求）格式是由项目团队向客户提供的，这些格式应构成工程和测试的基础。 |  |  |  | 1
a
a
| 1900-01-07 12:00 | FAT Report - Documents Change Management
| S.No | Check Items |  | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 8.5.1 | Are you clear about how documents change shall be managed during the FAT? | 您是否清楚在FAT期间应如何管理文件更改？ |  |  |  |  | 1
| 8.5.2 | Have you marked up the changes on Master FAT documents with dates and signature? | 您是否用日期和签名标记了FAT主文件上的更改？ |  |  |  | 1
Total

## SE5-Batch
SE5 Checklist - Internal Test for Batch
Template Revision History
| Rev. Nr. | Date | By | Approved |  |  |  | Description
| R03.05 | 2014-11-26 | H.Usami / YHQ | EP & Batch GSME |  |  |  | The items for batch ( Section 5 ) was divided into another sheet by YEF's comment.
| ENDUSER | :
| CUSTOMER | :
| CONSULTANT | :
| PROJECT NAME | :
| PROJECT NUMBER | :
| Name of Participants | :
| Reviewed by / date | :
| Approved by / date | :
Number of Failure Items
Number of Attention Items
Number of OK Items
Number of NA Items
a
a
a | SE5
a
a
a
a | 1900-01-04 | BATCH
a | 1900-01-04 02:24 | General and Recipes
| S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 5.1.1 | Have units, equipment modules and common resources been configured and tested?
| 5.1.2 | Are the groups and the recipes created as per operation philosophy?
| 5.1.3 | Is the RM panel (Product Control View) designed as per the requirement (Standard or custom)?
| 5.1.4 | Have the Recipe procedures and formula data been configured and tested?
| 5.1.5 | Have the common blocks data items and security been configured and tested?
| 5.1.6 | Have Operation and phase design including Pause and Suspend logic been configured and tested?
| 5.1.7 | Is State transition matrix configured and tested? (Standard or custom Matrix)
| 5.1.8 | Are all the Unit procedures configured and tested?
| 5.1.9 | Has proper arbitration of ech shared resource been tested?
| 5.1.10 | Have the equipment modules been tested by starting them in stand-alone mode and also by starting them by a recipe (if applicable)?
| 5.1.11 | Has the Standard header been used consistently throughout the project?
| 5.1.12 | Have the User functions been configured and tested?
a | 5.1.13 | Have the Unit Procedures, SFC Sequences and SEBOL User Functions been copied between FCS's (if required)?
a | 5.1.14 | Have all the recipes been executed (including Pause/Restart on each operation) with no SEBOL run time errors?
a | 5.1.15 | Has the CENTUM VP Batch Cross-Reference tool been run on the completed project and any Errors or Warnings been considered? (R5.03 projects and later)
| 5.1.16 | Have all internal counters or internal variables been normalised or reset in all abnormal conditions?
| 5.1.17 | Is the interface between units configured and tested?
a
a
a | 1900-01-04 04:48 | Batch Reports
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
| 5.2.1 | Are Batch Reports configured and tested?
a
a | 1900-01-04 07:12 | Batch Trend
a | S.No | Check Items | Remarks | FL | AT | OK | NA | Follow-up Action | Action Owner | Due date | Cause category
a | 5.3.1 | Are Batch trends configured and tested?
a
a
Total