## Sheet0
LOOP NO1 | PID_TAG | INSTRUMENT TYPE | COMMENT | P&IDNO | DCSTAG1 | 信号类型1 | REDUN1 | SIGNAL1 | SIGNAL | Unnamed: 10 | QTY | Signal_Detail | IS-BARRIER | IS_Non_IS | CARD#/RACK# | REMARKS | Unnamed: 17 | JB_CABLE_NM1 | J.B.NAME1 | CardTpye | LOOP NO | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | DCSTAG1.1 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28
1840 | 18-TT-61110 | Integral Temperature Transmitter | HCS FROM TA-6101 BOTTOM TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-002-iSC | 18-IJB-40-002 | AI-IS | 1840 | 18- | TI | -61110 | 18-TI-61110 | - | 6 | -
1840 | 18-TT-61102 | Integral Temperature Transmitter | GC TO TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AI-IS | 1840 | 18- | TI | -61102 | 18-TI-61102 | - | 6 | -
1840 | 18-TT-61109 | Integral Temperature Transmitter | GC FROM ET-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AI-IS | 1840 | 18- | TI | -61109 | 18-TI-61109 | - | 6 | -
1840 | 18-TT-61107 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AI-IS | 1840 | 18- | TI | -61107 | 18-TI-61107 | - | 6 | -
1840 | 18-TT-61108 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AI-IS | 1840 | 18- | TI | -61108 | 18-TI-61108 | - | 6 | -
1840 | 18-TT-61104 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AI-IS | 1840 | 18- | TI | -61104 | 18-TI-61104 | - | 6 | -
1840 | 18-TT-61106 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AI-IS | 1840 | 18- | TI | -61106 | 18-TI-61106 | - | 6 | -
1840 | 18-TT-61105 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC., CONTR. | 1840-PS07-611 | TIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AIR-IS | 1840 | 18- | TIC | -61105 | 18-TIC-61105 | - | 6 | -
1840 | 18-TT-61103 | Integral Temperature Transmitter | GC FROM TA-6101 TOP TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-016-iSC | 18-IJB-40-016 | AI-IS | 1840 | 18- | TI | -61103 | 18-TI-61103 | - | 6 | -
Note on B1: a: 带“-”
Note on F1: a: YGET使用 带“-”
Note on S1: a: 现场接线箱电缆名称 （参考设计资料）
Note on T1: a: 现场接线箱名称 （参考设计资料）

## Sheet1
LOCAL
| Job Name.: | 天津渤化发展“两化”搬迁改造项目一期工程
| Process: | PP
| Control Name: | FCS0301 |  |  |  |  | Front | [13 empty] | Rear
| Station Address: | 03.01 | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Cabinet No.:
[8 empty] | AAI143/R | AAI143/R | ADCV01 | ADCV01 | ADV151/R | ADV151/R | EC401 | EC401 | CPU | CPU | Power | Power |  |  | AAI143/R | AAI143/R | AAI543/R | AAI543/R | AAI143 | ADCV01 | ADCV01 | ADCV01 | ESB bus | ESB bus | Power | Power
[5 empty] | Qty. | F1 | [13 empty] | R1
| FCS Model: | AFV30D |  |  | 1
| I/O Node Model: | ANB10D-425/CU2N |  |  | 8 | [16 empty] | NIS | NIS | NIS | NIS | NIS | bar: 1 to 6
|  | ANB10D-425/CU2T |  |  | 1 | [10 empty] | YCB301-C100 | [13 empty] | YCB301-C020
|  | ANB11D-425//BU2A |  |  | 0 |  |  | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADV151 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143 | AAI143 | AAI143 | AAI143 | ADCV01 | ADCV01 | ADV551 | ADV551 | ESB bus | ESB bus | Power | Power
|  | ANB11D-425//BU2B |  |  | 0 | F2 | [13 empty] | R2
|  |  | S | R | [17 empty] | IS | IS | IS | NIS |  |  | dry | dry | bar: 1 to 4; 6 to 8
| I/O Module Model: | AAI143 | [13 empty] | YCB301-C020 | [13 empty] | YCB301-C100
|  | AAI543 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADCV01 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143 | AAI143 | AAI143 | AAI143 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ADV151 |  |  |  | F3 | [13 empty] | R3
ADV551
|  | AAP135 | [19 empty] | IS | IS | IS | NIS |  |  | dry | dry | bar: 1 to 4; 7 to 8
|  | ALP121 | [13 empty] | YCB301-C100 | [13 empty] | YCB301-C020
|  | ALR121 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADCV01 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143 | AAI143 | AAI143 | AAI143 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ALE111 |  |  |  | F4 | [13 empty] | R4
ADCV01
|  | YCB301-C020 | [19 empty] | IS | IS | IS | NIS |  |  | 24v | 24v | bar: 1 to 4; 7 to 8
|  | YCB301-C100 | [13 empty] | YCB301-C020 | [13 empty] | YCB301-C100
|  | YCB301-C200 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADCV01 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143 | AAI143 | AAI143 | AAI143 | ALE111 | ADCV01 | ADCV01 | ADV551 | ESB bus | ESB bus | Power | Power
[6 empty] | F5 | [13 empty] | R5
| Single: | S | [19 empty] | IS | IS | NIS | NIS |  |  |  | dry | bar: 1 to 4; 7 to 8
| Redundant: | R | [13 empty] | YCB301-C200
[30 empty] | Page： |  |  | /

## Sheet2
LOCAL
| Job Name.: | 天津渤化发展“两化”搬迁改造项目一期工程
| Process: | PP
| Control Name: | FCS0302 |  |  |  |  | Front | [13 empty] | Rear
| Station Address: | 03.02 | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Cabinet No.:
[8 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADV151/R | ADV151/R | EC401 | EC401 | CPU | CPU | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | AAI143 | AAI143 | ADV551 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
[5 empty] | Qty. | F1 | [13 empty] | R1
| FCS Model: | AFV30D |  |  | 1
| I/O Node Model: | ANB10D-425/CU2N |  |  | 8 | [16 empty] | IS | IS | IS | IS | IS | dry | dry | dry | bar: 1 to 6
|  | ANB10D-425/CU2T |  |  | 1 | [10 empty] | YCB301-C100 | [13 empty] | YCB301-C020
|  | ANB11D-425//BU2A |  |  | 0 |  |  | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADV151 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | AAI143 | AAI143 | ADV551 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ANB11D-425//BU2B |  |  | 0 | F2 | [13 empty] | R2
|  |  | S | R | [17 empty] | IS | IS | IS | IS | NIS | 24v | dry | dry | bar: 1 to 4; 6 to 8
| I/O Module Model: | AAI143 | [13 empty] | YCB301-C020 | [13 empty] | YCB301-C100
|  | AAI543 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADV151 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | 1 | AAI143/R | AAI143/R | AAI143/R | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ADV151 |  |  |  | F3 | [13 empty] | R3
ADV551
|  | AAP135 | [5 empty] | IS | IS | IS | IS |  | RE | MI | MI | [6 empty] | IS | IS | NIS | NIS |  |  | dry | dry
|  | ALP121 | [13 empty] | YCB301-C100 | [13 empty] | YCB301-C020
|  | ALR121 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADV151 | ADV151/R | ADV151/R | ESB bus | ESB bus | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | AAI143 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ALE111 |  |  |  | F4 | [13 empty] | R4
ADCV01
|  | YCB301-C020 | [19 empty] | NIS | NIS | NIS | NIS |  |  | 24v | 24v | bar: 1 to 4; 6 to 8
|  | YCB301-C100 | [13 empty] | YCB301-C020 | [13 empty] | YCB301-C100
|  | YCB301-C200 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADV151 | ADV151/R | ADV151/R | ESB bus | ESB bus | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | AAI143 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
[6 empty] | F5 | [13 empty] | R5
| Single: | S | [5 empty] | IS | IS | NIS | NIS |  | RE | RE | RE | [6 empty] | NIS | NIS | NIS | NIS |  |  | 24v | 24v
| Redundant: | R | [13 empty] | YCB301-C200
[30 empty] | Page： |  |  | /

## Sheet3
LOCAL
| Job Name.: | 天津渤化发展“两化”搬迁改造项目一期工程
| Process: | PP
| Control Name: | FCS0303 |  |  |  |  | Front | [13 empty] | Rear
| Station Address: | 03.03 | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Cabinet No.:
[8 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADV151/R | ADV151/R | EC401 | EC401 | CPU | CPU | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | ADV151 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
[5 empty] | Qty. | F1 | [13 empty] | R1
| FCS Model: | AFV30D |  |  | 1
| I/O Node Model: | ANB10D-425/CU2N |  |  | 8 | [16 empty] | IS | IS | IS | IS |  |  | dry | dry | bar: 1 to 6
|  | ANB10D-425/CU2T |  |  | 1 | [10 empty] | YCB301-C100 | [13 empty] | YCB301-C020
|  | ANB11D-425//BU2A |  |  | 0 |  |  | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADV151 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | ALE111 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ANB11D-425//BU2B |  |  | 0 | F2 | [13 empty] | R2
|  |  | S | R | [17 empty] | IS | IS | IS |  |  |  | dry | dry | bar: 1 to 4; 6 to 8
| I/O Module Model: | AAI143 | [13 empty] | YCB301-C020 | [13 empty] | YCB301-C100
|  | AAI543 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADV151 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | AAI143 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ADV151 |  |  |  | F3 | [13 empty] | R3
ADV551
|  | AAP135 | [5 empty] | IS | IS | IS | IS |  | RE | MI | MI | [6 empty] | NIS | NIS | NIS | NIS |  |  | 24v | 24v
|  | ALP121 | [13 empty] | YCB301-C100 | [13 empty] | YCB301-C020
|  | ALR121 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADV151 | ADV151/R | ADV151/R | ESB bus | ESB bus | Power | Power |  |  | AAI143 | AAI143 | AAI143 | AAI143 | ADCV01 | ADCV01 | ADCV01 | ADV551 | ESB bus | ESB bus | Power | Power
|  | ALE111 |  |  |  | F4 | [13 empty] | R4
ADCV01
|  | YCB301-C020 | [19 empty] | IS | IS | NIS | NIS |  |  |  | dry | bar: 1 to 4; 6 to 8
|  | YCB301-C100 | [13 empty] | YCB301-C020 | [13 empty] | YCB301-C100
|  | YCB301-C200 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADV151 | ADV151/R | ADV151/R | ESB bus | ESB bus | Power | Power |  |  | AAI143 | AAI143 | AAI143 | AAI143 | ADCV01 | ADCV01 | ADCV01 | ADV551 | ESB bus | ESB bus | Power | Power
[6 empty] | F5 | [13 empty] | R5
| Single: | S | [5 empty] | IS | IS | NIS | NIS |  | RE | IS | IS | [6 empty] | IS | IS | NIS | NIS |  |  |  | 24v
| Redundant: | R | [13 empty] | YCB301-C200
[30 empty] | Page： |  |  | /

## Sheet4
LOCAL
| Job Name.: | 天津渤化发展“两化”搬迁改造项目一期工程
| Process: | PP
| Control Name: | FCS0304 |  |  |  |  | Front | [13 empty] | Rear
| Station Address: | 03.04 | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Cabinet No.:
[8 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADV151/R | ADV151/R | EC401 | EC401 | CPU | CPU | Power | Power |  |  | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
[5 empty] | Qty. | F1 | [13 empty] | R1
| FCS Model: | AFV30D |  |  | 1
| I/O Node Model: | ANB10D-425/CU2N |  |  | 8 | [16 empty] | IS | IS | NIS | NIS |  |  | dry | dry | bar: 1 to 6
|  | ANB10D-425/CU2T |  |  | 1 | [10 empty] | YCB301-C100 | [13 empty] | YCB301-C020
|  | ANB11D-425//BU2A |  |  | 0 |  |  | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADV151 | ADCV01 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ANB11D-425//BU2B |  |  | 0 | F2 | [13 empty] | R2
|  |  | S | R | [17 empty] | NIS | NIS | NIS | NIS |  |  | dry | dry | bar: 1 to 5; 7 to 8
| I/O Module Model: | AAI143 | [13 empty] | YCB301-C020 | [13 empty] | YCB301-C100
|  | AAI543 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ALE111 | ADCV01 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143 | AAI143 | AAI143 | AAI143 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ADV151 |  |  |  | F3 | [13 empty] | R3
ADV551
|  | AAP135 | [19 empty] | IS | IS | IS | IS |  |  | dry | dry | bar: 1 to 4; 7 to 8
|  | ALP121 | [13 empty] | YCB301-C100 | [13 empty] | YCB301-C020
|  | ALR121 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ALE111 | ADCV01 | ADV151/R | ADV151/R | ESB bus | ESB bus | Power | Power |  |  | AAI143 | AAI143 | ADV151 | ADV151 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ALE111 |  |  |  | F4 | [13 empty] | R4
ADCV01
|  | YCB301-C020 | [19 empty] | IS | IS | RE | RE |  |  | 24v | 24v | bar: 1 to 4; 7 to 8
|  | YCB301-C100 | [13 empty] | YCB301-C020 | [13 empty] | YCB301-C100
|  | YCB301-C200 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADCV01 | ADCV01 | ADV151/R | ADV151/R | ESB bus | ESB bus | Power | Power |  |  | AAI143 | AAI143 | ADV151 | ADV151 | ADCV01 | ADCV01 | ADV551 | ADV551
[6 empty] | F5 | [13 empty] | R5
| Single: | S | [19 empty] | NIS | NIS | RE | RE |  |  | 24v | dry | bar: 1 to 4; 7 to 8
| Redundant: | R | [13 empty] | YCB301-C200
[30 empty] | Page： |  |  | /

## Sheet5
LOCAL
| Job Name.: | 天津渤化发展“两化”搬迁改造项目一期工程
| Process: | PP
| Control Name: | FCS0305 |  |  |  |  | Front | [13 empty] | Rear
| Station Address: | 03.05 | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Cabinet No.:
[8 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ADV151/R | ADV151/R | EC401 | EC401 | CPU | CPU | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | ADV151 | ADCV01 | ADV551 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
[5 empty] | Qty. | F1 | [13 empty] | R1
| FCS Model: | AFV30D |  |  | 1
| I/O Node Model: | ANB10D-425/CU2N |  |  | 8 | [16 empty] | IS | IS | IS | IS |  | dry | dry | dry | bar: 1 to 6
|  | ANB10D-425/CU2T |  |  | 1 | [10 empty] | YCB301-C100 | [13 empty] | YCB301-C020
|  | ANB11D-425//BU2A |  |  | 0 |  |  | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ALE111 | ADCV01 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | ADV151 | ADCV01 | ADV551 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ANB11D-425//BU2B |  |  | 0 | F2 | [13 empty] | R2
|  |  | S | R | [17 empty] | IS | IS | IS | RE |  | dry | dry | dry | bar: 1 to 4; 7 to 8
| I/O Module Model: | AAI143 | [13 empty] | YCB301-C020 | [13 empty] | YCB301-C100
|  | AAI543 | [5 empty] | AAI143/R | AAI143/R | AAI543/R | AAI543/R | ALE111 | ADCV01 | ADV151/R | ADV151/R | ESB bus | ESB bus | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | ADV151 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ADV151 |  |  |  | F3 | [13 empty] | R3
ADV551
|  | AAP135 | [5 empty] | IS | IS | NIS | NIS |  |  | IS | IS | [6 empty] | IS | IS | IS | RE |  |  | 24v | 24v
|  | ALP121 | [13 empty] | YCB301-C100 | [13 empty] | YCB301-C020
|  | ALR121 | [5 empty] | AAI143/R | AAI143/R | AAI143 | AAI143 | ALR121 | ADCV01 | ADV151/R | ADV151/R | ESB bus | ESB bus | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | ADV151 | ADCV01 | ADCV01 | ADV551/R | ADV551/R | ESB bus | ESB bus | Power | Power
|  | ALE111 |  |  |  | F4 | [13 empty] | R4
ADCV01
|  | YCB301-C020 | [19 empty] | IS | IS | IS | RE |  |  | 24v | 24v | bar: 1 to 4; 7 to 8
|  | YCB301-C100 | [13 empty] | YCB301-C020 | [13 empty] | YCB301-C100
|  | YCB301-C200 | [5 empty] | AAI143/R | AAI143/R | AAI143 | AAI143 | ALR121 | ADCV01 | ADV151 | ADV151 | ESB bus | ESB bus | Power | Power |  |  | AAI143/R | AAI143/R | AAI143 | ADV151 | ADCV01 | ADCV01 | ADV551 | ADV551 | ESB bus | ESB bus | Power | Power
[6 empty] | F5 | [13 empty] | R5
| Single: | S | [19 empty] | NIS | NIS | NIS | RE |  |  | 24v | 24v | bar: 1 to 4; 7 to 8
| Redundant: | R | [13 empty] | YCB301-C200
[30 empty] | Page： |  |  | /

## Sheet11
| LOOP NO1 | PID_TAG | INSTRUMENT TYPE | COMMENT | P&IDNO | DCSTAG1 | 信号类型1 | REDUN1 | SIGNAL1 | SIGNAL | Unnamed: 10 | QTY | Signal_Detail | IS-BARRIER | IS_Non_IS | CARD#/RACK# | REMARKS | Unnamed: 17 | JB_CABLE_NM1 | J.B.NAME1 | CardTpye | LOOP NO | Unnamed: 22 | Unnamed: 23 | Unnamed: 24 | DCSTAG1.1 | Unnamed: 26 | Unnamed: 27 | Unnamed: 28
0 | 1840 | 18-TT-61110 | Integral Temperature Transmitter | HCS FROM TA-6101 BOTTOM TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-002-iSC | 18-IJB-40-002 | AI-IS | 1840 | 18- | TI | -61110 | 18-TI-61110 | - | 6 | -
1 | 1840 | 18-TT-61102 | Integral Temperature Transmitter | GC TO TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AI-IS | 1840 | 18- | TI | -61102 | 18-TI-61102 | - | 6 | -
2 | 1840 | 18-TT-61109 | Integral Temperature Transmitter | GC FROM ET-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AI-IS | 1840 | 18- | TI | -61109 | 18-TI-61109 | - | 6 | -
3 | 1840 | 18-TT-61107 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AI-IS | 1840 | 18- | TI | -61107 | 18-TI-61107 | - | 6 | -
4 | 1840 | 18-TT-61108 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AI-IS | 1840 | 18- | TI | -61108 | 18-TI-61108 | - | 6 | -
5 | 1840 | 18-TT-61104 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AI-IS | 1840 | 18- | TI | -61104 | 18-TI-61104 | - | 6 | -
6 | 1840 | 18-TT-61106 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AI-IS | 1840 | 18- | TI | -61106 | 18-TI-61106 | - | 6 | -
7 | 1840 | 18-TT-61105 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC., CONTR. | 1840-PS07-611 | TIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AIR-IS | 1840 | 18- | TIC | -61105 | 18-TIC-61105 | - | 6 | -
8 | 1840 | 18-TT-61103 | Integral Temperature Transmitter | GC FROM TA-6101 TOP TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes | Y | - | - | C01 | 18-40-016-iSC | 18-IJB-40-016 | AI-IS | 1840 | 18- | TI | -61103 | 18-TI-61103 | - | 6 | -