## Sheet1
| DIOTAG | AREA | PID_TAG | COMMENT | LOOP | TYPNO | FCS_Comp_Name | Station_Name | NODE_Seq_No | SLOT_Seq_No | Channel | IOMODULE | SIGNAL | DUPLEX | DRWNO | DCSTAG | TGCOMM | ENG_LO | ENG_HI | ENG_UNITS | IOADDR/SYSTAG | TAGMARK | COMMAND | FF_Segment_Name | signal_origin | SB-Surge | SB-Surge Detial | IS_Non_IS | IS_Non_IS Detial | IO_type | Signal_Location | Signal_Detail | SIGNAL_LEVEL | TAG.NO. 1 | 2/3/4 WIRE 2 | J.B.NAME 3 | JB_CABLE_NM | Core.No._Tot | CHANNEL 4 | JB_CABLE_PAIR | JB_CABLE_SET_LEVEL | MRP_COMP_Name 5 | TS_Name 6 | TS_Channel | TS1 7 | TS2 8 | TS3 9 | TS 10 | TS 11 | TS 12 | TB No. 13 | TB Model 14 | TP_TS1 12 | TP_TS2 13 | TP_TS3 14 | Signal | ALARM_HI | ALARM_HH | ALARM_LO | ALARM_LL | Y_REV_NO | Y_REV_COMMENT | PID_SHT | Remarks
0 | %%I5501-01CEMS006DCS | 5501 | 5501-01CEMS006DCS | #1 Boiler SNCR outlet NOX #1锅炉脱硝SNCR出口NOx |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 1 | AAI143-H | 4-20mA | N |  | 5501-01CEMS006DCS | #1 B SNCR OUT NOX | 0 | 1000 | mg/Nm3 | %Z011101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01CEMS006DCS | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 1A | 1B
16 | %%I5501-01PT3404 | 5501 | 5501-01PT3404 | #1 Boiler closed circulating water of induced draft fan inlet main pipe pressure #1锅炉引风机闭式循环冷却水进水母管压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 1 | AAI143-H | 4-20mA | N |  | 5501-01PT3404 | #1 B CC IDF IN MP Pre | 0 | 1 | Mpa | %Z012101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT3404 | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 1A | 1B
464 | %%I5501-01Y01A-M31 | 5501 | 5501-01Y01A-M31 | #1炉给煤机A累计脉冲 #1 Boiler coal feeder A accumulated pulse |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 3 | 1 | AAP135-S | PI | N |  | 5501-01Y01A-M31 | #1 B coal feed A pulse |  |  |  | %Z013101 |  |  |  | DCS | Y | PI Surge protective device PI防雷栅 | N |  | AI |  |  |  | 01-Y-01A(M)-31 | [7 empty] | 5501-01DCS-AMC-02 | SPD09 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPB09 | A1BA4D-05 | 2A | 2B
32 | %%I5501-01LT0101 | 5501 | 5501-01LT0101 | #1 Boiler steam drum level 3 #1锅炉汽包水位3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01LT0101 | #1 BSD Lev. 3 | -430 | 430 | mm | %Z021101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01LT0101 | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 1A | 1B
96 | %%I5501-01CV0101-06 | 5501 | 5501-01CV0101-06 | #1 Boiler economizer inlet water supply electric control valve position #1锅炉省煤器进口给水电动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01CV0101-06 | #1 BEI WS ECV ZF | 0 | 100 | % | %Z023101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0101-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 1B | 1A
224 | %%I5501-01TE0101 | 5501 | 5501-01TE0101 | #1 Boiler economizer inlet feed water temperature #1锅炉省煤器进口给水温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0101 | #1 BEI FW Temp. | 0 | 300 | ℃ | %Z025101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0101 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 1 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
480 | %%O5501-01CV0101-05 | 5501 | 5501-01CV0101-05 | #1 Boiler economizer inlet water supply electric control valve control command #1锅炉省煤器进口给水电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 1 | AAI543-H | 4-20mA | Y |  | 5501-01CV0101-05 | #1 BEI WS ECV CO | 0 | 100 | % | %Z027101 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0101-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 1A | 1B
48 | %%I5501-01LT0102 | 5501 | 5501-01LT0102 | #1 Boiler steam drum level 4 #1锅炉汽包水位4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01LT0102 | #1 BSD Lev. 4 | -430 | 430 | mm | %Z031101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01LT0102 | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 1A | 1B
112 | %%I5501-01CV0102-06 | 5501 | 5501-01CV0102-06 | #1 Boiler economizer inlet bypass water supply electric control valve position #1锅炉省煤器进口旁路给水电动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01CV0102-06 | #1 BEI BWS ECV ZF | 0 | 100 | % | %Z033101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0102-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 1B | 1A
240 | %%I5501-01TE0102 | 5501 | 5501-01TE0102 | #1 Boiler economizer outlet temperature 1 #1锅炉省煤器出口温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0102 | #1 BE OUT Temp. 1 | 0 | 400 | ℃ | %Z035101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0102 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 1 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
496 | %%O5501-01CV0102-05 | 5501 | 5501-01CV0102-05 | #1 Boiler economizer inlet bypass water supply electric control valve control command #1锅炉省煤器进口旁路给水电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 1 | AAI543-H | 4-20mA | Y |  | 5501-01CV0102-05 | #1 BEI BWS ECV CO | 0 | 100 | % | %Z037101 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0102-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 1A | 1B
64 | %%I5501-01LT0103 | 5501 | 5501-01LT0103 | #1 Boiler steam drum level 5 #1锅炉汽包水位5 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01LT0103 | #1 BSD Lev. 5 | -430 | 430 | mm | %Z041101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01LT0103 | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 1A | 1B
128 | %%I5501-01CV0501A-06 | 5501 | 5501-01CV0501A-06 | #1 Boiler primary air fan A inlet motor control damper position #1锅炉一次风A机入口电动调节挡板阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01CV0501A-06 | #1 B PAF A IN MCD ZF | 0 | 100 | % | %Z043101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0501A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 1B | 1A
256 | %%I5501-01TE0103 | 5501 | 5501-01TE0103 | #1 Boiler economizer outlet temperature 2 #1锅炉省煤器出口温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0103 | #1 BE OUT Temp. 2 | 0 | 400 | ℃ | %Z045101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0103 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 1 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
512 | %%O5501-01CV0501A-05 | 5501 | 5501-01CV0501A-05 | #1 Boiler primary air fan A inlet motor control damper control command #1锅炉一次风A机入口电动调节挡板控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 1 | AAI543-H | 4-20mA | Y |  | 5501-01CV0501A-05 | #1 B PAF A IN MCD CO | 0 | 100 | % | %Z047101 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0501A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 1A | 1B
80 | %%I5501-01FT0104 | 5501 | 5501-01FT0104 | #1 Boiler right side secondary spray desuperheater feed water flow #1锅炉右侧二级喷水减温器减温水流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01FT0104 | #1 B RS SSD FW flow | 0 | 5.8 | t/h | %Z051101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0104 | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 1A | 1B
144 | %%I5501-01CV0501B-06 | 5501 | 5501-01CV0501B-06 | #1 Boiler primary air fan B inlet motor control damper position #1锅炉一次风机B入口电动调节挡板阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01CV0501B-06 | #1 B PAF B IN MCD ZF | 0 | 100 | % | %Z053101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0501B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 1B | 1A
272 | %%I5501-01TE0116 | 5501 | 5501-01TE0116 | #1 Boiler superheater desuperheating water temperature #1锅炉过热器减温水母管温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0116 | #1 B SD W Temp.. | 0 | 300 | ℃ | %Z055101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0116 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 1 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
528 | %%O5501-01CV0501B-05 | 5501 | 5501-01CV0501B-05 | #1 Boiler primary air fan B inlet motor control damper control command #1锅炉一次风机B入口电动调节挡板控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 1 | AAI543-H | 4-20mA | Y |  | 5501-01CV0501B-05 | #1 B PAF B IN MCD CO | 0 | 100 | % | %Z057101 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0501B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 1A | 1B
160 | %%I5501-01FIT0901A | 5501 | 5501-01FIT0901A | #1 Boiler coal feeder A instantaneous flow #1锅炉给煤机A瞬时流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01FIT0901A | #1 B CF A Inst flow | 0 | 27 | t/h | %Z061101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FIT0901A | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 1A | 1B
288 | %%I5501-01TE0213 | 5501 | 5501-01TE0213 | #1 Boiler High temperature superheater outlet temperature 1 #1锅炉高温过热器出口温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0213 | #1 B HTS OUT Temp. 1 | 0 | 700 | ℃ | %Z063101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0213 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 1 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
352 | %%I5501-01TE0901A | 5501 | 5501-01TE0901A | #1 Boiler furnace front wall upside bed temperature 1 #1锅炉炉膛前墙上层床温温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0901A | #1 B furnaceFW UP bed T1 | 0 | 1300 | ℃ | %Z064101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0901A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 1 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
544 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 1 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 400 | t/h | %Z067101 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 1A | 1B | [9 empty] | 2017.12.1删除
640 | 5501-01CV0501A-07 | 5501 | 5501-01CV0501A-07 | #1 Boiler primary air fan A inlet motor control damper fault #1锅炉一次风机A入口电动调节挡板执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 1 | ADV151-P | SI | Y |  | 5501-01CV0501A-07 | #1 B PAF A IN MCD F |  |  |  | %Z065101 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0501A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 1A | 1B
176 | %%I5501-01FIT0901B | 5501 | 5501-01FIT0901B | #1 Boiler coal feeder B instantaneous flow #1锅炉给煤机B瞬时流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01FIT0901B | #1 B CF B Inst flow | 0 | 27 | t/h | %Z071101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FIT0901B | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 1A | 1B
304 | %%I5501-01TE0214 | 5501 | 5501-01TE0214 | #1 Boiler High temperature superheater outlet temperature 2 #1锅炉高温过热器出口温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0214 | #1 B HTS OUT Temp. 2 | 0 | 700 | ℃ | %Z073101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0214 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 1 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
368 | %%I5501-01TE0902A | 5501 | 5501-01TE0902A | #1 Boiler furnace front wall upside bed temperature 2 #1锅炉炉膛前墙上层床温温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0902A | #1 B furnaceFW UP bed T2 | 0 | 1300 | ℃ | %Z074101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0902A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 1 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
416 | %%I5501-01TE0501A | 5501 | 5501-01TE0501A | #1 Boiler air heater inlet cool primary air temperature 1 #1锅炉空预器入口冷一次风温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0501A | #1 B AH IN CPA Temp. 1 | 0 | 100 | ℃ | %Z075101 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  | 5501-01TE0501A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 1 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
576 | 5501-01CV0101-07 | 5501 | 5501-01CV0101-07 | #1 Boiler economizer inlet water supply electric control valve fault #1锅炉省煤器进口给水电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 1 | ADV151-P | SI | N |  | 5501-01CV0101-07 | #1 BEI WS ECV F |  |  |  | %Z076101 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0101-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 1A | 1B
192 | %%I5501-01FIT0901C | 5501 | 5501-01FIT0901C | #1 Boiler coal feeder C instantaneous flow #1锅炉给煤机C瞬时流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01FIT0901C | #1 B CF C Inst flow | 0 | 27 | t/h | %Z081101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FIT0901C | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 1A | 1B
320 | %%I5501-01TE0215 | 5501 | 5501-01TE0215 | #1 Boiler High temperature superheater outlet temperature 3 #1锅炉高温过热器出口温度3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0215 | #1 B HTS OUT Temp. 3 | 0 | 700 | ℃ | %Z083101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0215 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 1 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
384 | %%I5501-01TE0903A | 5501 | 5501-01TE0903A | #1 Boiler furnace front wall upside bed temperature 3 #1锅炉炉膛前墙上层床温温度3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0903A | #1 B furnaceFW UP bed T3 | 0 | 1300 | ℃ | %Z084101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0903A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 1 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
432 | %%I5501-01TE0501B | 5501 | 5501-01TE0501B | #1 Boiler air heater inlet cool primary air temperature 2 #1锅炉空预器入口冷一次风温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0501B | #1 B AH IN CPA Temp. 2 | 0 | 100 | ℃ | %Z085101 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  | 5501-01TE0501B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 1 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
608 | 5501-01CV0102-07 | 5501 | 5501-01CV0102-07 | #1 Boiler economizer inlet bypass water supply electric control valve fault #1锅炉省煤器进口旁路给水电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 1 | ADV151-P | SI | N |  | 5501-01CV0102-07 | #1 BEI BWS ECV F |  |  |  | %Z086101 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0102-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 1A | 1B
208 | %%I5501-01FIT0901D | 5501 | 5501-01FIT0901D | #1 Boiler coal feeder D instantaneous flow #1锅炉给煤机D瞬时流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 1 | AAI143-H | 4-20mA | Y |  | 5501-01FIT0901D | #1 B CF D Inst flow | 0 | 27 | t/h | %Z091101 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FIT0901D | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 1A | 1B
336 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 1 | AAI143-H | 4-20mA | N |  |  |  | 0 | 600 | ℃ | %Z093101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 1 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
400 | %%I5501-01TE0904A | 5501 | 5501-01TE0904A | #1 Boiler furnace front wall upside bed temperature 4 #1锅炉炉膛前墙上层床温温度4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0904A | #1 B furnaceFW UP bed T4 | 0 | 1300 | ℃ | %Z094101 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0904A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 1 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
448 | %%I5501-01TE0521 | 5501 | 5501-01TE0521 | #1 Boiler high pressure fluidization fan outlet main pipe temperature #1锅炉高压流化风机出口母管温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 1 | AAI143-H | 4-20mA | N |  | 5501-01TE0521 | #1 B HPFA OUT MP Temp. | 0 | 150 | ℃ | %Z095101 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  | 5501-01TE0521 | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 1 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
560 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 1 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 400 | t/h | %Z097101 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD06 | 1 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 1A | 1B | [9 empty] | 2017.12.1删除
1 | %%I5501-01CEMS007DCS | 5501 | 5501-01CEMS007DCS | #1 Boiler SNCR outlet O2 #1锅炉脱硝SNCR出口O2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 2 | AAI143-H | 4-20mA | N |  | 5501-01CEMS007DCS | #1 B SNCR OUT O2 | 0 | 25 | % | %Z011102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01CEMS007DCS | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 2A | 2B
17 | %%I5501-01FT1101 | 5501 | 5501-01FT1101 | #1 Boiler dilution water flow #1锅炉稀释水流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 2 | AAI143-H | 4-20mA | N |  | 5501-01FT1101 | #1 B diutionSOL flow | 0 | 1.2 | m3/h | %Z012102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT1101 | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 2A | 2B
465 | %%I5501-01Y01B-M31 | 5501 | 5501-01Y01B-M31 | #1炉给煤机B累计脉冲 #1 Boiler coal feeder B accumulated pulse |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 3 | 2 | AAP135-S | PI | N |  | 5501-01Y01B-M31 | #1 B coal feed B pulse |  |  |  | %Z013102 |  |  |  | DCS | Y | PI Surge protective device PI防雷栅 | N |  | AI |  |  |  | 01-Y-01B(M)-31 | [7 empty] | 5501-01DCS-AMC-02 | SPD09 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPB09 | A1BA4D-05 | 4A | 4B
33 | %%I5501-01PT0102 | 5501 | 5501-01PT0102 | #1 Boiler steam drum pressure 1 #1锅炉汽包压力1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01PT0102 | #1 BSD Pre. 1 | 0 | 12 | MPa | %Z021102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0102 | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 2A | 2B
97 | %%I5501-01CV0103-06 | 5501 | 5501-01CV0103-06 | #1 Boiler left side primary spray desuperheater inlet electric control valve position #1锅炉左侧一级喷水减温器进口电动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01CV0103-06 | #1 B LS PSD IN ECV ZF | 0 | 100 | % | %Z023102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0103-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 2B | 2A
225 | %%I5501-01TE0104 | 5501 | 5501-01TE0104 | #1 Boiler steam drum outer temperature 1 #1锅炉汽包外壁温1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0104 | #1 BSD OUT Temp. 1 | 0 | 400 | ℃ | %Z025102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0104 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 2 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
481 | %%O5501-01CV0103-05 | 5501 | 5501-01CV0103-05 | #1 Boiler left side primary spray desuperheater inlet electric control valve control command #1锅炉左侧一级喷水减温器进口电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 2 | AAI543-H | 4-20mA | Y |  | 5501-01CV0103-05 | #1 B LS PSD IN ECV CO | 0 | 100 | % | %Z027102 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0103-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 2A | 2B
49 | %%I5501-01PT0103 | 5501 | 5501-01PT0103 | #1 Boiler steam drum pressure 2 #1锅炉汽包压力2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01PT0103 | #1 BSD Pre. 2 | 0 | 12 | MPa | %Z031102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0103 | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 2A | 2B
113 | %%I5501-01CV0104-06 | 5501 | 5501-01CV0104-06 | #1 Boiler right side primary spray desuperheater inlet electric control valve position #1锅炉右侧一级喷水减温器进口电动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01CV0104-06 | #1 B RS PSD IN ECV ZF | 0 | 100 | % | %Z033102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0104-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 2B | 2A
241 | %%I5501-01TE0106 | 5501 | 5501-01TE0106 | #1 Boiler steam drum outer temperature 3 #1锅炉汽包外壁温3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0106 | #1 BSD OUT Temp. 3 | 0 | 400 | ℃ | %Z035102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0106 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 2 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
497 | %%O5501-01CV0104-05 | 5501 | 5501-01CV0104-05 | #1 Boiler right side primary spray desuperheater inlet electric control valve control command #1锅炉右侧一级喷水减温器进口电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 2 | AAI543-H | 4-20mA | Y |  | 5501-01CV0104-05 | #1 B RS PSD IN ECV CO | 0 | 100 | % | %Z037102 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0104-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 2A | 2B
65 | %%I5501-01PT0104 | 5501 | 5501-01PT0104 | #1 Boiler steam drum pressure 3 #1锅炉汽包压力3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01PT0104 | #1 BSD Pre. 3 | 0 | 12 | MPa | %Z041102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0104 | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 2A | 2B
129 | %%I5501-01CV0105-06 | 5501 | 5501-01CV0105-06 | #1 Boiler left side secondary spray desuperheater inlet electric control valve position #1锅炉左侧二级喷水减温器进口电动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01CV0105-06 | #1 B LS SSD IN ECV ZF | 0 | 100 | % | %Z043102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0105-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 2B | 2A
257 | %%I5501-01TE0108 | 5501 | 5501-01TE0108 | #1 Boiler steam drum outer temperature 5 #1锅炉汽包外壁温5 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0108 | #1 BSD OUT Temp. 5 | 0 | 400 | ℃ | %Z045102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0108 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 2 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
513 | %%O5501-01CV0105-05 | 5501 | 5501-01CV0105-05 | #1 Boiler left side secondary spray desuperheater inlet electric control valve control command #1锅炉左侧二级喷水减温器进口电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 2 | AAI543-H | 4-20mA | Y |  | 5501-01CV0105-05 | #1 B LS SSD IN ECV CO | 0 | 100 | % | %Z047102 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0105-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 2A | 2B
81 | %%I5501-01FT0501B | 5501 | 5501-01FT0501B | #1 Boiler right hot primary air flow #1锅炉右侧热一次风流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01FT0501B | #1 B RHPA flow | 0 | 120339 | Nm3/h | %Z051102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0501B | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 2A | 2B
145 | %%I5501-01CV0106-06 | 5501 | 5501-01CV0106-06 | #1 Boiler right side secondary spray desuperheater inlet electric control valve position #1锅炉右侧二级喷水减温器进口电动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01CV0106-06 | #1 B RS SSD IN ECV ZF | 0 | 100 | % | %Z053102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0106-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 2B | 2A
273 | %%I5501-01TE0110 | 5501 | 5501-01TE0110 | #1 Boiler steam drum outer temperature 7 #1锅炉汽包外壁温7 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0110 | #1 BSD OUT Temp. 7 | 0 | 400 | ℃ | %Z055102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0110 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 2 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
529 | %%O5501-01CV0106-05 | 5501 | 5501-01CV0106-05 | #1 Boiler right side secondary spray desuperheater inlet electric control valve control command #1锅炉右侧二级喷水减温器进口电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 2 | AAI543-H | 4-20mA | Y |  | 5501-01CV0106-05 | #1 B RS SSD IN ECV CO | 0 | 100 | % | %Z057102 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0106-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 2A | 2B
161 | %%I5501-01LT0901A | 5501 | 5501-01LT0901A | #1 Boiler raw coal bunker A material level #1锅炉原煤仓A料位 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01LT0901A | #1 B RCB A Lev. | 0 | 16 | m | %Z061102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01LT0901A | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 2A | 2B
289 | %%I5501-01TE0216 | 5501 | 5501-01TE0216 | #1 Boiler low temperature superheater pipe surface temperature 1 #1锅炉低温过热器管壁温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0216 | #1 B LTS PS Temp. 1 | 0 | 600 | ℃ | %Z063102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0216 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 2 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
353 | %%I5501-01TE0901B | 5501 | 5501-01TE0901B | #1 Boiler furnace back wall upside bed temperature 1 #1锅炉炉膛后墙上层床温温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0901B | #1 B furnaceBW UP bed T1 | 0 | 1300 | ℃ | %Z064102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0901B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 2 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
545 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 2 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 16 | Mpa | %Z067102 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 2A | 2B | [9 empty] | 2017.12.1删除
641 | 5501-01CV0501B-07 | 5501 | 5501-01CV0501B-07 | #1 Boiler primary air fan B inlet motor control damper fault #1锅炉一次风机B入口电动调节挡板执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 2 | ADV151-P | SI | Y |  | 5501-01CV0501B-07 | #1 B PAF B IN MCD F |  |  |  | %Z065102 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0501B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 2A | 2B
177 | %%I5501-01LT0901B | 5501 | 5501-01LT0901B | #1 Boiler raw coal bunker B material level #1锅炉原煤仓B料位 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01LT0901B | #1 B RCB B Lev. | 0 | 16 | m | %Z071102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01LT0901B | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 2A | 2B
305 | %%I5501-01TE0218 | 5501 | 5501-01TE0218 | #1 Boiler low temperature superheater pipe surface temperature 3 #1锅炉低温过热器管壁温度3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0218 | #1 B LTS PS Temp. 3 | 0 | 600 | ℃ | %Z073102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0218 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 2 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
369 | %%I5501-01TE0902B | 5501 | 5501-01TE0902B | #1 Boiler furnace back wall upside bed temperature 2 #1锅炉炉膛后墙上层床温温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0902B | #1 B furnaceBW UP bed T2 | 0 | 1300 | ℃ | %Z074102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0902B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 2 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
417 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 2 | AAI143-H | 4-20mA | N | [6 empty] | %Z075102 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 2 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4- | [8 empty] | 2017.11.9修改
577 | 5501-01CV0103-07 | 5501 | 5501-01CV0103-07 | #1 Boiler left side primary spray desuperheater inlet electric control valve fault #1锅炉左侧一级喷水减温器进口电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 2 | ADV151-P | SI | N |  | 5501-01CV0103-07 | #1 B LS PSD IN ECV F |  |  |  | %Z076102 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0103-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 2A | 2B
193 | %%I5501-01PDT0901A | 5501 | 5501-01PDT0901A | #1 Boiler right wall furnace differential pressure #1锅炉右侧墙炉膛差压 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01PDT0901A | #1 B R wall furnace DP | 0 | 20 | Kpa | %Z081102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PdT0901A | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 2A | 2B
321 | %%I5501-01TE0220 | 5501 | 5501-01TE0220 | #1 Boiler low temperature superheater pipe surface temperature 5 #1锅炉低温过热器管壁温度5 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0220 | #1 B LTS PS Temp. 5 | 0 | 600 | ℃ | %Z083102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0220 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 2 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
385 | %%I5501-01TE0903B | 5501 | 5501-01TE0903B | #1 Boiler furnace back wall upside bed temperature 3 #1锅炉炉膛后墙上层床温温度3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0903B | #1 B furnaceBW UP bed T3 | 0 | 1300 | ℃ | %Z084102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0903B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 2 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
433 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 2 | AAI143-H | 4-20mA | N | [6 empty] | %Z085102 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 2 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4- | [8 empty] | 2017.11.9修改
609 | 5501-01CV0104-07 | 5501 | 5501-01CV0104-07 | #1 Boiler right side primary spray desuperheater inlet electric control valve fault #1锅炉右侧一级喷水减温器进口电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 2 | ADV151-P | SI | N |  | 5501-01CV0104-07 | #1 B RS PSD IN ECV F |  |  |  | %Z086102 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0104-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 2A | 2B
209 | %%I5501-01PDT0901B | 5501 | 5501-01PDT0901B | #1 Boiler left wall furnace differential pressure #1锅炉左侧墙炉膛差压 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 2 | AAI143-H | 4-20mA | Y |  | 5501-01PDT0901B | #1 B L wall furnace DP | 0 | 20 | Kpa | %Z091102 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PdT0901B | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 2A | 2B
337 | %%I5501-01TE0222 | 5501 | 5501-01TE0222 | #1 Boiler low temperature superheater pipe surface temperature 7 #1锅炉低温过热器管壁温度7 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0222 | #1 B LTS PS Temp. 7 | 0 | 600 | ℃ | %Z093102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0222 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 2 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
401 | %%I5501-01TE0904B | 5501 | 5501-01TE0904B | #1 Boiler furnace back wall upside bed temperature 4 #1锅炉炉膛后墙上层床温温度4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE0904B | #1 B furnaceBW UP bed T4 | 0 | 1300 | ℃ | %Z094102 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0904B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 2 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
449 | %%I5501-01TE2421 | 5501 | 5501-01TE2421 | #1 Boiler feed water main pipe temperature #1锅炉给水母管温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 2 | AAI143-H | 4-20mA | N |  | 5501-01TE2421 | #1 B FW MP Temp.. | 0 | 300 | ℃ | %Z095102 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  | 5501-01TE2421 | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 2 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
561 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 2 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 16 | Mpa | %Z097102 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD06 | 2 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 2A | 2B | [9 empty] | 2017.12.1删除
2 | %%I5501-01CEMS008DCS | 5501 | 5501-01CEMS008DCS | #1 Boiler SNCR outlet NH3 #1锅炉脱硝SNCR出口NH3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 3 | AAI143-H | 4-20mA | N |  | 5501-01CEMS008DCS | #1 B SNCR OUT NH3 | 0 | 100 | ppm | %Z011103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01CEMS008DCS | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 3A | 3B
18 | %%I5501-01PT1111 | 5501 | 5501-01PT1111 | #1 Boiler compressed air pressure #1锅炉压缩空气压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 3 | AAI143-H | 4-20mA | N |  | 5501-01PT1111 | #1 B CA pressure | 0 | 1 | Mpa | %Z012103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT1111 | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 3A | 3B
466 | %%I5501-01Y01C-M31 | 5501 | 5501-01Y01C-M31 | #1炉给煤机C累计脉冲 #1 Boiler coal feeder C accumulated pulse |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 3 | 3 | AAP135-S | PI | N |  | 5501-01Y01C-M31 | #1 B coal feed C pulse |  |  |  | %Z013103 |  |  |  | DCS | Y | PI Surge protective device PI防雷栅 | N |  | AI |  |  |  | 01-Y-01C(M)-31 | [7 empty] | 5501-01DCS-AMC-02 | SPD09 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPB09 | A1BA4D-05 | 6A | 6B
34 | %%I5501-01FT0101 | 5501 | 5501-01FT0101 | #1 Boiler left side primary spray desuperheater feed water flow #1锅炉左侧一级喷水减温器减温水流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01FT0101 | #1 B LS PSD FW flow | 0 | 13.5 | t/h | %Z021103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0101 | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 3A | 3B
98 | %%I5501-01CV0502A-06 | 5501 | 5501-01CV0502A-06 | #1 Boiler left hot primary air motor control valve position #1锅炉左侧热一次风电动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01CV0502A-06 | #1 B LHPA MCV ZF | 0 | 100 | % | %Z023103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0502A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 3B | 3A
226 | %%I5501-01TE0105 | 5501 | 5501-01TE0105 | #1 Boiler steam drum outer temperature 2 #1锅炉汽包外壁温2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0105 | #1 BSD OUT Temp. 2 | 0 | 400 | ℃ | %Z025103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0105 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 3 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
482 | %%O5501-01CV0502A-05 | 5501 | 5501-01CV0502A-05 | #1 Boiler left hot primary air motor control valve control command #1锅炉左侧热一次风电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 3 | AAI543-H | 4-20mA | Y |  | 5501-01CV0502A-05 | #1 B LHPA MCV CO | 0 | 100 | % | %Z027103 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0502A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 3A | 3B
50 | %%I5501-01FT0102 | 5501 | 5501-01FT0102 | #1 Boiler right side primary spray desuperheater feed water flow #1锅炉右侧一级喷水减温器减温水流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01FT0102 | #1 B RS PSD FW flow | 0 | 13.5 | t/h | %Z031103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0102 | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 3A | 3B
114 | %%I5501-01CV0502B-06 | 5501 | 5501-01CV0502B-06 | #1 Boiler right hot primary air motor control valve position #1锅炉右侧热一次风电动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01CV0502B-06 | #1 B LHPA MCV ZF | 0 | 100 | % | %Z033103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0502B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 3B | 3A
242 | %%I5501-01TE0107 | 5501 | 5501-01TE0107 | #1 Boiler steam drum outer temperature 4 #1锅炉汽包外壁温4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0107 | #1 BSD OUT Temp. 4 | 0 | 400 | ℃ | %Z035103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0107 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 3 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
498 | %%O5501-01CV0502B-05 | 5501 | 5501-01CV0502B-05 | #1 Boiler right hot primary air motor control valve control command #1锅炉右侧热一次风电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 3 | AAI543-H | 4-20mA | Y |  | 5501-01CV0502B-05 | #1 B LHPA MCV CO | 0 | 100 | % | %Z037103 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0502B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 3A | 3B
66 | %%I5501-01FT0103 | 5501 | 5501-01FT0103 | #1 Boiler left side secondary spray desuperheater feed water flow #1锅炉左侧二级喷水减温器减温水流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01FT0103 | #1 B LS SSD FW flow | 0 | 5.8 | t/h | %Z041103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0103 | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 3A | 3B
130 | %%I5501-01CV0511A-06 | 5501 | 5501-01CV0511A-06 | #1 Boiler secondary air fan A inlet motor control damper position #1锅炉二次风机A入口电动调节挡板阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01CV0511A-06 | #1 B SAF A IN MCD ZF | 0 | 100 | % | %Z043103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0511A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 3B | 3A
258 | %%I5501-01TE0109 | 5501 | 5501-01TE0109 | #1 Boiler steam drum outer temperature 6 #1锅炉汽包外壁温6 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0109 | #1 BSD OUT Temp. 6 | 0 | 400 | ℃ | %Z045103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0109 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 3 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
514 | %%O5501-01CV0511A-05 | 5501 | 5501-01CV0511A-05 | #1 Boiler secondary air fan A inlet motor control damper control command #1锅炉二次风机A入口电动调节挡板控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 3 | AAI543-H | 4-20mA | Y |  | 5501-01CV0511A-05 | #1 B SAF A IN MCD CO | 0 | 100 | % | %Z047103 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0511A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 3A | 3B
82 | %%I5501-01PT0501B | 5501 | 5501-01PT0501B | #1 Boiler primary air fan B pressure #1锅炉一次风机B出口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01PT0501B | #1 B PA B Pre. | 0 | 40 | Kpa | %Z051103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0501B | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 3A | 3B
146 | %%I5501-01CV0511B-06 | 5501 | 5501-01CV0511B-06 | #1 Boiler secondary air fan B inlet motor control damper position #1锅炉二次风机B入口电动调节挡板阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01CV0511B-06 | #1 B SAF B IN MCD ZF | 0 | 100 | % | %Z053103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0511B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 3B | 3A
274 | %%I5501-01TE0111 | 5501 | 5501-01TE0111 | #1 Boiler steam drum outer temperature 8 #1锅炉汽包外壁温8 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0111 | #1 BSD OUT Temp. 8 | 0 | 400 | ℃ | %Z055103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0111 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 3 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
530 | %%O5501-01CV0511B-05 | 5501 | 5501-01CV0511B-05 | #1 Boiler secondary air fan B inlet motor control damper control command #1锅炉二次风机B入口电动调节挡板控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 3 | AAI543-H | 4-20mA | Y |  | 5501-01CV0511B-05 | #1 B SAF B IN MCD CO | 0 | 100 | % | %Z057103 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0511B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 3A | 3B
162 | %%I5501-01PDT0902A | 5501 | 5501-01PDT0902A | #1 Boiler right wall central furnace differential pressure #1锅炉右侧墙炉膛中部差压 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01PDT0902A | #1 B R wall C furnace DP | 0 | 9 | Kpa | %Z061103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PdT0902A | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 3A | 3B
290 | %%I5501-01TE0217 | 5501 | 5501-01TE0217 | #1 Boiler low temperature superheater pipe surface temperature 2 #1锅炉低温过热器管壁温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0217 | #1 B LTS PS Temp. 2 | 0 | 600 | ℃ | %Z063103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0217 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 3 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
354 | %%I5501-01TE0905A | 5501 | 5501-01TE0905A | #1 Boiler furnace front wall down bed temperature 1 #1锅炉炉膛前墙下层床温温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0905A | #1 B furnaceFW DW bed T1 | 0 | 1300 | ℃ | %Z064103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0905A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 3 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
546 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 3 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 600 | ℃ | %Z067103 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 3A | 3B | [9 empty] | 2017.12.1删除
642 | 5501-01CV0502A-07 | 5501 | 5501-01CV0502A-07 | #1 Boiler left hot primary air motor control valve fault #1锅炉左侧热一次风电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 3 | ADV151-P | SI | Y |  | 5501-01CV0502A-07 | #1 B LHPA MCV F |  |  |  | %Z065103 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0502A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 3A | 3B
178 | %%I5501-01PDT0902B | 5501 | 5501-01PDT0902B | #1 Boiler left wall central furnace differential pressure #1锅炉左侧墙炉膛中部差压 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01PDT0902B | #1 B L wall C furnace DP | 0 | 9 | Kpa | %Z071103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PdT0902B | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 3A | 3B
306 | %%I5501-01TE0219 | 5501 | 5501-01TE0219 | #1 Boiler low temperature superheater pipe surface temperature 4 #1锅炉低温过热器管壁温度4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0219 | #1 B LTS PS Temp. 4 | 0 | 600 | ℃ | %Z073103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0219 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 3 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
370 | %%I5501-01TE0906A | 5501 | 5501-01TE0906A | #1 Boiler furnace front wall down bed temperature 2 #1锅炉炉膛前墙下层床温温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0906A | #1 B furnaceFW DW bed T2 | 0 | 1300 | ℃ | %Z074103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0906A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 3 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
418 | %%I5501-01TE0511A | 5501 | 5501-01TE0511A | #1 Boiler air heater inlet cool secondary air temperature 1 #1锅炉空预器入口冷二次风温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0511A | #1 B AH IN CSA Temp. 1 | 0 | 100 | ℃ | %Z075103 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  | 5501-01TE0511A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
578 | 5501-01CV0105-07 | 5501 | 5501-01CV0105-07 | #1 Boiler left side secondary spray desuperheater inlet electric control valve fault #1锅炉左侧二级喷水减温器进口电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 3 | ADV151-P | SI | N |  | 5501-01CV0105-07 | #1 B LS SSD IN ECV F |  |  |  | %Z076103 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0105-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 3A | 3B
194 | %%I5501-01PDT0903A | 5501 | 5501-01PDT0903A | #1 Boiler right wall upside furnace differential pressure #1锅炉右侧墙炉膛上部差压 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01PDT0903A | #1 B R wall U furnace DP | 0 | 5 | Kpa | %Z081103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PdT0903A | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 3A | 3B
322 | %%I5501-01TE0221 | 5501 | 5501-01TE0221 | #1 Boiler low temperature superheater pipe surface temperature 6 #1锅炉低温过热器管壁温度6 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0221 | #1 B LTS PS Temp. 6 | 0 | 600 | ℃ | %Z083103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0221 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 3 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
386 | %%I5501-01TE0907A | 5501 | 5501-01TE0907A | #1 Boiler furnace front wall down bed temperature 3 #1锅炉炉膛前墙下层床温温度3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0907A | #1 B furnaceFW DW bed T3 | 0 | 1300 | ℃ | %Z084103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0907A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 3 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
434 | %%I5501-01TE0511B | 5501 | 5501-01TE0511B | #1 Boiler air heater inlet cool secondary air temperature 2 #1锅炉空预器入口冷二次风温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0511B | #1 B AH IN CSA Temp. 2 | 0 | 100 | ℃ | %Z085103 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  | 5501-01TE0511B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
610 | 5501-01CV0106-07 | 5501 | 5501-01CV0106-07 | #1 Boiler right side secondary spray desuperheater inlet electric control valve fault #1锅炉右侧二级喷水减温器进口电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 3 | ADV151-P | SI | N |  | 5501-01CV0106-07 | #1 B RS SSD IN ECV F |  |  |  | %Z086103 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0106-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 3A | 3B
210 | %%I5501-01PDT0903B | 5501 | 5501-01PDT0903B | #1 Boiler left wall upside furnace differential pressure #1锅炉左侧墙炉膛上部差压 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 3 | AAI143-H | 4-20mA | Y |  | 5501-01PDT0903B | #1 B L wall U furnace DP | 0 | 5 | Kpa | %Z091103 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PdT0903B | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 3A | 3B
338 | %%I5501-01TE0223 | 5501 | 5501-01TE0223 | #1 Boiler low temperature superheater pipe surface temperature 8 #1锅炉低温过热器管壁温度8 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0223 | #1 B LTS PS Temp. 8 | 0 | 600 | ℃ | %Z093103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0223 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 3 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
402 | %%I5501-01TE0908A | 5501 | 5501-01TE0908A | #1 Boiler furnace front wall down bed temperature 4 #1锅炉炉膛前墙下层床温温度4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE0908A | #1 B furnaceFW DW bed T4 | 0 | 1300 | ℃ | %Z094103 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0908A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 3 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
450 | %%I5501-01TE3405 | 5501 | 5501-01TE3405 | #1 Boiler closed circulating water of induced draft fan outlet main pipe temperture #1锅炉引风机冷却水回水母管温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 3 | AAI143-H | 4-20mA | N |  | 5501-01TE3405 | #1 B CC IDFOUT MP Temp. | 0 | 100 | ℃ | %Z095103 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  | 5501-01TE3405 | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
562 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 3 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 16 | Mpa | %Z097103 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD06 | 3 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 3A | 3B | [9 empty] | 2017.12.1删除
3 | %%I5501-01PT0535A | 5501 | 5501-01PT0535A | #1 Boiler left low overheater outlet fule pressure #1锅炉低温过热器左侧出口烟道压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 4 | AAI143-H | 4-20mA | N |  | 5501-01PT0535A | #1 B L LO OUT fule Pre | -4 | 0 | Kpa | %Z011104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0535A | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 4A | 4B
19 | %%I5501-01PT0535B | 5501 | 5501-01PT0535B | #1 Boiler right low overheater outlet fule pressure #1锅炉低温过热器右侧出口烟道压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 4 | AAI143-H | 4-20mA | N |  | 5501-01PT0535B | #1 B R LO OUT fule Pre | -4 | 0 | Kpa | %Z012104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0535B | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 4A | 4B
467 | %%I5501-01Y01D-M31 | 5501 | 5501-01Y01D-M31 | #1炉给煤机D累计脉冲 #1 Boiler coal feeder D accumulated pulse |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 3 | 4 | AAP135-S | PI | N |  | 5501-01Y01D-M31 | #1 B coal feed D pulse |  |  |  | %Z013104 |  |  |  | DCS | Y | PI Surge protective device PI防雷栅 | N |  | AI |  |  |  | 01-Y-01D(M)-31 | [7 empty] | 5501-01DCS-AMC-02 | SPD09 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPB09 | A1BA4D-05 | 8A | 8B
35 | %%I5501-01FT0501A | 5501 | 5501-01FT0501A | #1 Boiler left hot primary air flow #1锅炉左侧热一次风流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01FT0501A | #1 B LHPA flow | 0 | 120339 | Nm3/h | %Z021104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0501A | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 4A | 4B
99 | %%I5501-01CV0512A-06 | 5501 | 5501-01CV0512A-06 | #1 Boiler front of flame ignitor air motor damper A position #1锅炉点火风前电动调节风门A阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01CV0512A-06 | #1 B F FIA MD A ZF | 0 | 100 | % | %Z023104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0512A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 4B | 4A
227 | %%I5501-01TE0112 | 5501 | 5501-01TE0112 | #1 Boiler steam drum inner temperature 1 #1锅炉汽包内壁温1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 4 | AAI143-H | 4-20mA | N |  | 5501-01TE0112 | #1 BSD IN Temp. 1 | 0 | 400 | ℃ | %Z025104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0112 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 4 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
483 | %%O5501-01CV0512A-05 | 5501 | 5501-01CV0512A-05 | #1 Boiler front of flame ignitor air motor damper A control command #1锅炉点火风前电动调节风门A控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 4 | AAI543-H | 4-20mA | Y |  | 5501-01CV0512A-05 | #1 B F FIA MD A CO | 0 | 100 | % | %Z027104 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0512A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 4A | 4B
51 | %%I5501-01PT0501A | 5501 | 5501-01PT0501A | #1 Boiler primary air fan A pressure #1锅炉一次风机A出口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01PT0501A | #1 B PA A Pre. | 0 | 40 | Kpa | %Z031104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0501A | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 4A | 4B
115 | %%I5501-01CV0512B-06 | 5501 | 5501-01CV0512B-06 | #1 Boiler front of flame ignitor air motor damper B position #1锅炉点火风前电动调节风门B阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01CV0512B-06 | #1 B F FIA MD B ZF | 0 | 100 | % | %Z033104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0512B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 4B | 4A
243 | %%I5501-01TE0113 | 5501 | 5501-01TE0113 | #1 Boiler steam drum inner temperature 2 #1锅炉汽包内壁温2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 4 | AAI143-H | 4-20mA | N |  | 5501-01TE0113 | #1 BSD IN Temp. 2 | 0 | 400 | ℃ | %Z035104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0113 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 4 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
499 | %%O5501-01CV0512B-05 | 5501 | 5501-01CV0512B-05 | #1 Boiler front of flame ignitor air motor damper B control command #1锅炉点火风前电动调节风门B控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 4 | AAI543-H | 4-20mA | Y |  | 5501-01CV0512B-05 | #1 B F FIA MD B CO | 0 | 100 | % | %Z037104 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0512B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 4A | 4B
67 | %%I5501-01PT0502A | 5501 | 5501-01PT0502A | #1 Boiler left hot primary air pressure #1锅炉左侧热一次风压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01PT0502A | #1 B L HPA Pre. | 0 | 20 | Kpa | %Z041104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0502A | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 4A | 4B
131 | %%I5501-01CV0512C-06 | 5501 | 5501-01CV0512C-06 | #1 Boiler front of flame ignitor air motor damper C position #1锅炉点火风前电动调节风门C阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01CV0512C-06 | #1 B F FIA MD C ZF | 0 | 100 | % | %Z043104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0512C-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 4B | 4A
259 | %%I5501-01TE0114 | 5501 | 5501-01TE0114 | #1 Boiler steam drum inner temperature 3 #1锅炉汽包内壁温3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 4 | AAI143-H | 4-20mA | N |  | 5501-01TE0114 | #1 BSD IN Temp. 3 | 0 | 400 | ℃ | %Z045104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0114 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 4 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
515 | %%O5501-01CV0512C-05 | 5501 | 5501-01CV0512C-05 | #1 Boiler front of flame ignitor air motor damper C control command #1锅炉点火风前电动调节风门C控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 4 | AAI543-H | 4-20mA | Y |  | 5501-01CV0512C-05 | #1 B F FIA MD C CO | 0 | 100 | % | %Z047104 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0512C-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 4A | 4B
83 | %%I5501-01PT0502B | 5501 | 5501-01PT0502B | #1 Boiler right hot primary air pressure #1锅炉右侧热一次风压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01PT0502B | #1 B R HPA Pre. | 0 | 20 | Kpa | %Z051104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0502B | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 4A | 4B
147 | %%I5501-01CV0512D-06 | 5501 | 5501-01CV0512D-06 | #1 Boiler front of flame ignitor air motor damper D position #1锅炉点火风前电动调节风门D阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01CV0512D-06 | #1 B F FIA MD D ZF | 0 | 100 | % | %Z053104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0512D-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 4B | 4A
275 | %%I5501-01TE0115 | 5501 | 5501-01TE0115 | #1 Boiler steam drum inner temperature 4 #1锅炉汽包内壁温4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 4 | AAI143-H | 4-20mA | N |  | 5501-01TE0115 | #1 BSD IN Temp. 4 | 0 | 400 | ℃ | %Z055104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0115 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 4 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
531 | %%O5501-01CV0512D-05 | 5501 | 5501-01CV0512D-05 | #1 Boiler front of flame ignitor air motor damper D control command #1锅炉点火风前电动调节风门D控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 4 | AAI543-H | 4-20mA | Y |  | 5501-01CV0512D-05 | #1 B F FIA MD D CO | 0 | 100 | % | %Z057104 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0512D-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 4A | 4B
163 | %%I5501-01PT0901 | 5501 | 5501-01PT0901 | #1 Boiler front wall furnace pressure 1 #1锅炉前墙炉膛压力1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01PT0901 | #1 B F wall furnace Pre1 | -3 | 4 | Kpa | %Z061104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0901 | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 4A | 4B
291 | %%I5501-01TE0224 | 5501 | 5501-01TE0224 | #1 Boiler low temperature superheater pipe surface temperature 9 #1锅炉低温过热器管壁温度9 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 4 | AAI143-H | 4-20mA | N |  | 5501-01TE0224 | #1 B LTS PS Temp. 9 | 0 | 600 | ℃ | %Z063104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0224 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 4 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
355 | %%I5501-01TE0905B | 5501 | 5501-01TE0905B | #1 Boiler furnace back wall down bed temperature 1 #1锅炉炉膛后墙下层床温温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 4 | AAI143-H | 4-20mA | N |  | 5501-01TE0905B | #1 B furnaceBW DW bed T1 | 0 | 1300 | ℃ | %Z064104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0905B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 4 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
547 | %%O5501-43E101A-M15 | 5501 | 5501-43E101A-M15 | #1炉冷渣机A远方调速 #1 Boiler slag cooler A remote speed control (4-20mA) |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 4 | AAI543-H | 4-20mA | Y |  | 5501-43E101A-M15 | #1 B SC A SPD CL | 0 | 100 | % | %Z067104 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 43-E101A(M)-15 | [7 empty] | 5501-01DCS-AMC-02 | SPD05 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 4A | 4B
643 | 5501-01CV0502B-07 | 5501 | 5501-01CV0502B-07 | #1 Boiler right hot primary air motor control valve fault #1锅炉右侧热一次风电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 4 | ADV151-P | SI | Y |  | 5501-01CV0502B-07 | #1 B LHPA MCV F |  |  |  | %Z065104 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0502B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 4A | 4B
179 | %%I5501-01PT0902 | 5501 | 5501-01PT0902 | #1 Boiler front wall furnace pressure 2 #1锅炉前墙炉膛压力2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01PT0902 | #1 B F wall furnace Pre2 | -3 | 4 | Kpa | %Z071104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0902 | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 4A | 4B
307 | %%I5501-01TE0225 | 5501 | 5501-01TE0225 | #1 Boiler low temperature superheater pipe surface temperature 10 #1锅炉低温过热器管壁温度10 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 4 | AAI143-H | 4-20mA | N |  | 5501-01TE0225 | #1 B LTS PS Temp. 10 | 0 | 600 | ℃ | %Z073104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0225 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 4 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
371 | %%I5501-01TE0906B | 5501 | 5501-01TE0906B | #1 Boiler furnace back wall down bed temperature 2 #1锅炉炉膛后墙下层床温温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 4 | AAI143-H | 4-20mA | N |  | 5501-01TE0906B | #1 B furnaceBW DW bed T2 | 0 | 1300 | ℃ | %Z074104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0906B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 4 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
419 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 4 | AAI143-H | 4-20mA | N | [6 empty] | %Z075104 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 4 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4- | [8 empty] | 2017.11.9修改
579 | 5501-01CV0512A-07 | 5501 | 5501-01CV0512A-07 | #1 Boiler front of flame ignitor air motor damper A fault #1锅炉点火风前电动调节风门A执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 4 | ADV151-P | SI | N |  | 5501-01CV0512A-07 | #1 B F FIA MD A F |  |  |  | %Z076104 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0512A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 4A | 4B
195 | %%I5501-01PT0903 | 5501 | 5501-01PT0903 | #1 Boiler front wall furnace pressure 3 #1锅炉前墙炉膛压力3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01PT0903 | #1 B F wall furnace Pre3 | -3 | 4 | Kpa | %Z081104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0903 | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 4A | 4B
323 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 4 | AAI143-H | 4-20mA | N | [6 empty] | %Z083104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI | [11 empty] | 5501-01DCS-SBC-01 | SPD08 | 4 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1- | [9 empty] | 20190318删除
387 | %%I5501-01TE0907B | 5501 | 5501-01TE0907B | #1 Boiler furnace back wall down bed temperature 3 #1锅炉炉膛后墙下层床温温度3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 4 | AAI143-H | 4-20mA | N |  | 5501-01TE0907B | #1 B furnaceBW DW bed T3 | 0 | 1300 | ℃ | %Z084104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0907B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 4 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
435 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 4 | AAI143-H | 4-20mA | N | [6 empty] | %Z085104 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 4 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4- | [8 empty] | 2017.11.9修改
611 | 5501-01CV0512B-07 | 5501 | 5501-01CV0512B-07 | #1 Boiler front of flame ignitor air motor damper B fault #1锅炉点火风前电动调节风门B执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 4 | ADV151-P | SI | N |  | 5501-01CV0512B-07 | #1 B F FIA MD B F |  |  |  | %Z086104 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0512B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 4A | 4B
211 | %%I5501-01PT0904 | 5501 | 5501-01PT0904 | #1 Boiler front wall furnace pressure 4 #1锅炉前墙炉膛压力4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 4 | AAI143-H | 4-20mA | Y |  | 5501-01PT0904 | #1 B F wall furnace Pre4 | -9 | 9 | Kpa | %Z091104 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0904 | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 4A | 4B
339 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 4 | AAI143-H | 4-20mA | N | [6 empty] | %Z093104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI | [11 empty] | 5501-01DCS-SBC-01 | SPD09 | 4 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1- | [9 empty] | 20190318删除
403 | %%I5501-01TE0908B | 5501 | 5501-01TE0908B | #1 Boiler furnace back wall down bed temperature 4 #1锅炉炉膛后墙下层床温温度4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 4 | AAI143-H | 4-20mA | N |  | 5501-01TE0908B | #1 B furnaceBW DW bed T4 | 0 | 1300 | ℃ | %Z094104 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0908B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 4 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
451 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 4 | AAI143-H | 4-20mA | N | [6 empty] | %Z095104 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 4 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
563 | %%O5501-43E101B-M15 | 5501 | 5501-43E101B-M15 | #1炉冷渣机B远方调速 #1 Boiler slag cooler B remote speed control (4-20mA) |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 4 | AAI543-H | 4-20mA | Y |  | 5501-43E101B-M15 | #1 B SC B SPD CL | 0 | 100 | % | %Z097104 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 43-E101B(M)-15 | [7 empty] | 5501-01DCS-AMC-02 | SPD06 | 4 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 4A | 4B
4 | %%I5501-01PT0536A | 5501 | 5501-01PT0536A | #1 Boiler left high temperature economizer outlet fule pressure #1锅炉高温省煤器左侧出口烟道压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 5 | AAI143-H | 4-20mA | N |  | 5501-01PT0536A | #1 B L HTE OUT fule Pre | -5 | 0 | Kpa | %Z011105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0536A | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 5A | 5B
20 | %%I5501-01PT0536B | 5501 | 5501-01PT0536B | #1 Boiler right high temperature economizer outlet fule pressure #1锅炉高温省煤器右侧出口烟道压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 5 | AAI143-H | 4-20mA | N |  | 5501-01PT0536B | #1 B R HTE OUT fule Pre | -5 | 0 | Kpa | %Z012105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0536B | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 5A | 5B
468 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 3 | 5 | AAP135-S | PI | N | [6 empty] | %Z013105 |  |  |  | DCS | Y | PI Surge protective device PI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD09 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPB09 | A1BA4D-05 | 10A | 10B
36 | %%I5501-01FT0511A | 5501 | 5501-01FT0511A | #1 Boiler left hot secondary air flow 1 #1锅炉左侧热二次风流量1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01FT0511A | #1 B L HSA flow 1 | 0 | 109648 | m3/h | %Z021105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0511A | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 5A | 5B
100 | %%I5501-01CV0513A-06 | 5501 | 5501-01CV0513A-06 | #1 Boiler front wall upper layer secondary air inlet motor damper 1 position #1锅炉前墙上层二次风入口电动调节风门1阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01CV0513A-06 | #1 B FWUL SAIN MD 1 ZF | 0 | 100 | % | %Z023105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0513A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 5B | 5A
228 | %%I5501-01TE0201A | 5501 | 5501-01TE0201A | #1 Boiler left side primary spray desuperheater inlet temperature 1 #1锅炉左侧一级喷水减温器进口汽温1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0201A | #1 B LS PSD IN Temp. 1 | 0 | 500 | ℃ | %Z025105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0201A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 5 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
484 | %%O5501-01CV0513A-05 | 5501 | 5501-01CV0513A-05 | #1 Boiler front wall upper layer secondary air inlet motor damper 1 control command #1锅炉前墙上层二次风入口电动调节风门1控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 5 | AAI543-H | 4-20mA | Y |  | 5501-01CV0513A-05 | #1 B FWUL SAIN MD 1 CO | 0 | 100 | % | %Z027105 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0513A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 5A | 5B
52 | %%I5501-01FT0511B | 5501 | 5501-01FT0511B | #1 Boiler right hot secondary air flow 1 #1锅炉右侧热二次风流量1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01FT0511B | #1 B R HSA flow 1 | 0 | 109648 | m3/h | %Z031105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0511B | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 5A | 5B
116 | %%I5501-01CV0513B-06 | 5501 | 5501-01CV0513B-06 | #1 Boiler front wall upper layer secondary air inlet motor damper 2 position #1锅炉前墙上层二次风入口电动调节风门2阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01CV0513B-06 | #1 B FWUL SAIN MD 2 ZF | 0 | 100 | % | %Z033105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0513B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 5B | 5A
244 | %%I5501-01TE0202A | 5501 | 5501-01TE0202A | #1 Boiler left side primary spray desuperheater inlet temperature 2 #1锅炉左侧一级喷水减温器进口汽温2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0202A | #1 B LS PSD IN Temp. 2 | 0 | 500 | ℃ | %Z035105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0202A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 5 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
500 | %%O5501-01CV0513B-05 | 5501 | 5501-01CV0513B-05 | #1 Boiler front wall upper layer secondary air inlet motor damper 2 control command #1锅炉前墙上层二次风入口电动调节风门2控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 5 | AAI543-H | 4-20mA | Y |  | 5501-01CV0513B-05 | #1 B FWUL SAIN MD 2 CO | 0 | 100 | % | %Z037105 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0513B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 5A | 5B
68 | %%I5501-01FT0512C | 5501 | 5501-01FT0512C | #1 Boiler flame ignitor air C inlet flow #1锅炉点火风C入口流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01FT0512C | #1 B FIA C IN flow | 0 | 40500 | m3/h | %Z041105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0512C | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 5A | 5B
132 | %%I5501-01CV0513C-06 | 5501 | 5501-01CV0513C-06 | #1 Boiler front wall upper layer secondary air inlet motor damper 3 position #1锅炉前墙上层二次风入口电动调节风门3阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01CV0513C-06 | #1 B FWUL SAIN MD 3 ZF | 0 | 100 | % | %Z043105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0513C-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 5B | 5A
260 | %%I5501-01TE0203A | 5501 | 5501-01TE0203A | #1 Boiler left side primary spray desuperheater inlet temperature 3 #1锅炉左侧一级喷水减温器进口汽温3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0203A | #1 B LS PSD IN Temp. 3 | 0 | 500 | ℃ | %Z045105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0203A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 5 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
516 | %%O5501-01CV0513C-05 | 5501 | 5501-01CV0513C-05 | #1 Boiler front wall upper layer secondary air inlet motor damper 3 control command #1锅炉前墙上层二次风入口电动调节风门3控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 5 | AAI543-H | 4-20mA | Y |  | 5501-01CV0513C-05 | #1 B FWUL SAIN MD 3 CO | 0 | 100 | % | %Z047105 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0513C-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 5A | 5B
84 | %%I5501-01FT0512D | 5501 | 5501-01FT0512D | #1 Boiler flame ignitor air D inlet flow #1锅炉点火风D入口流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01FT0512D | #1 B FIA D IN flow | 0 | 40500 | m3/h | %Z051105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0512D | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 5A | 5B
148 | %%I5501-01CV0513D-06 | 5501 | 5501-01CV0513D-06 | #1 Boiler front wall upper layer secondary air inlet motor damper 4 position #1锅炉前墙上层二次风入口电动调节风门4阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01CV0513D-06 | #1 B FWUL SAIN MD 4 ZF | 0 | 100 | % | %Z053105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0513D-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 5B | 5A
276 | %%I5501-01TE0206A | 5501 | 5501-01TE0206A | #1 Boiler left side primary spray desuperheater outlet temperature 3 #1锅炉左侧一级喷水减温器出口汽温3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0206A | #1 B LS PSD OUT Temp. 3 | 0 | 500 | ℃ | %Z055105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0206A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 5 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
532 | %%O5501-01CV0513D-05 | 5501 | 5501-01CV0513D-05 | #1 Boiler front wall upper layer secondary air inlet motor damper 4 control command #1锅炉前墙上层二次风入口电动调节风门4控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 5 | AAI543-H | 4-20mA | Y |  | 5501-01CV0513D-05 | #1 B FWUL SAIN MD 4 CO | 0 | 100 | % | %Z057105 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0513D-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 5A | 5B
164 | %%I5501-01PT0911A | 5501 | 5501-01PT0911A | #1 Boiler left seal pot standpipe upside pressure #1锅炉左侧回料器立管上部压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01PT0911A | #1 B L SPS upside Pre | 0 | 30 | Kpa | %Z061105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0911A | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 5A | 5B
292 | %%I5501-01TE0226 | 5501 | 5501-01TE0226 | #1 Boiler moderate temperature superheater pipe surface temperature 1 #1锅炉中温过热器管壁温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0226 | #1 B MTS PS Temp. 1 | 0 | 700 | ℃ | %Z063105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0226 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 5 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
356 | %%I5501-01TE0909A | 5501 | 5501-01TE0909A | #1 Boiler furnace left wall upside bed temperature 1 #1锅炉炉膛左侧墙上层床温温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0909A | #1 B furnaceRW UP bed T1 | 0 | 1300 | ℃ | %Z064105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0909A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 5 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
548 | %%O5501-01CV0303-05 | 5501 | 5501-01CV0303-05 | #1 Boiler steam drum continuous blowdown electric control valve control command #1锅炉汽包连续排污电动调节阀1控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 5 | AAI543-H | 4-20mA | Y |  | 5501-01CV0303-05 | #1B CBF tankECV 1 CO | 0 | 100 | % | %Z067105 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0303-05 | [7 empty] | 5501-01DCS-AMC-02 | SPD05 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 5A | 5B | [9 empty] | 2017.11.23新增
644 | 5501-01CV0511A-07 | 5501 | 5501-01CV0511A-07 | #1 Boiler secondary air fan A inlet motor control damper fault #1锅炉二次风机A入口电动调节挡板执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 5 | ADV151-P | SI | Y |  | 5501-01CV0511A-07 | #1 B SAF A IN MCD F |  |  |  | %Z065105 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0511A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 5A | 5B
180 | %%I5501-01PT0911B | 5501 | 5501-01PT0911B | #1 Boiler right seal pot standpipe upside pressure #1锅炉右侧回料器立管上部压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01PT0911B | #1 B R SPS upside Pre | 0 | 30 | Kpa | %Z071105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0911B | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 5A | 5B
308 | %%I5501-01TE0229 | 5501 | 5501-01TE0229 | #1 Boiler moderate temperature superheater pipe surface temperature 4 #1锅炉中温过热器管壁温度4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0229 | #1 B MTS PS Temp. 4 | 0 | 700 | ℃ | %Z073105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0229 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 5 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
372 | %%I5501-01TE0909B | 5501 | 5501-01TE0909B | #1 Boiler furnace right wall upside bed temperature 1 #1锅炉炉膛右侧墙上层床温温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0909B | #1 B furnaceLW UP bed T1 | 0 | 1300 | ℃ | %Z074105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0909B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 5 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
420 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 5 | AAI143-H | 4-20mA | N | [6 empty] | %Z075105 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI | [11 empty] | 5501-01DCS-SBC-02 | SPD06 | 5 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4- | [8 empty] | 20190318删除
580 | 5501-01CV0512C-07 | 5501 | 5501-01CV0512C-07 | #1 Boiler front of flame ignitor air motor damper C fault #1锅炉点火风前电动调节风门C执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 5 | ADV151-P | SI | N |  | 5501-01CV0512C-07 | #1 B F FIA MD C F |  |  |  | %Z076105 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0512C-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 5A | 5B
196 | %%I5501-01PT0912A | 5501 | 5501-01PT0912A | #1 Boiler left seal pot standpipe downside pressure #1锅炉左侧回料器立管下部压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01PT0912A | #1 B L SPS Down Pre | 0 | 30 | Kpa | %Z081105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0912A | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 5A | 5B
324 | %%I5501-01TE0232 | 5501 | 5501-01TE0232 | #1 Boiler moderate temperature superheater pipe surface temperature 7 #1锅炉中温过热器管壁温度7 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0232 | #1 B MTS PS Temp. 7 | 0 | 700 | ℃ | %Z083105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0232 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 5 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
388 | %%I5501-01TE0910A | 5501 | 5501-01TE0910A | #1 Boiler furnace left wall upside bed temperature 2 #1锅炉炉膛左侧墙上层床温温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0910A | #1 B furnaceRW UP bed T2 | 0 | 1300 | ℃ | %Z084105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0910A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 5 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
436 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 5 | AAI143-H | 4-20mA | N | [6 empty] | %Z085105 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI | [11 empty] | 5501-01DCS-SBC-02 | SPD07 | 5 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4- | [8 empty] | 20190318删除
612 | 5501-01CV0512D-07 | 5501 | 5501-01CV0512D-07 | #1 Boiler front of flame ignitor air motor damper D fault #1锅炉点火风前电动调节风门D执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 5 | ADV151-P | SI | N |  | 5501-01CV0512D-07 | #1 B F FIA MD D F |  |  |  | %Z086105 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0512D-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 5A | 5B
212 | %%I5501-01PT0912B | 5501 | 5501-01PT0912B | #1 Boiler right seal pot standpipe downside pressure #1锅炉右侧回料器立管下部压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 5 | AAI143-H | 4-20mA | Y |  | 5501-01PT0912B | #1 B R SPS Down Pre | 0 | 30 | Kpa | %Z091105 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0912B | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 5A | 5B
340 | %%I5501-01TE0235 | 5501 | 5501-01TE0235 | #1 Boiler moderate temperature superheater pipe surface temperature 10 #1锅炉中温过热器管壁温度10 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0235 | #1 B MTS PS Temp. 10 | 0 | 700 | ℃ | %Z093105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0235 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 5 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
404 | %%I5501-01TE0910B | 5501 | 5501-01TE0910B | #1 Boiler furnace right wall upside bed temperature 2 #1锅炉炉膛右侧墙上层床温温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 5 | AAI143-H | 4-20mA | N |  | 5501-01TE0910B | #1 B furnaceLW UP bed T2 | 0 | 1300 | ℃ | %Z094105 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0910B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 5 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
452 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 5 | AAI143-H | 4-20mA | N | [6 empty] | %Z095105 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 5 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
564 | %%O5501-01CV1102-05 | 5501 | 5501-01CV1102-05 | #1 Boiler urea solution outlet electic control valve control command #1锅炉尿素溶液出口电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 5 | AAI543-H | 4-20mA | Y |  | 5501-01CV1102-05 | #1 B US OUT ECV CO | 0 | 100 | % | %Z097105 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV1102-05 | [7 empty] | 5501-01DCS-AMC-02 | SPD06 | 5 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 5A | 5B
5 | %%I5501-01PT0537A | 5501 | 5501-01PT0537A | #1 Boiler left heater inlet fule pressure #1锅炉空预器左侧进口烟道压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 6 | AAI143-H | 4-20mA | N |  | 5501-01PT0537A | #1 B L Heat IN fule Pre | -5 | 0 | Kpa | %Z011106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0537A | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 6A | 6B
21 | %%I5501-01PT0537B | 5501 | 5501-01PT0537B | #1 Boiler right heater inlet fule pressure #1锅炉空预器右侧进口烟道压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 6 | AAI143-H | 4-20mA | N |  | 5501-01PT0537B | #1 B R Heat IN fule Pre | -5 | 0 | Kpa | %Z012106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0537B | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 6A | 6B
469 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 3 | 6 | AAP135-S | PI | N | [6 empty] | %Z013106 |  |  |  | DCS | Y | PI Surge protective device PI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD09 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPB09 | A1BA4D-05 | 12A | 12B
37 | %%I5501-01FT0512A | 5501 | 5501-01FT0512A | #1 Boiler flame ignitor air A inlet flow #1锅炉点火风A入口流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01FT0512A | #1 B FIA A IN flow | 0 | 40500 | m3/h | %Z021106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0512A | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 6A | 6B
101 | %%I5501-01CV0514A-06 | 5501 | 5501-01CV0514A-06 | #1 Boiler front wall down layer secondary air inlet motor damper 1 position #1锅炉前墙下层二次风入口电动调节风门1阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01CV0514A-06 | #1 B FWDL SAIN MD 1 ZF | 0 | 100 | % | %Z023106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0514A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 6B | 6A
229 | %%I5501-01TE0201B | 5501 | 5501-01TE0201B | #1 Boiler right side primary spray desuperheater inlet temperature 1 #1锅炉右侧一级喷水减温器进口汽温1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0201B | #1 B RS PSD IN Temp. 1 | 0 | 500 | ℃ | %Z025106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0201B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 6 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
485 | %%O5501-01CV0514A-05 | 5501 | 5501-01CV0514A-05 | #1 Boiler front wall down layer secondary air inlet motor damper 1 control command #1锅炉前墙下层二次风入口电动调节风门1控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 6 | AAI543-H | 4-20mA | Y |  | 5501-01CV0514A-05 | #1 B FWDL SAIN MD 1 CO | 0 | 100 | % | %Z027106 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0514A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 6A | 6B
53 | %%I5501-01FT0512B | 5501 | 5501-01FT0512B | #1 Boiler flame ignitor air B inlet flow #1锅炉点火风B入口流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01FT0512B | #1 B FIA B IN flow | 0 | 40500 | m3/h | %Z031106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0512B | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 6A | 6B
117 | %%I5501-01CV0514B-06 | 5501 | 5501-01CV0514B-06 | #1 Boiler front wall down layer secondary air inlet motor damper 2 position #1锅炉前墙下层二次风入口电动调节风门2阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01CV0514B-06 | #1 B FWDL SAIN MD 2 ZF | 0 | 100 | % | %Z033106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0514B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 6B | 6A
245 | %%I5501-01TE0202B | 5501 | 5501-01TE0202B | #1 Boiler right side primary spray desuperheater inlet temperature 2 #1锅炉右侧一级喷水减温器进口汽温2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0202B | #1 B RS PSD IN Temp. 2 | 0 | 500 | ℃ | %Z035106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0202B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 6 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
501 | %%O5501-01CV0514B-05 | 5501 | 5501-01CV0514B-05 | #1 Boiler front wall down layer secondary air inlet motor damper 2 control command #1锅炉前墙下层二次风入口电动调节风门2控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 6 | AAI543-H | 4-20mA | Y |  | 5501-01CV0514B-05 | #1 B FWDL SAIN MD 2 CO | 0 | 100 | % | %Z037106 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0514B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 6A | 6B
69 | %%I5501-01FT0513A | 5501 | 5501-01FT0513A | #1 Boiler left hot secondary air flow 2 #1锅炉左侧热二次风流量2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01FT0513A | #1 B L HSA flow 2 | 0 | 109648 | m3/h | %Z041106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0513A | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 6A | 6B
133 | %%I5501-01CV0514C-06 | 5501 | 5501-01CV0514C-06 | #1 Boiler front wall down layer secondary air inlet motor damper 3 position #1锅炉前墙下层二次风入口电动调节风门3阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01CV0514C-06 | #1 B FWDL SAIN MD 3 ZF | 0 | 100 | % | %Z043106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0514C-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 6B | 6A
261 | %%I5501-01TE0203B | 5501 | 5501-01TE0203B | #1 Boiler right side primary spray desuperheater inlet temperature 3 #1锅炉右侧一级喷水减温器进口汽温3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0203B | #1 B RS PSD IN Temp. 3 | 0 | 500 | ℃ | %Z045106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0203B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 6 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
517 | %%O5501-01CV0514C-05 | 5501 | 5501-01CV0514C-05 | #1 Boiler front wall down layer secondary air inlet motor damper 3 control command #1锅炉前墙下层二次风入口电动调节风门3控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 6 | AAI543-H | 4-20mA | Y |  | 5501-01CV0514C-05 | #1 B FWDL SAIN MD 3 CO | 0 | 100 | % | %Z047106 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0514C-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 6A | 6B
85 | %%I5501-01FT0513B | 5501 | 5501-01FT0513B | #1 Boiler right hot secondary air flow 2 #1锅炉右侧热二次风流量2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01FT0513B | #1 B R HSA flow 2 | 0 | 109648 | m3/h | %Z051106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0513B | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 6A | 6B
149 | %%I5501-01CV0514D-06 | 5501 | 5501-01CV0514D-06 | #1 Boiler front wall down layer secondary air inlet motor damper 4 position #1锅炉前墙下层二次风入口电动调节风门4阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01CV0514D-06 | #1 B FWDL SAIN MD 4 ZF | 0 | 100 | % | %Z053106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0514D-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 6B | 6A
277 | %%I5501-01TE0206B | 5501 | 5501-01TE0206B | #1 Boiler right side primary spray desuperheater outlet temperature 3 #1锅炉右侧一级喷水减温器出口汽温3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0206B | #1 B RS PSD OUT Temp. 3 | 0 | 500 | ℃ | %Z055106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0206B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 6 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
533 | %%O5501-01CV0514D-05 | 5501 | 5501-01CV0514D-05 | #1 Boiler front wall down layer secondary air inlet motor damper 4 control command #1锅炉前墙下层二次风入口电动调节风门4控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 6 | AAI543-H | 4-20mA | Y |  | 5501-01CV0514D-05 | #1 B FWDL SAIN MD 4 CO | 0 | 100 | % | %Z057106 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0514D-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 6A | 6B
165 | %%I5501-01PT0201A | 5501 | 5501-01PT0201A | #1 Boiler left side primary spray desuperheater inlet pressure #1锅炉左侧一级喷水减温器进口汽压 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01PT0201A | #1 B LS PSD IN Pre. | 0 | 12 | MPa | %Z061106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0201A | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 6A | 6B
293 | %%I5501-01TE0227 | 5501 | 5501-01TE0227 | #1 Boiler moderate temperature superheater pipe surface temperature 2 #1锅炉中温过热器管壁温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0227 | #1 B MTS PS Temp. 2 | 0 | 700 | ℃ | %Z063106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0227 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 6 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
357 | %%I5501-01TE0911A | 5501 | 5501-01TE0911A | #1 Boiler left seal pot standpipe temperature 1 #1锅炉左侧回料器立管温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0911A | #1 B L SPS Temp..1 | 0 | 1300 | ℃ | %Z064106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0911A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 6 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
549 | %%O5501-01CV0621A-05 | 5501 | 5501-01CV0621A-05 | #1 Boiler In-duct burner A oil supply control valve control command #1锅炉风道燃烧器A供油气动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 6 | AAI543-H | 4-20mA | Y |  | 5501-01CV0621A-05 | #1 B IDB A oil valve CO | 0 | 100 | % | %Z067106 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0621A-05 | [7 empty] | 5501-01DCS-AMC-02 | SPD05 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 6A | 6B | [9 empty] | 2017.12.11新增
645 | 5501-01CV0511B-07 | 5501 | 5501-01CV0511B-07 | #1 Boiler secondary air fan B inlet motor control damper fault #1锅炉二次风机B入口电动调节挡板执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 6 | ADV151-P | SI | Y |  | 5501-01CV0511B-07 | #1 B SAF B IN MCD F |  |  |  | %Z065106 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0511B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 6A | 6B
181 | %%I5501-01PT0201B | 5501 | 5501-01PT0201B | #1 Boiler right side primary spray desuperheater inlet pressure #1锅炉右侧一级喷水减温器进口汽压 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01PT0201B | #1 B RS PSD IN Pre. | 0 | 12 | MPa | %Z071106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0201B | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 6A | 6B
309 | %%I5501-01TE0230 | 5501 | 5501-01TE0230 | #1 Boiler moderate temperature superheater pipe surface temperature 5 #1锅炉中温过热器管壁温度5 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0230 | #1 B MTS PS Temp. 5 | 0 | 700 | ℃ | %Z073106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0230 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 6 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
373 | %%I5501-01TE0911B | 5501 | 5501-01TE0911B | #1 Boiler rihgt seal pot standpipe temperature 1 #1锅炉右侧回料器立管温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0911B | #1 B R SPS Temp..1 | 0 | 1300 | ℃ | %Z074106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0911B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 6 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
421 | %%I5501-01TE3403 | 5501 | 5501-01TE3403 | #1 Boiler Primary&secondary air fan and fluidization fan outlet main pipe water temperture 1 #1锅炉一次风机、二次风机、流化风机冷却水回水母管温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE3403 | #1 B P&SAF OUT MP W T 1 | 0 | 100 | ℃ | %Z075106 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  | 5501-01TE3403 | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 6 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
581 | 5501-01CV0513A-07 | 5501 | 5501-01CV0513A-07 | #1 Boiler front wall upper layer secondary air inlet motor damper 1 fault #1锅炉前墙上层二次风入口电动调节风门1执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 6 | ADV151-P | SI | N |  | 5501-01CV0513A-07 | #1 B FWUL SAIN MD 1 F |  |  |  | %Z076106 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0513A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 6A | 6B
197 | %%I5501-01PT0202A | 5501 | 5501-01PT0202A | #1 Boiler left side secondary spray desuperheater inlet pressure #1锅炉左侧二级喷水减温器进口汽压 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01PT0202A | #1 B LS SSD IN Pre. | 0 | 12 | MPa | %Z081106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0202A | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 6A | 6B
325 | %%I5501-01TE0233 | 5501 | 5501-01TE0233 | #1 Boiler moderate temperature superheater pipe surface temperature 8 #1锅炉中温过热器管壁温度8 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0233 | #1 B MTS PS Temp. 8 | 0 | 700 | ℃ | %Z083106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0233 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 6 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
389 | %%I5501-01TE0912A | 5501 | 5501-01TE0912A | #1 Boiler left seal pot standpipe temperature 2 #1锅炉左侧回料器立管温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0912A | #1 B L SPS Temp..2 | 0 | 1300 | ℃ | %Z084106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0912A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 6 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
437 | %%I5501-01TE3404 | 5501 | 5501-01TE3404 | #1 Boiler Primary&secondary air fan and fluidization fan outlet main pipe water temperture 2 #1锅炉一次风机、二次风机、流化风机冷却水回水母管温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE3404 | #1 B P&SAF OUT MP W T 2 | 0 | 100 | ℃ | %Z085106 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  | 5501-01TE3404 | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 6 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
613 | 5501-01CV0514A-07 | 5501 | 5501-01CV0514A-07 | #1 Boiler front wall down layer secondary air inlet motor damper 1 fault #1锅炉前墙下层二次风入口电动调节风门1执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 6 | ADV151-P | SI | N |  | 5501-01CV0514A-07 | #1 B FWDL SAIN MD 1 F |  |  |  | %Z086106 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0514A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 6A | 6B
213 | %%I5501-01PT0202B | 5501 | 5501-01PT0202B | #1 Boiler right side secondary spray desuperheater inlet pressure #1锅炉右侧二级喷水减温器进口汽压 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 6 | AAI143-H | 4-20mA | Y |  | 5501-01PT0202B | #1 B RS SSD IN Pre. | 0 | 12 | MPa | %Z091106 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0202B | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 6A | 6B
341 | %%I5501-01TE0236 | 5501 | 5501-01TE0236 | #1 Boiler moderate temperature superheater pipe surface temperature 11 #1锅炉中温过热器管壁温度11 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0236 | #1 B MTS PS Temp. 11 | 0 | 700 | ℃ | %Z093106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0236 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 6 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
405 | %%I5501-01TE0912B | 5501 | 5501-01TE0912B | #1 Boiler rihgt seal pot standpipe temperature 2 #1锅炉右侧回料器立管温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 6 | AAI143-H | 4-20mA | N |  | 5501-01TE0912B | #1 B R SPS Temp..2 | 0 | 1300 | ℃ | %Z094106 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0912B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 6 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
453 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 6 | AAI143-H | 4-20mA | N | [6 empty] | %Z095106 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 6 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
565 | %%O5501-01CV0304-05 | 5501 | 5501-01CV0304-05 | #1 Boiler continuous blowdown flash tank electric control valve control command #1锅炉汽包连续排污电动调节阀2控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 6 | AAI543-H | 4-20mA | Y |  | 5501-01CV0304-05 | #1B CBF tankECV 2 CO | 0 | 100 | % | %Z097106 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0304-05 | [7 empty] | 5501-01DCS-AMC-02 | SPD06 | 6 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 6A | 6B | [9 empty] | 2017.11.23新增
6 | %%I5501-01PT0538A | 5501 | 5501-01PT0538A | #1 Boiler left heater outlet fule pressure #1锅炉空预器左侧出口烟道压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 7 | AAI143-H | 4-20mA | N |  | 5501-01PT0538A | #1 B L Heat OUT fule Pre | -6 | 0 | Kpa | %Z011107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0538A | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 7A | 7B
22 | %%I5501-01PT0538B | 5501 | 5501-01PT0538B | #1 Boiler right heater outlet fule pressure #1锅炉空预器右侧出口烟道压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 7 | AAI143-H | 4-20mA | N |  | 5501-01PT0538B | #1 B R Heat OUT fule Pre | -6 | 0 | Kpa | %Z012107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0538B | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 7A | 7B
470 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 3 | 7 | AAP135-S | PI | N | [6 empty] | %Z013107 |  |  |  | DCS | Y | PI Surge protective device PI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD09 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPB09 | A1BA4D-05 | 14A | 14B
38 | %%I5501-01PT0511A | 5501 | 5501-01PT0511A | #1 Boiler secondary air A outlet pressure #1锅炉二次风机A出口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01PT0511A | #1 B SA A OUT Pre. | 0 | 30 | Kpa | %Z021107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0511A | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 7A | 7B
102 | %%I5501-01CV0515A-06 | 5501 | 5501-01CV0515A-06 | #1 Boiler back wall upper layer secondary air inlet motor damper 1 position #1锅炉后墙上层二次风入口电动调节风门1阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01CV0515A-06 | #1 B BWUL SAIN MD 1 ZF | 0 | 100 | % | %Z023107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0515A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 7B | 7A
230 | %%I5501-01TE0204A | 5501 | 5501-01TE0204A | #1 Boiler left side primary spray desuperheater outlet temperature 1 #1锅炉左侧一级喷水减温器出口汽温1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0204A | #1 B LS PSD OUT Temp. 1 | 0 | 500 | ℃ | %Z025107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0204A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 7 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
486 | %%O5501-01CV0515A-05 | 5501 | 5501-01CV0515A-05 | #1 Boiler back wall upper layer secondary air inlet motor damper 1 control command #1锅炉后墙上层二次风入口电动调节风门1控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 7 | AAI543-H | 4-20mA | Y |  | 5501-01CV0515A-05 | #1 B BWUL SAIN MD 1 CO | 0 | 100 | % | %Z027107 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0515A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 7A | 7B
54 | %%I5501-01PT0511B | 5501 | 5501-01PT0511B | #1 Boiler secondary air B outlet pressure #1锅炉二次风机B出口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01PT0511B | #1 B SA B OUT Pre. | 0 | 30 | Kpa | %Z031107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0511B | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 7A | 7B
118 | %%I5501-01CV0515B-06 | 5501 | 5501-01CV0515B-06 | #1 Boiler back wall upper layer secondary air inlet motor damper 2 position #1锅炉后墙上层二次风入口电动调节风门2阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01CV0515B-06 | #1 B BWUL SAIN MD 2 ZF | 0 | 100 | % | %Z033107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0515B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 7B | 7A
246 | %%I5501-01TE0205A | 5501 | 5501-01TE0205A | #1 Boiler left side primary spray desuperheater outlet temperature 2 #1锅炉左侧一级喷水减温器出口汽温2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0205A | #1 B LS PSD OUT Temp. 2 | 0 | 500 | ℃ | %Z035107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0205A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 7 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
502 | %%O5501-01CV0515B-05 | 5501 | 5501-01CV0515B-05 | #1 Boiler back wall upper layer secondary air inlet motor damper 2 control command #1锅炉后墙上层二次风入口电动调节风门2控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 7 | AAI543-H | 4-20mA | Y |  | 5501-01CV0515B-05 | #1 B BWUL SAIN MD 2 CO | 0 | 100 | % | %Z037107 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0515B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 7A | 7B
70 | %%I5501-01PT0512A | 5501 | 5501-01PT0512A | #1 Boiler left hot secondary air pressure #1锅炉左侧热二次风压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01PT0512A | #1 B L HSA Pre. | 0 | 13 | Kpa | %Z041107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0512A | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 7A | 7B
134 | %%I5501-01CV0515C-06 | 5501 | 5501-01CV0515C-06 | #1 Boiler back wall upper layer secondary air inlet motor damper 3 position #1锅炉后墙上层二次风入口电动调节风门3阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01CV0515C-06 | #1 B BWUL SAIN MD 3 ZF | 0 | 100 | % | %Z043107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0515C-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 7B | 7A
262 | %%I5501-01TE0208A | 5501 | 5501-01TE0208A | #1 Boiler left side secondary spray desuperheater inlet temperature 2 #1锅炉左侧二级喷水减温器进口汽温2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0208A | #1 B LS SSD IN Temp. 2 | 0 | 600 | ℃ | %Z045107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0208A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 7 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
518 | %%O5501-01CV0515C-05 | 5501 | 5501-01CV0515C-05 | #1 Boiler back wall upper layer secondary air inlet motor damper 3 control command #1锅炉后墙上层二次风入口电动调节风门3控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 7 | AAI543-H | 4-20mA | Y |  | 5501-01CV0515C-05 | #1 B BWUL SAIN MD 3 CO | 0 | 100 | % | %Z047107 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0515C-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 7A | 7B
86 | %%I5501-01PT0512B | 5501 | 5501-01PT0512B | #1 Boiler right hot secondary air pressure #1锅炉右侧热二次风压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01PT0512B | #1 B R HSA Pre. | 0 | 13 | Kpa | %Z051107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0512B | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 7A | 7B
150 | %%I5501-01CV0515D-06 | 5501 | 5501-01CV0515D-06 | #1 Boiler back wall upper layer secondary air inlet motor damper 4 position #1锅炉后墙上层二次风入口电动调节风门4阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01CV0515D-06 | #1 B BWUL SAIN MD 4 ZF | 0 | 100 | % | %Z053107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0515D-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 7B | 7A
278 | %%I5501-01TE0209A | 5501 | 5501-01TE0209A | #1 Boiler left side secondary spray desuperheater inlet temperature 3 #1锅炉左侧二级喷水减温器进口汽温3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0209A | #1 B LS SSD IN Temp. 3 | 0 | 600 | ℃ | %Z055107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0209A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 7 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
534 | %%O5501-01CV0515D-05 | 5501 | 5501-01CV0515D-05 | #1 Boiler back wall upper layer secondary air inlet motor damper 4 control command #1锅炉后墙上层二次风入口电动调节风门4控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 7 | AAI543-H | 4-20mA | Y |  | 5501-01CV0515D-05 | #1 B BWUL SAIN MD 4 CO | 0 | 100 | % | %Z057107 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0515D-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 7A | 7B
166 | %%I5501-01FT0502A | 5501 | 5501-01FT0502A | #1 Boiler NO.1 coal sowing port flow #1锅炉1号播煤口流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01FT0502A | #1 B NO 1 CSP flow | 0 | 5535 | Nm3/h | %Z061107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0502A | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 7A | 7B
294 | %%I5501-01TE0228 | 5501 | 5501-01TE0228 | #1 Boiler moderate temperature superheater pipe surface temperature 3 #1锅炉中温过热器管壁温度3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0228 | #1 B MTS PS Temp. 3 | 0 | 700 | ℃ | %Z063107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0228 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 7 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
358 | %%I5501-01TE0531A | 5501 | 5501-01TE0531A | #1 Boiler left cyclone inlet fule temperature 1 #1锅炉左侧旋风分离器入口烟道温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0531A | #1 B L CYC IN fule T 1 | 0 | 1100 | ℃ | %Z064107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0531A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 7 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
550 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 7 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z067107 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 7A | 7B
646 | 5501-01CV0531A-07 | 5501 | 5501-01CV0531A-07 | #1 Boiler induced draft fan A inlet motor control damper fault #1锅炉引风机A入口电动调节挡板执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 7 | ADV151-P | SI | Y |  | 5501-01CV0531A-07 | #1 B IDF A IN MCD F |  |  |  | %Z065107 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0531A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 7A | 7B
182 | %%I5501-01FT0502B | 5501 | 5501-01FT0502B | #1 Boiler NO.2 coal sowing port flow #1锅炉2号播煤口流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01FT0502B | #1 B NO 2 CSP flow | 0 | 5535 | Nm3/h | %Z071107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0502B | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 7A | 7B
310 | %%I5501-01TE0231 | 5501 | 5501-01TE0231 | #1 Boiler moderate temperature superheater pipe surface temperature 6 #1锅炉中温过热器管壁温度6 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0231 | #1 B MTS PS Temp. 6 | 0 | 700 | ℃ | %Z073107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0231 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 7 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
374 | %%I5501-01TE0532A | 5501 | 5501-01TE0532A | #1 Boiler left cyclone inlet fule temperature 2 #1锅炉左侧旋风分离器入口烟道温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0532A | #1 B L CYC IN fule T 2 | 0 | 1100 | ℃ | %Z074107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0532A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 7 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
422 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 7 | AAI143-H | 4-20mA | N | [6 empty] | %Z075107 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 7 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
582 | 5501-01CV0513B-07 | 5501 | 5501-01CV0513B-07 | #1 Boiler front wall upper layer secondary air inlet motor damper 2 fault #1锅炉前墙上层二次风入口电动调节风门2执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 7 | ADV151-P | SI | N |  | 5501-01CV0513B-07 | #1 B FWUL SAIN MD 2 F |  |  |  | %Z076107 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0513B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 7A | 7B
198 | %%I5501-01FT0502C | 5501 | 5501-01FT0502C | #1 Boiler NO.3 coal sowing port flow #1锅炉3号播煤口流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01FT0502C | #1 B NO 3 CSP flow | 0 | 5535 | Nm3/h | %Z081107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0502C | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 7A | 7B
326 | %%I5501-01TE0234 | 5501 | 5501-01TE0234 | #1 Boiler moderate temperature superheater pipe surface temperature 9 #1锅炉中温过热器管壁温度9 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0234 | #1 B MTS PS Temp. 9 | 0 | 700 | ℃ | %Z083107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0234 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 7 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
390 | %%I5501-01TE0533A | 5501 | 5501-01TE0533A | #1 Boiler left cyclone outlet fule temperature 1 #1锅炉左侧旋风分离器出口烟道温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0533A | #1 B L CYC OUT fule T 1 | 0 | 1100 | ℃ | %Z084107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0533A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 7 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
438 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 7 | AAI143-H | 4-20mA | N | [6 empty] | %Z085107 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 7 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
614 | 5501-01CV0514B-07 | 5501 | 5501-01CV0514B-07 | #1 Boiler front wall down layer secondary air inlet motor damper 2 fault #1锅炉前墙下层二次风入口电动调节风门2执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 7 | ADV151-P | SI | N |  | 5501-01CV0514B-07 | #1 B FWDL SAIN MD 2 F |  |  |  | %Z086107 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0514B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 7A | 7B
214 | %%I5501-01FT0502D | 5501 | 5501-01FT0502D | #1 Boiler NO.4 coal sowing port flow #1锅炉4号播煤口流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 7 | AAI143-H | 4-20mA | Y |  | 5501-01FT0502D | #1 B NO 4 CSP flow | 0 | 5535 | Nm3/h | %Z091107 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0502D | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 7A | 7B
342 | %%I5501-01TE0237 | 5501 | 5501-01TE0237 | #1 Boiler moderate temperature superheater pipe surface temperature 12 #1锅炉中温过热器管壁温度12 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0237 | #1 B MTS PS Temp. 12 | 0 | 700 | ℃ | %Z093107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0237 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 7 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
406 | %%I5501-01TE0534A | 5501 | 5501-01TE0534A | #1 Boiler left cyclone outlet fule temperature 2 #1锅炉左侧旋风分离器出口烟道温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 7 | AAI143-H | 4-20mA | N |  | 5501-01TE0534A | #1 B L CYC OUT fule T 2 | 0 | 1100 | ℃ | %Z094107 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0534A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 7 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
454 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 7 | AAI143-H | 4-20mA | N | [6 empty] | %Z095107 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 7 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
566 | %%O5501-01CV0621B-05 | 5501 | 5501-01CV0621B-05 | #1 Boiler In-duct burner B oil supply control valve control command #1锅炉风道燃烧器B供油气动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 7 | AAI543-H | 4-20mA | Y |  | 5501-01CV0621B-05 | #1 B IDB B oil valve CO | 0 | 100 | % | %Z097107 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0621B-05 | [7 empty] | 5501-01DCS-AMC-02 | SPD06 | 7 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 7A | 7B | [9 empty] | 2017.12.11新增
7 | %%I5501-01FT0522A | 5501 | 5501-01FT0522A | #1 Boiler left seal pot fiuidizing air main pipe flow #1锅炉左侧回料器流化风母管流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 8 | AAI143-H | 4-20mA | N |  | 5501-01FT0522A | #1 B L SPFA MP flow | 0 | 6948 | Nm3/h | %Z011108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0522A | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 8A | 8B
23 | %%I5501-01FT0522B | 5501 | 5501-01FT0522B | #1 Boiler right seal pot fiuidizing air main pipe flow #1锅炉右侧回料器流化风母管流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 8 | AAI143-H | 4-20mA | N |  | 5501-01FT0522B | #1 B R SPFA MP flow | 0 | 6948 | Nm3/h | %Z012108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0522B | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 8A | 8B
471 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 3 | 8 | AAP135-S | PI | N | [6 empty] | %Z013108 |  |  |  | DCS | Y | PI Surge protective device PI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD09 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPB09 | A1BA4D-05 | 16A | 16B
39 | %%I5501-01FT0523A | 5501 | 5501-01FT0523A | #1 Boiler left seal pot fiuidizing air flow 1 #1锅炉左侧回料器流化风流量1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01FT0523A | #1 B L SPFA flow 1 | 0 | 2210 | Nm3/h | %Z021108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0523A | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 8A | 8B
103 | %%I5501-01CV0516A-06 | 5501 | 5501-01CV0516A-06 | #1 Boiler back wall down layer secondary air inlet motor damper 1 position #1锅炉后墙下层二次风入口电动调节风门1阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01CV0516A-06 | #1 B BWDL SAIN MD 1 ZF | 0 | 100 | % | %Z023108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0516A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 8B | 8A
231 | %%I5501-01TE0204B | 5501 | 5501-01TE0204B | #1 Boiler right side primary spray desuperheater outlet temperature 1 #1锅炉右侧一级喷水减温器出口汽温1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0204B | #1 B RS PSD OUT Temp. 1 | 0 | 500 | ℃ | %Z025108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0204B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 8 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
487 | %%O5501-01CV0516A-05 | 5501 | 5501-01CV0516A-05 | #1 Boiler back wall down layer secondary air inlet motor damper 1 control command #1锅炉后墙下层二次风入口电动调节风门1控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 8 | AAI543-H | 4-20mA | Y |  | 5501-01CV0516A-05 | #1 B BWDL SAIN MD 1 CO | 0 | 100 | % | %Z027108 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0516A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 8A | 8B
55 | %%I5501-01FT0523B | 5501 | 5501-01FT0523B | #1 Boiler right seal pot fiuidizing air flow 1 #1锅炉右侧回料器流化风流量1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01FT0523B | #1 B R SPFA flow 1 | 0 | 2210 | Nm3/h | %Z031108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0523B | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 8A | 8B
119 | %%I5501-01CV0516B-06 | 5501 | 5501-01CV0516B-06 | #1 Boiler back wall down layer secondary air inlet motor damper 2 position #1锅炉后墙下层二次风入口电动调节风门2阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01CV0516B-06 | #1 B BWDL SAIN MD 2 ZF | 0 | 100 | % | %Z033108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0516B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 8B | 8A
247 | %%I5501-01TE0205B | 5501 | 5501-01TE0205B | #1 Boiler right side primary spray desuperheater outlet temperature 2 #1锅炉右侧一级喷水减温器出口汽温2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0205B | #1 B RS PSD OUT Temp. 2 | 0 | 500 | ℃ | %Z035108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0205B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 8 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
503 | %%O5501-01CV0516B-05 | 5501 | 5501-01CV0516B-05 | #1 Boiler back wall down layer secondary air inlet motor damper 2 control command #1锅炉后墙下层二次风入口电动调节风门2控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 8 | AAI543-H | 4-20mA | Y |  | 5501-01CV0516B-05 | #1 B BWDL SAIN MD 2 CO | 0 | 100 | % | %Z037108 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0516B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 8A | 8B
71 | %%I5501-01FT0524A | 5501 | 5501-01FT0524A | #1 Boiler left seal pot fiuidizing air flow 2 #1锅炉左侧回料器流化风流量2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01FT0524A | #1 B L SPFA flow 2 | 0 | 2210 | Nm3/h | %Z041108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0524A | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 8A | 8B
135 | %%I5501-01CV0516C-06 | 5501 | 5501-01CV0516C-06 | #1 Boiler back wall down layer secondary air inlet motor damper 3 position #1锅炉后墙下层二次风入口电动调节风门3阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01CV0516C-06 | #1 B BWDL SAIN MD 3 ZF | 0 | 100 | % | %Z043108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0516C-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 8B | 8A
263 | %%I5501-01TE0208B | 5501 | 5501-01TE0208B | #1 Boiler right side secondary spray desuperheater inlet temperature 2 #1锅炉右侧二级喷水减温器进口汽温2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0208B | #1 B RS SSD IN Temp. 2 | 0 | 600 | ℃ | %Z045108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0208B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 8 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
519 | %%O5501-01CV0516C-05 | 5501 | 5501-01CV0516C-05 | #1 Boiler back wall down layer secondary air inlet motor damper 3 control command #1锅炉后墙下层二次风入口电动调节风门3控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 8 | AAI543-H | 4-20mA | Y |  | 5501-01CV0516C-05 | #1 B BWDL SAIN MD 3 CO | 0 | 100 | % | %Z047108 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0516C-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 8A | 8B
87 | %%I5501-01FT0524B | 5501 | 5501-01FT0524B | #1 Boiler right seal pot fiuidizing air flow 2 #1锅炉右侧回料器流化风流量2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01FT0524B | #1 B R SPFA flow 2 | 0 | 2210 | Nm3/h | %Z051108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0524B | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 8A | 8B
151 | %%I5501-01CV0516D-06 | 5501 | 5501-01CV0516D-06 | #1 Boiler back wall down layer secondary air inlet motor damper 4 position #1锅炉后墙下层二次风入口电动调节风门4阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01CV0516D-06 | #1 B BWDL SAIN MD 4 ZF | 0 | 100 | % | %Z053108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0516D-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 8B | 8A
279 | %%I5501-01TE0209B | 5501 | 5501-01TE0209B | #1 Boiler right side secondary spray desuperheater inlet temperature 3 #1锅炉右侧二级喷水减温器进口汽温3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0209B | #1 B RS SSD IN Temp. 3 | 0 | 600 | ℃ | %Z055108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0209B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 8 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
535 | %%O5501-01CV0516D-05 | 5501 | 5501-01CV0516D-05 | #1 Boiler back wall down layer secondary air inlet motor damper 4 control command #1锅炉后墙下层二次风入口电动调节风门4控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 8 | AAI543-H | 4-20mA | Y |  | 5501-01CV0516D-05 | #1 B BWDL SAIN MD 4 CO | 0 | 100 | % | %Z057108 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0516D-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 8A | 8B
167 | %%I5501-01FT0503A | 5501 | 5501-01FT0503A | #1 Boiler coal feeder A coal sowing air flow #1锅炉给煤机A播煤风流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01FT0503A | #1 B CF A CSA flow | 0 | 2302 | Nm3/h | %Z061108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0503A | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 8A | 8B
295 | %%I5501-01TE0238 | 5501 | 5501-01TE0238 | #1 Boiler high temperature superheater pipe surface temperature 1 #1锅炉高温过热器管壁温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0238 | #1 B MTS PS Temp. 1 | 0 | 700 | ℃ | %Z063108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0238 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 8 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
359 | %%I5501-01TE0531B | 5501 | 5501-01TE0531B | #1 Boiler right cyclone inlet fule temperature 1 #1锅炉右侧旋风分离器入口烟道温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0531B | #1 B R CYC IN fule T 1 | 0 | 1100 | ℃ | %Z064108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0531B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 8 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
551 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 8 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z067108 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 8A | 8B
647 | 5501-01CV0531B-07 | 5501 | 5501-01CV0531B-07 | #1 Boiler induced draft fan B inlet motor control damper fault #1锅炉引风机B入口电动调节挡板执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 8 | ADV151-P | SI | Y |  | 5501-01CV0531B-07 | #1 B IDF B IN MCD F |  |  |  | %Z065108 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0531B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 8A | 8B
183 | %%I5501-01FT0503B | 5501 | 5501-01FT0503B | #1 Boiler coal feeder B coal sowing air flow #1锅炉给煤机B播煤风流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01FT0503B | #1 B CF B CSA flow | 0 | 2302 | Nm3/h | %Z071108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0503B | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 8A | 8B
311 | %%I5501-01TE0241 | 5501 | 5501-01TE0241 | #1 Boiler high temperature superheater pipe surface temperature 4 #1锅炉高温过热器管壁温度4 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0241 | #1 B MTS PS Temp. 4 | 0 | 700 | ℃ | %Z073108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0241 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 8 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
375 | %%I5501-01TE0532B | 5501 | 5501-01TE0532B | #1 Boiler right cyclone inlet fule temperature 2 #1锅炉右侧旋风分离器入口烟道温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0532B | #1 B R CYC IN fule T 2 | 0 | 1100 | ℃ | %Z074108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0532B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 8 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
423 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 8 | AAI143-H | 4-20mA | N | [6 empty] | %Z075108 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 8 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
583 | 5501-01CV0513C-07 | 5501 | 5501-01CV0513C-07 | #1 Boiler front wall upper layer secondary air inlet motor damper 3 fault #1锅炉前墙上层二次风入口电动调节风门3执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 8 | ADV151-P | SI | N |  | 5501-01CV0513C-07 | #1 B FWUL SAIN MD 3 F |  |  |  | %Z076108 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0513C-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 8A | 8B
199 | %%I5501-01FT0503C | 5501 | 5501-01FT0503C | #1 Boiler coal feeder C coal sowing air flow #1锅炉给煤机C播煤风流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01FT0503C | #1 B CF C CSA flow | 0 | 2302 | Nm3/h | %Z081108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0503C | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 8A | 8B
327 | %%I5501-01TE0244 | 5501 | 5501-01TE0244 | #1 Boiler high temperature superheater pipe surface temperature 7 #1锅炉高温过热器管壁温度7 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0244 | #1 B MTS PS Temp. 7 | 0 | 700 | ℃ | %Z083108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0244 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 8 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
391 | %%I5501-01TE0533B | 5501 | 5501-01TE0533B | #1 Boiler right cyclone outlet fule temperature 1 #1锅炉右侧旋风分离器出口烟道温度1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0533B | #1 B R CYC OUT fule T 1 | 0 | 1100 | ℃ | %Z084108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0533B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 8 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
439 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 8 | AAI143-H | 4-20mA | N | [6 empty] | %Z085108 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 8 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
615 | 5501-01CV0514C-07 | 5501 | 5501-01CV0514C-07 | #1 Boiler front wall down layer secondary air inlet motor damper 3 fault #1锅炉前墙下层二次风入口电动调节风门3执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 8 | ADV151-P | SI | N |  | 5501-01CV0514C-07 | #1 B FWDL SAIN MD 3 F |  |  |  | %Z086108 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0514C-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 8A | 8B
215 | %%I5501-01FT0503D | 5501 | 5501-01FT0503D | #1 Boiler coal feeder D coal sowing air flow #1锅炉给煤机D播煤风流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 8 | AAI143-H | 4-20mA | Y |  | 5501-01FT0503D | #1 B CF D CSA flow | 0 | 2302 | Nm3/h | %Z091108 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0503D | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 8A | 8B
343 | %%I5501-01TE0247 | 5501 | 5501-01TE0247 | #1 Boiler high temperature superheater pipe surface temperature 10 #1锅炉高温过热器管壁温度10 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0247 | #1 B MTS PS Temp. 10 | 0 | 700 | ℃ | %Z093108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0247 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 8 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
407 | %%I5501-01TE0534B | 5501 | 5501-01TE0534B | #1 Boiler right cyclone outlet fule temperature 2 #1锅炉右侧旋风分离器出口烟道温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 8 | AAI143-H | 4-20mA | N |  | 5501-01TE0534B | #1 B R CYC OUT fule T 2 | 0 | 1100 | ℃ | %Z094108 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0534B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 8 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
455 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 8 | AAI143-H | 4-20mA | N | [6 empty] | %Z095108 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 8 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
567 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 8 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z097108 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD06 | 8 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 8A | 8B
8 | %%I5501-01PT0556A | 5501 | 5501-01PT0556A | #1 Boiler secondary air fan A coupler oil outlet pressure #1锅炉二次风机A耦合器出油口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 9 | AAI143-H | 4-20mA | N |  | 5501-01PT0556A | #1 B SAF A C O Out Pre | 0 | 0.6 | Mpa | %Z011109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0556A | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 9A | 9B
24 | %%I5501-01PT0556B | 5501 | 5501-01PT0556B | #1 Boiler secondary air fan B coupler oil outlet pressure #1锅炉二次风机B耦合器出油口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 9 | AAI143-H | 4-20mA | N |  | 5501-01PT0556B | #1 B SAF B C O Out Pre | 0 | 0.6 | Mpa | %Z012109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0556B | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 9A | 9B
40 | %%I5501-01AT0501A | 5501 | 5501-01AT0501A | #1 Boiler left heater inlet fule oxygen level #1锅炉空预器左侧进口烟道氧量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01AT0501A | #1 B L Heat IN FULE O2 | 0 | 10 | % | %Z021109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01AT0501A | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 9B | 9A
104 | %%I5501-01CV0513E-06 | 5501 | 5501-01CV0513E-06 | #1 Boiler front wall upper layer secondary air inlet motor damper 5 position #1锅炉前墙上层二次风入口电动调节风门5阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01CV0513E-06 | #1 B FWUL SAIN MD 5 ZF | 0 | 100 | % | %Z023109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0513E-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 9B | 9A
232 | %%I5501-01TE0207A | 5501 | 5501-01TE0207A | #1 Boiler left side secondary spray desuperheater inlet temperature 1 #1锅炉左侧二级喷水减温器进口汽温1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0207A | #1 B LS SSD IN Temp. 1 | 0 | 600 | ℃ | %Z025109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0207A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 9 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
488 | %%O5501-01CV0513E-05 | 5501 | 5501-01CV0513E-05 | #1 Boiler front wall upper layer secondary air inlet motor damper 5 control command #1锅炉前墙上层二次风入口电动调节风门5控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 9 | AAI543-H | 4-20mA | Y |  | 5501-01CV0513E-05 | #1 B FWUL SAIN MD 5 CO | 0 | 100 | % | %Z027109 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0513E-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 9A | 9B
56 | %%I5501-01AT0501B | 5501 | 5501-01AT0501B | #1 Boiler right heater inlet fule oxygen level #1锅炉空预器右侧进口烟道氧量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01AT0501B | #1 B R Heat IN FULE O2 | 0 | 10 | % | %Z031109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01AT0501B | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 9B | 9A
120 | %%I5501-01CV0514E-06 | 5501 | 5501-01CV0514E-06 | #1 Boiler front wall down layer secondary air inlet motor damper 5 position #1锅炉前墙下层二次风入口电动调节风门5阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01CV0514E-06 | #1 B FWDL SAIN MD 5 ZF | 0 | 100 | % | %Z033109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0514E-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 9B | 9A
248 | %%I5501-01TE0210A | 5501 | 5501-01TE0210A | #1 Boiler left side secondary spray desuperheater outlet temperature 1 #1锅炉左侧二级喷水减温器出口汽温1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0210A | #1 B LS SSD OUT Temp. 1 | 0 | 600 | ℃ | %Z035109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0210A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 9 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
504 | %%O5501-01CV0514E-05 | 5501 | 5501-01CV0514E-05 | #1 Boiler front wall down layer secondary air inlet motor damper 5 control command #1锅炉前墙下层二次风入口电动调节风门5控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 9 | AAI543-H | 4-20mA | Y |  | 5501-01CV0514E-05 | #1 B FWDL SAIN MD 5 CO | 0 | 100 | % | %Z037109 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0514E-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 9A | 9B
72 | %%I5501-01PT0533A | 5501 | 5501-01PT0533A | #1 Boiler induced draft fan A inlet pressure #1锅炉引风机A入口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01PT0533A | #1 B IDF A inlet Pre. | -10 | 0 | Kpa | %Z041109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0533A | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 9A | 9B
136 | %%I5501-01CV0531A-06 | 5501 | 5501-01CV0531A-06 | #1 Boiler induced draft fan A inlet motor control damper position #1锅炉引风机A入口电动调节挡板阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01CV0531A-06 | #1 B IDF A IN MCD ZF | 0 | 100 | % | %Z043109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0531A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 9B | 9A
264 | %%I5501-01TE0211A | 5501 | 5501-01TE0211A | #1 Boiler left side secondary spray desuperheater outlet temperature 2 #1锅炉左侧二级喷水减温器出口汽温2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0211A | #1 B LS SSD OUT Temp. 2 | 0 | 600 | ℃ | %Z045109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0211A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 9 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
520 | %%O5501-01CV0531A-05 | 5501 | 5501-01CV0531A-05 | #1 Boiler induced draft fan A inlet motor control damper control command #1锅炉引风机A入口电动调节挡板控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 9 | AAI543-H | 4-20mA | Y |  | 5501-01CV0531A-05 | #1 B IDF A IN MCD CO | 0 | 100 | % | %Z047109 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0531A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 9A | 9B
88 | %%I5501-01PT0533B | 5501 | 5501-01PT0533B | #1 Boiler induced draft fan B inlet pressure #1锅炉引风机B入口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01PT0533B | #1 B IDF B inlet Pre. | -10 | 0 | Kpa | %Z051109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0533B | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 9A | 9B
152 | %%I5501-01CV0531B-06 | 5501 | 5501-01CV0531B-06 | #1 Boiler induced draft fan B inlet motor control damper position #1锅炉引风机B入口电动调节挡板阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01CV0531B-06 | #1 B IDF B IN MCD ZF | 0 | 100 | % | %Z053109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0531B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 9B | 9A
280 | %%I5501-01TE0212A | 5501 | 5501-01TE0212A | #1 Boiler left side secondary spray desuperheater outlet temperature 3 #1锅炉左侧二级喷水减温器出口汽温3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0212A | #1 B LS SSD OUT Temp. 3 | 0 | 600 | ℃ | %Z055109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0212A | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 9 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
536 | %%O5501-01CV0531B-05 | 5501 | 5501-01CV0531B-05 | #1 Boiler induced draft fan B inlet motor control damper control command #1锅炉引风机B入口电动调节挡板控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 9 | AAI543-H | 4-20mA | Y |  | 5501-01CV0531B-05 | #1 B IDF B IN MCD CO | 0 | 100 | % | %Z057109 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0531B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 9A | 9B
168 | %%I5501-01PT0101 | 5501 | 5501-01PT0101 | #1 Boiler economizer inlet feed water pressure #1锅炉省煤器进口给水压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01PT0101 | #1 BEI FW Pre. | 0 | 12 | MPa | %Z061109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0101 | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 9A | 9B
296 | %%I5501-01TE0239 | 5501 | 5501-01TE0239 | #1 Boiler high temperature superheater pipe surface temperature 2 #1锅炉高温过热器管壁温度2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0239 | #1 B MTS PS Temp. 2 | 0 | 700 | ℃ | %Z063109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0239 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 9 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
360 | %%I5501-01TE0536A | 5501 | 5501-01TE0536A | #1 Boiler left low overheater outlet fule temperature #1锅炉低温过热器左侧出口烟道温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0536A | #1 B L LO OUT fule T | 0 | 700 | ℃ | %Z064109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0536A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 9 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
552 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 9 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z067109 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 9A | 9B
648 | 5501-01CV0541A-07 | 5501 | 5501-01CV0541A-07 | #1 Boiler primary air fan A coupler fault #1锅炉一次风机A液偶执行器执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 9 | ADV151-P | SI | Y |  | 5501-01CV0541A-07 | #1 B PAF A coupler F |  |  |  | %Z065109 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0541A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 9A | 9B
184 | %%I5501-01PT0105 | 5501 | 5501-01PT0105 | #1 Boiler superheater desuperheating water pressure #1锅炉过热器减温水母管压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01PT0105 | #1 B SD W Pre. | 0 | 16 | MPa | %Z071109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0105 | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 9A | 9B
312 | %%I5501-01TE0242 | 5501 | 5501-01TE0242 | #1 Boiler high temperature superheater pipe surface temperature 5 #1锅炉高温过热器管壁温度5 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0242 | #1 B MTS PS Temp. 5 | 0 | 700 | ℃ | %Z073109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0242 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 9 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
376 | %%I5501-01TE0536B | 5501 | 5501-01TE0536B | #1 Boiler right low overheater outlet fule temperature #1锅炉低温过热器右侧出口烟道温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0536B | #1 B R LO OUT fule T | 0 | 700 | ℃ | %Z074109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0536B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 9 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
424 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 9 | AAI143-H | 4-20mA | N | [6 empty] | %Z075109 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 9 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
584 | 5501-01CV0513D-07 | 5501 | 5501-01CV0513D-07 | #1 Boiler front wall upper layer secondary air inlet motor damper 4 fault #1锅炉前墙上层二次风入口电动调节风门4执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 9 | ADV151-P | SI | N |  | 5501-01CV0513D-07 | #1 B FWUL SAIN MD 4 F |  |  |  | %Z076109 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0513D-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 9A | 9B
200 | %%I5501-01PT0203 | 5501 | 5501-01PT0203 | #1 Boiler High temperature superheater outlet pressure #1锅炉高温过热器出口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01PT0203 | #1 B HTS O Pre. | 0 | 12 | MPa | %Z081109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0203 | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 9A | 9B
328 | %%I5501-01TE0245 | 5501 | 5501-01TE0245 | #1 Boiler high temperature superheater pipe surface temperature 8 #1锅炉高温过热器管壁温度8 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0245 | #1 B MTS PS Temp. 8 | 0 | 700 | ℃ | %Z083109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0245 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 9 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
392 | %%I5501-01TE0537A | 5501 | 5501-01TE0537A | #1 Boiler left high temperature economizer outlet fule temperature #1锅炉高温省煤器左侧出口烟道温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0537A | #1 B L HTE OUT fule T | 0 | 500 | ℃ | %Z084109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0537A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 9 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
440 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 9 | AAI143-H | 4-20mA | N | [6 empty] | %Z085109 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 9 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
616 | 5501-01CV0514D-07 | 5501 | 5501-01CV0514D-07 | #1 Boiler front wall down layer secondary air inlet motor damper 4 fault #1锅炉前墙下层二次风入口电动调节风门4执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 9 | ADV151-P | SI | N |  | 5501-01CV0514D-07 | #1 B FWDL SAIN MD 4 F |  |  |  | %Z086109 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0514D-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 9A | 9B
216 | %%I5501-01FT0521 | 5501 | 5501-01FT0521 | #1 Boiler high pressure fluidizing air outlet main pipe flow #1锅炉高压流化风机出口母管流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 9 | AAI143-H | 4-20mA | Y |  | 5501-01FT0521 | #1 B HPFA OUT MP flow | 0 | 18000 | Nm3/h | %Z091109 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0521 | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 9A | 9B
344 | %%I5501-01TE0248 | 5501 | 5501-01TE0248 | #1 Boiler high temperature superheater pipe surface temperature 11 #1锅炉高温过热器管壁温度11 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0248 | #1 B MTS PS Temp. 11 | 0 | 700 | ℃ | %Z093109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0248 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 9 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
408 | %%I5501-01TE0537B | 5501 | 5501-01TE0537B | #1 Boiler right high temperature economizer outlet fule temperature #1锅炉高温省煤器右侧出口烟道温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 9 | AAI143-H | 4-20mA | N |  | 5501-01TE0537B | #1 B R HTE OUT fule T | 0 | 500 | ℃ | %Z094109 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0537B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 9 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
456 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 9 | AAI143-H | 4-20mA | N | [6 empty] | %Z095109 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 9 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
568 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 9 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z097109 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD06 | 9 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 9A | 9B
9 | %%I5501-01PT0571A | 5501 | 5501-01PT0571A | #1 Boiler induced draft fan A coupler oil outlet pressure #1锅炉引风机A耦合器出油口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 10 | AAI143-H | 4-20mA | N |  | 5501-01PT0571A | #1 B IDF A C O Out Pre | 0 | 0.6 | Mpa | %Z011110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0571A | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 10A | 10B
25 | %%I5501-01PT0571B | 5501 | 5501-01PT0571B | #1 Boiler induced draft fan B coupler oil outlet pressure #1锅炉引风机B耦合器出油口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 10 | AAI143-H | 4-20mA | N |  | 5501-01PT0571B | #1 B IDF B C O Out Pre | 0 | 0.6 | Mpa | %Z012110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0571B | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 10A | 10B
41 | %%I5501-01PT0611 | 5501 | 5501-01PT0611 | #1 Boiler over-bed burner oil inlet pressure #1锅炉床上燃烧器油母管压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01PT0611 | #1 B OBB oil IN Pre | 0 | 6 | Mpa | %Z021110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0611 | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 10A | 10B
105 | %%I5501-01CV0521A-06 | 5501 | 5501-01CV0521A-06 | #1 Boiler left seal pot fiuidizing air main damper 1 position #1锅炉左侧回料器流化风电动调节风门1阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01CV0521A-06 | #1 B L SPFA MD 1 ZF | 0 | 100 | % | %Z023110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0521A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 10B | 10A
233 | %%I5501-01TE0207B | 5501 | 5501-01TE0207B | #1 Boiler right side secondary spray desuperheater inlet temperature 1 #1锅炉右侧二级喷水减温器进口汽温1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0207B | #1 B RS SSD IN Temp. 1 | 0 | 600 | ℃ | %Z025110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0207B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 10 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
489 | %%O5501-01CV0521A-05 | 5501 | 5501-01CV0521A-05 | #1 Boiler left seal pot fiuidizing air main damper 1 control command #1锅炉左侧回料器流化风电动调节风门1控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 10 | AAI543-H | 4-20mA | Y |  | 5501-01CV0521A-05 | #1 B L SPFA MD 1 CO | 0 | 100 | % | %Z027110 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0521A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 10A | 10B
57 | %%I5501-01PT2101 | 5501 | 5501-01PT2101 | #1 Boiler superheater outlet header steam pressure 1 #1锅炉高过出口集箱蒸汽压力1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01PT2101 | #1 B SUPER OUT HS Pre 1 | 0 | 16 | Mpa | %Z031110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT2101 | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 10A | 10B | [9 empty] | 20190222删除一分二安全栅
121 | %%I5501-01CV0521B-06 | 5501 | 5501-01CV0521B-06 | #1 Boiler right seal pot fiuidizing air main damper 1 position #1锅炉右侧回料器流化风电动调节风门1阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01CV0521B-06 | #1 B R SPFA MD 1 ZF | 0 | 100 | % | %Z033110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0521B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 10B | 10A
249 | %%I5501-01TE0210B | 5501 | 5501-01TE0210B | #1 Boiler right side secondary spray desuperheater outlet temperature 1 #1锅炉右侧二级喷水减温器出口汽温1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0210B | #1 B RS SSD OUT Temp. 1 | 0 | 600 | ℃ | %Z035110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0210B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 10 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
505 | %%O5501-01CV0521B-05 | 5501 | 5501-01CV0521B-05 | #1 Boiler right seal pot fiuidizing air main damper 1 control command #1锅炉右侧回料器流化风电动调节风门1控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 10 | AAI543-H | 4-20mA | Y |  | 5501-01CV0521B-05 | #1 B R SPFA MD 1 CO | 0 | 100 | % | %Z037110 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0521B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 10A | 10B
73 | %%I5501-01PT2102 | 5501 | 5501-01PT2102 | #1 Boiler superheater outlet header steam pressure 2 #1锅炉高过出口集箱蒸汽压力2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01PT2102 | #1 B SUPER OUT HS Pre 2 | 0 | 16 | Mpa | %Z041110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT2102 | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 10A | 10B | [9 empty] | 20190222删除一分二安全栅
137 | %%I5501-01CV0522A-06 | 5501 | 5501-01CV0522A-06 | #1 Boiler left seal pot fiuidizing air main damper 2 position #1锅炉左侧回料器流化风电动调节风门2阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01CV0522A-06 | #1 B L SPFA MD 2 ZF | 0 | 100 | % | %Z043110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0522A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 10B | 10A
265 | %%I5501-01TE0211B | 5501 | 5501-01TE0211B | #1 Boiler right side secondary spray desuperheater outlet temperature 2 #1锅炉右侧二级喷水减温器出口汽温2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0211B | #1 B RS SSD OUT Temp. 2 | 0 | 600 | ℃ | %Z045110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0211B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 10 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
521 | %%O5501-01CV0522A-05 | 5501 | 5501-01CV0522A-05 | #1 Boiler left seal pot fiuidizing air main damper 2 control command #1锅炉左侧回料器流化风电动调节风门2控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 10 | AAI543-H | 4-20mA | Y |  | 5501-01CV0522A-05 | #1 B L SPFA MD 2 CO | 0 | 100 | % | %Z047110 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0522A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 10A | 10B
89 | %%I5501-01PT2103 | 5501 | 5501-01PT2103 | #1 Boiler superheater outlet header steam pressure 3 #1锅炉高过出口集箱蒸汽压力3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01PT2103 | #1 B SUPER OUT HS Pre 3 | 0 | 16 | Mpa | %Z051110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT2103 | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 10A | 10B | [9 empty] | 20190222删除一分二安全栅
153 | %%I5501-01CV0522B-06 | 5501 | 5501-01CV0522B-06 | #1 Boiler right seal pot fiuidizing air main damper 2 position #1锅炉右侧回料器流化风电动调节风门2阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01CV0522B-06 | #1 B R SPFA MD 2 ZF | 0 | 100 | % | %Z053110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0522B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 10B | 10A
281 | %%I5501-01TE0212B | 5501 | 5501-01TE0212B | #1 Boiler right side secondary spray desuperheater outlet temperature 3 #1锅炉右侧二级喷水减温器出口汽温3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0212B | #1 B RS SSD OUT Temp. 3 | 0 | 600 | ℃ | %Z055110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0212B | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 10 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
537 | %%O5501-01CV0522B-05 | 5501 | 5501-01CV0522B-05 | #1 Boiler right seal pot fiuidizing air main damper 2 control command #1锅炉右侧回料器流化风电动调节风门2控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 10 | AAI543-H | 4-20mA | Y |  | 5501-01CV0522B-05 | #1 B R SPFA MD 2 CO | 0 | 100 | % | %Z057110 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0522B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 10A | 10B
169 | %%I5501-01PT0521A | 5501 | 5501-01PT0521A | #1 Boiler high pressure fluidization fan A outlet pressure #1锅炉高压流化风机A出口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01PT0521A | #1 B HPFA A OUT Pre. | 0 | 0.16 | MPa | %Z061110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0521A | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 10A | 10B
297 | %%I5501-01TE0240 | 5501 | 5501-01TE0240 | #1 Boiler high temperature superheater pipe surface temperature 3 #1锅炉高温过热器管壁温度3 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0240 | #1 B MTS PS Temp. 3 | 0 | 700 | ℃ | %Z063110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0240 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 10 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
361 | %%I5501-01TE0538A | 5501 | 5501-01TE0538A | #1 Boiler left heater inlet fule temperature #1锅炉空预器左侧进口烟道温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0538A | #1 B L Heat IN fule T | 0 | 300 | ℃ | %Z064110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0538A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 10 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
553 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 10 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z067110 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 10A | 10B
649 | 5501-01CV0541B-07 | 5501 | 5501-01CV0541B-07 | #1 Boiler primary air fan B coupler fault #1锅炉一次风机B液偶执行器执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 10 | ADV151-P | SI | Y |  | 5501-01CV0541B-07 | #1 B PAF B coupler F |  |  |  | %Z065110 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0541B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 10A | 10B
185 | %%I5501-01PT0521B | 5501 | 5501-01PT0521B | #1 Boiler high pressure fluidization fan B outlet pressure #1锅炉高压流化风机B出口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01PT0521B | #1 B HPFA B OUT Pre. | 0 | 0.16 | MPa | %Z071110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0521B | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 10A | 10B
313 | %%I5501-01TE0243 | 5501 | 5501-01TE0243 | #1 Boiler high temperature superheater pipe surface temperature 6 #1锅炉高温过热器管壁温度6 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0243 | #1 B MTS PS Temp. 6 | 0 | 700 | ℃ | %Z073110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0243 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 10 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
377 | %%I5501-01TE0538B | 5501 | 5501-01TE0538B | #1 Boiler right heater inlet fule temperature #1锅炉空预器右侧进口烟道温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0538B | #1 B R Heat IN fule T | 0 | 300 | ℃ | %Z074110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0538B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 10 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
425 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 10 | AAI143-H | 4-20mA | N | [6 empty] | %Z075110 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 10 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
585 | 5501-01CV0513E-07 | 5501 | 5501-01CV0513E-07 | #1 Boiler front wall upper layer secondary air inlet motor damper 5 fault #1锅炉前墙上层二次风入口电动调节风门5执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 10 | ADV151-P | SI | N |  | 5501-01CV0513E-07 | #1 B FWUL SAIN MD 5 F |  |  |  | %Z076110 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0513E-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 10A | 10B
201 | %%I5501-01PT0521C | 5501 | 5501-01PT0521C | #1 Boiler high pressure fluidization fan C outlet pressure #1锅炉高压流化风机C出口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01PT0521C | #1 B HPFA C OUT Pre. | 0 | 0.16 | MPa | %Z081110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0521C | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 10A | 10B
329 | %%I5501-01TE0246 | 5501 | 5501-01TE0246 | #1 Boiler high temperature superheater pipe surface temperature 9 #1锅炉高温过热器管壁温度9 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0246 | #1 B MTS PS Temp. 9 | 0 | 700 | ℃ | %Z083110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0246 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 10 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
393 | %%I5501-01TE0539A | 5501 | 5501-01TE0539A | #1 Boiler left heater outlet fule temperature #1锅炉空预器左侧出口烟道温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0539A | #1 B L Heat OUT fule T | 0 | 200 | ℃ | %Z084110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0539A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 10 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
441 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 10 | AAI143-H | 4-20mA | N | [6 empty] | %Z085110 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 10 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
617 | 5501-01CV0514E-07 | 5501 | 5501-01CV0514E-07 | #1 Boiler front wall down layer secondary air inlet motor damper 5 fault #1锅炉前墙下层二次风入口电动调节风门5执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 10 | ADV151-P | SI | N |  | 5501-01CV0514E-07 | #1 B FWDL SAIN MD 5 F |  |  |  | %Z086110 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0514E-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 10A | 10B
217 | %%I5501-01PT0522 | 5501 | 5501-01PT0522 | #1 Boiler high pressure fluidization fan outlet main pipe pressure #1锅炉高压流化风机出口母管压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 10 | AAI143-H | 4-20mA | Y |  | 5501-01PT0522 | #1 B HPFA OUT MP pre | 0 | 0.16 | MPa | %Z091110 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0522 | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 10A | 10B
345 | %%I5501-01TE0249 | 5501 | 5501-01TE0249 | #1 Boiler high temperature superheater pipe surface temperature 12 #1锅炉高温过热器管壁温度12 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0249 | #1 B MTS PS Temp. 12 | 0 | 700 | ℃ | %Z093110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0249 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 10 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
409 | %%I5501-01TE0539B | 5501 | 5501-01TE0539B | #1 Boiler right heater outlet fule temperature #1锅炉空预器右侧出口烟道温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 10 | AAI143-H | 4-20mA | N |  | 5501-01TE0539B | #1 B R Heat OUT fule T | 0 | 200 | ℃ | %Z094110 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0539B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 10 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
457 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 10 | AAI143-H | 4-20mA | N | [6 empty] | %Z095110 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 10 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
569 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 10 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z097110 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD06 | 10 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 10A | 10B
10 | %%I5501-01FT0601 | 5501 | 5501-01FT0601 | #1 Boiler over-bed burner oil inlet flow #1锅炉床上燃烧器进油流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 11 | AAI143-H | 4-20mA | N |  | 5501-01FT0601 | #1 B OB Burnoil IN flow | 0 | 7 | t/h | %Z011111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0601 | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 11A | 11B
26 | %%I5501-01FT0602 | 5501 | 5501-01FT0602 | #1 Boiler oil return flow #1锅炉回油流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 11 | AAI143-H | 4-20mA | N |  | 5501-01FT0602 | #1 B oil return flow | 0 | 8 | t/h | %Z012111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0602 | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 11A | 11B
42 | %%I5501-01PT0621A | 5501 | 5501-01PT0621A | #1 Boiler In-duct burner A oil inlet pressure #1锅炉风道燃烧器A进油压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01PT0621A | #1 B IDB A oil IN Pre | 0 | 6 | Mpa | %Z021111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0621A | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 11A | 11B
106 | %%I5501-01CV0541A-06 | 5501 | 5501-01CV0541A-06 | #1 Boiler primary air fan A coupler position #1锅炉一次风机A液偶执行器阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01CV0541A-06 | #1 B PAF A coupler ZF | 0 | 100 | % | %Z023111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0541A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 11B | 11A
234 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 11 | AAI143-H | 4-20mA | N | [6 empty] | %Z025111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI | [11 empty] | 5501-01DCS-SBC-01 | SPD01 | 11 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1- | [9 empty] | 20190222更换通道到此
490 | %%O5501-01CV0541A-05 | 5501 | 5501-01CV0541A-05 | #1 Boiler primary air fan A coupler control command #1锅炉一次风机A液偶执行器控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 11 | AAI543-H | 4-20mA | Y |  | 5501-01CV0541A-05 | #1 B PAF A coupler CO | 0 | 100 | % | %Z027111 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0541A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 11A | 11B
58 | %%I5501-01PT0621B | 5501 | 5501-01PT0621B | #1 Boiler In-duct burner B oil inlet pressure #1锅炉风道燃烧器B进油压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01PT0621B | #1 B IDB B oil IN Pre | 0 | 6 | Mpa | %Z031111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0621B | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 11A | 11B
122 | %%I5501-01CV0541B-06 | 5501 | 5501-01CV0541B-06 | #1 Boiler primary air fan B coupler position #1锅炉一次风机B液偶执行器阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01CV0541B-06 | #1 B PAF B coupler ZF | 0 | 100 | % | %Z033111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0541B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 11B | 11A
250 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 11 | AAI143-H | 4-20mA | N | [6 empty] | %Z035111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 11 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
506 | %%O5501-01CV0541B-05 | 5501 | 5501-01CV0541B-05 | #1 Boiler primary air fan B coupler control command #1锅炉一次风机B液偶执行器控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 11 | AAI543-H | 4-20mA | Y |  | 5501-01CV0541B-05 | #1 B PAF B coupler CO | 0 | 100 | % | %Z037111 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0541B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 11A | 11B
74 | %%I5501-01FT2101 | 5501 | 5501-01FT2101 | #1 Boiler superheater outlet header steam flow 1 #1锅炉高过出口集箱蒸汽流量1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01FT2101 | #1 B SUPER OUT HS flow1 | 0 | 400 | t/h | %Z041111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT2101 | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 11A | 11B | [9 empty] | 20190222删除一分二安全栅
138 | %%I5501-01CV0556A-06 | 5501 | 5501-01CV0556A-06 | #1 Boiler secondary air fan A coupler position #1锅炉二次风机A液偶执行器阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01CV0556A-06 | #1 B SAF A coupler ZF | 0 | 100 | % | %Z043111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0556A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 11B | 11A
266 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 11 | AAI143-H | 4-20mA | N | [6 empty] | %Z045111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 11 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
522 | %%O5501-01CV0556A-05 | 5501 | 5501-01CV0556A-05 | #1 Boiler secondary air fan A coupler control command #1锅炉二次风机A液偶执行器控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 11 | AAI543-H | 4-20mA | Y |  | 5501-01CV0556A-05 | #1 B SAF A coupler CO | 0 | 100 | % | %Z047111 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0556A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 11A | 11B
90 | %%I5501-01FT2102 | 5501 | 5501-01FT2102 | #1 Boiler superheater outlet header steam flow 2 #1锅炉高过出口集箱蒸汽流量2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01FT2102 | #1 B SUPER OUT HS flow2 | 0 | 400 | t/h | %Z051111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT2102 | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 11A | 11B
154 | %%I5501-01CV0556B-06 | 5501 | 5501-01CV0556B-06 | #1 Boiler secondary air fan B coupler position #1锅炉二次风机B液偶执行器阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01CV0556B-06 | #1 B SAF B coupler ZF | 0 | 100 | % | %Z053111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0556B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 11B | 11A
282 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 11 | AAI143-H | 4-20mA | N | [6 empty] | %Z055111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 11 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
538 | %%O5501-01CV0556B-05 | 5501 | 5501-01CV0556B-05 | #1 Boiler secondary air fan B coupler control command #1锅炉二次风机B液偶执行器控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 11 | AAI543-H | 4-20mA | Y |  | 5501-01CV0556B-05 | #1 B SAF B coupler CO | 0 | 100 | % | %Z057111 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0556B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 11A | 11B
170 | %%I5501-01PT0523 | 5501 | 5501-01PT0523 | #1 Boiler cooling air for oil system main pipe pressure #1锅炉燃烧器火检冷却风母管压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01PT0523 | #1 B CA for OS MP pre | 0 | 0.16 | MPa | %Z061111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0523 | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 11A | 11B
298 | %%I5501-01TE0401 | 5501 | 5501-01TE0401 | #1 Boiler left soot blowing drain temperature #1锅炉左墙吹灰疏水温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 11 | AAI143-H | 4-20mA | N |  | 5501-01TE0401 | #1 B L SBD Temp. | 0 | 600 | ℃ | %Z063111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0401 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 11 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
362 | %%I5501-01TE0503A | 5501 | 5501-01TE0503A | #1 Boiler air duct burner A outlet temperature #1锅炉风道燃烧器A出口温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 11 | AAI143-H | 4-20mA | N |  | 5501-01TE0503A | #1 B ADB A OUT Temp. | 0 | 1000 | ℃ | %Z064111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0503A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 11 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
554 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 11 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z067111 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 11A | 11B
650 | 5501-01CV0556A-07 | 5501 | 5501-01CV0556A-07 | #1 Boiler secondary air fan A coupler fault #1锅炉二次风机A液偶执行器执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 11 | ADV151-P | SI | Y |  | 5501-01CV0556A-07 | #1 B SAF A coupler F |  |  |  | %Z065111 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0556A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 11A | 11B
186 | %%I5501-01FT0531 | 5501 | 5501-01FT0531 | #1 Boiler purge air for cyclone inlet flow #1锅炉分离器入口吹扫风流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01FT0531 | #1 B PA for CYC IN flow | 0 | 3866 | Nm3/h | %Z071111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0531 | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 11A | 11B
314 | %%I5501-01TE0402 | 5501 | 5501-01TE0402 | #1 Boiler right soot blowing drain temperature #1锅炉右墙吹灰疏水温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 11 | AAI143-H | 4-20mA | N |  | 5501-01TE0402 | #1 B R SBD Temp. | 0 | 600 | ℃ | %Z073111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0402 | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 11 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
378 | %%I5501-01TE0503B | 5501 | 5501-01TE0503B | #1 Boiler air duct burner B outlet temperature #1锅炉风道燃烧器B出口温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 11 | AAI143-H | 4-20mA | N |  | 5501-01TE0503B | #1 B ADB B OUT Temp. | 0 | 1000 | ℃ | %Z074111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0503B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 11 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
426 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 11 | AAI143-H | 4-20mA | N | [6 empty] | %Z075111 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 11 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
586 | 5501-01CV0515A-07 | 5501 | 5501-01CV0515A-07 | #1 Boiler back wall upper layer secondary air inlet motor damper 1 fault #1锅炉后墙上层二次风入口电动调节风门1执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 11 | ADV151-P | SI | N |  | 5501-01CV0515A-07 | #1 B BWUL SAIN MD 1 F |  |  |  | %Z076111 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0515A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 11A | 11B
202 | %%I5501-01PT0534A | 5501 | 5501-01PT0534A | #1 Boiler induced draft fan A outlet pressure #1锅炉引风机A出口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01PT0534A | #1 B IDF A outlet Pre. | 0 | 20 | Kpa | %Z081111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0534A | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 11A | 11B
330 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 11 | AAI143-H | 4-20mA | N | [6 empty] | %Z083111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 11 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
394 | %%I5501-01TE0502A | 5501 | 5501-01TE0502A | #1 Boiler left hot primary air temperature #1锅炉左侧热一次风温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 11 | AAI143-H | 4-20mA | N |  | 5501-01TE0502A | #1 B L HPA Temp.. | 0 | 300 | ℃ | %Z084111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0502A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 11 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1- | [9 empty] | 2017.11.9修改
442 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 11 | AAI143-H | 4-20mA | N | [6 empty] | %Z085111 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 11 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
618 | 5501-01CV0516A-07 | 5501 | 5501-01CV0516A-07 | #1 Boiler back wall down layer secondary air inlet motor damper 1 fault #1锅炉后墙下层二次风入口电动调节风门1执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 11 | ADV151-P | SI | N |  | 5501-01CV0516A-07 | #1 B BWDL SAIN MD 1 F |  |  |  | %Z086111 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0516A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 11A | 11B
218 | %%I5501-01PT0534B | 5501 | 5501-01PT0534B | #1 Boiler induced draft fan B outlet pressure #1锅炉引风机B出口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 11 | AAI143-H | 4-20mA | Y |  | 5501-01PT0534B | #1 B IDF B outlet Pre. | 0 | 20 | Kpa | %Z091111 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0534B | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 11A | 11B
346 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 11 | AAI143-H | 4-20mA | N | [6 empty] | %Z093111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 11 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
410 | %%I5501-01TE0502B | 5501 | 5501-01TE0502B | #1 Boiler right hot primary air temperature #1锅炉右侧热一次风温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 11 | AAI143-H | 4-20mA | N |  | 5501-01TE0502B | #1 B R HPA Temp.. | 0 | 300 | ℃ | %Z094111 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0502B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 11 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1- | [9 empty] | 2017.11.9修改
458 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 11 | AAI143-H | 4-20mA | N | [6 empty] | %Z095111 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 11 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
570 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 11 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z097111 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD06 | 11 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 11A | 11B
11 | %%I5501-01FT0621A | 5501 | 5501-01FT0621A | #1 Boiler In-duct burner A oil inlet flow #1锅炉风道燃烧器A进油流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 12 | AAI143-H | 4-20mA | N |  | 5501-01FT0621A | #1 B IDB A oil IN flow | 0 | 0.5 | t/h | %Z011112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0621A | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 12A | 12B
27 | %%I5501-01FT0621B | 5501 | 5501-01FT0621B | #1 Boiler In-duct burner B oil inlet flow #1锅炉风道燃烧器B进油流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 12 | AAI143-H | 4-20mA | N |  | 5501-01FT0621B | #1 B IDB B oil IN flow | 0 | 0.5 | t/h | %Z012112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0621B | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 12A | 12B
43 | %%I5501-01FT2421A | 5501 | 5501-01FT2421A | #1 Boiler feed water main pipe flow 1 #1锅炉给水母管流量1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01FT2421A | #1 B FW MP flow 1 | 0 | 450 | t/h | %Z021112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT2421A | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 12A | 12B
107 | %%I5501-01CV0571A-06 | 5501 | 5501-01CV0571A-06 | #1 Boiler induced draft fan A coupler position #1锅炉引风机A液偶执行器阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01CV0571A-06 | #1 B IDF A coupler ZF | 0 | 100 | % | %Z023112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0571A-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 12B | 12A
235 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z025112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 12 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
491 | %%O5501-01CV0571A-05 | 5501 | 5501-01CV0571A-05 | #1 Boiler induced draft fan A coupler control command #1锅炉引风机A液偶执行器控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 12 | AAI543-H | 4-20mA | Y |  | 5501-01CV0571A-05 | #1 B IDF A coupler CO | 0 | 100 | % | %Z027112 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0571A-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 12A | 12B
59 | %%I5501-01FT2421B | 5501 | 5501-01FT2421B | #1 Boiler feed water main pipe flow 2 #1锅炉给水母管流量2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01FT2421B | #1 B FW MP flow 2 | 0 | 450 | t/h | %Z031112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT2421B | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 12A | 12B
123 | %%I5501-01CV0571B-06 | 5501 | 5501-01CV0571B-06 | #1 Boiler induced draft fan A coupler position #1锅炉引风机B液偶执行器阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01CV0571B-06 | #1 B IDF B coupler ZF | 0 | 100 | % | %Z033112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0571B-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 12B | 12A
251 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z035112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 12 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
507 | %%O5501-01CV0571B-05 | 5501 | 5501-01CV0571B-05 | #1 Boiler induced draft fan A coupler control command #1锅炉引风机B液偶执行器控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 12 | AAI543-H | 4-20mA | Y |  | 5501-01CV0571B-05 | #1 B IDF B coupler CO | 0 | 100 | % | %Z037112 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0571B-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 12A | 12B
75 | %%I5501-01TC2331A | 5501 | 5501-01TC2331A | #1 Boiler slag cooler A water outlet temperature #1锅炉冷渣器A回水温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01TC2331A | #1 B SC A W OUT Temp. | 0 | 100 | ℃ | %Z041112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01TC2331A | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 12A | 12B
139 | %%I5501-01CV0301-06 | 5501 | 5501-01CV0301-06 | #1 Boiler continuous blowdown flash tank electric control valve position #1锅炉连续排污扩容器电动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01CV0301-06 | #1 B CBF tank EV ZF | 0 | 100 | % | %Z043112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0301-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 12B | 12A
267 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z045112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 12 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
523 | %%O5501-01CV0301-05 | 5501 | 5501-01CV0301-05 | #1 Boiler continuous blowdown flash tank electric control valve control command #1锅炉连续排污扩容器电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 12 | AAI543-H | 4-20mA | Y |  | 5501-01CV0301-05 | #1 B CBF tank EV CO | 0 | 100 | % | %Z047112 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0301-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 12A | 12B
91 | %%I5501-01TC2331B | 5501 | 5501-01TC2331B | #1 Boiler slag cooler B water outlet temperature #1锅炉冷渣器B回水温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01TC2331B | #1 B SC B W OUT Temp. | 0 | 100 | ℃ | %Z051112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01TC2331B | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 12A | 12B
155 | %%I5501-01CV0302-06 | 5501 | 5501-01CV0302-06 | #1 Boiler periodic blowdown header blowdown electric control valve position #1锅炉定期排污母管集箱排污电动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01CV0302-06 | #1 Boiler PBHB EV ZF | 0 | 100 | % | %Z053112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0302-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 12B | 12A
283 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z055112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 12 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
539 | %%O5501-01CV0302-05 | 5501 | 5501-01CV0302-05 | #1 Boiler periodic blowdown header blowdown electric control valve control command #1锅炉定期排污母管集箱排污电动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 12 | AAI543-H | 4-20mA | Y |  | 5501-01CV0302-05 | #1 Boiler PBHB EV CO | 0 | 100 | % | %Z057112 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0302-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 12A | 12B
171 | %%I5501-01PT0531A | 5501 | 5501-01PT0531A | #1 Boiler left cyclone outlet fule pressure #1锅炉左侧旋风分离器出口烟道压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01PT0531A | #1 B L CYC OUT fule Pre | -2.6 | 0 | Kpa | %Z061112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0531A | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 12A | 12B
299 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z063112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 12 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
363 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z064112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 12 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
555 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 12 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z067112 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 12A | 12B
651 | 5501-01CV0556B-07 | 5501 | 5501-01CV0556B-07 | #1 Boiler secondary air fan B coupler fault #1锅炉二次风机B液偶执行器执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 12 | ADV151-P | SI | Y |  | 5501-01CV0556B-07 | #1 B SAF B coupler F |  |  |  | %Z065112 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0556B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 12A | 12B
187 | %%I5501-01PT0531B | 5501 | 5501-01PT0531B | #1 Boiler right cyclone outlet fule pressure #1锅炉右侧旋风分离器出口烟道压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01PT0531B | #1 B R CYC OUT fule Pre | -2.6 | 0 | Kpa | %Z071112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0531B | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 12A | 12B
315 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z073112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 12 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
379 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z074112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 12 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
427 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z075112 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 12 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
587 | 5501-01CV0515B-07 | 5501 | 5501-01CV0515B-07 | #1 Boiler back wall upper layer secondary air inlet motor damper 2 fault #1锅炉后墙上层二次风入口电动调节风门2执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 12 | ADV151-P | SI | N |  | 5501-01CV0515B-07 | #1 B BWUL SAIN MD 2 F |  |  |  | %Z076112 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0515B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 12A | 12B
203 | %%I5501-01PT0541A | 5501 | 5501-01PT0541A | #1 Boiler primary air fan A coupler oil outlet pressure #1锅炉一次风机A耦合器出油口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01PT0541A | #1 B PAF A C O Out Pre | 0 | 0.6 | Mpa | %Z081112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0541A | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 12A | 12B
331 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z083112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 12 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
395 | %%I5501-01TE0512A | 5501 | 5501-01TE0512A | #1 Boiler left hot secondary air temperature #1锅炉左侧热二次风温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 12 | AAI143-H | 4-20mA | N |  | 5501-01TE0512A | #1 B L HSA Temp.. | 0 | 200 | ℃ | %Z084112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0512A | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 12 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1- | [9 empty] | 2017.11.9修改
443 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z085112 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 12 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
619 | 5501-01CV0516B-07 | 5501 | 5501-01CV0516B-07 | #1 Boiler back wall down layer secondary air inlet motor damper 2 fault #1锅炉后墙下层二次风入口电动调节风门2执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 12 | ADV151-P | SI | N |  | 5501-01CV0516B-07 | #1 B BWDL SAIN MD 2 F |  |  |  | %Z086112 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0516B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 12A | 12B
219 | %%I5501-01PT0541B | 5501 | 5501-01PT0541B | #1 Boiler primary air fan B coupler oil outlet pressure #1锅炉一次风机B耦合器出油口压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 12 | AAI143-H | 4-20mA | Y |  | 5501-01PT0541B | #1 B PAF B C O Out Pre | 0 | 0.6 | Mpa | %Z091112 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0541B | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 12A | 12B
347 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z093112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 12 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
411 | %%I5501-01TE0512B | 5501 | 5501-01TE0512B | #1 Boiler right hot secondary air temperature #1锅炉右侧热二次风温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 12 | AAI143-H | 4-20mA | N |  | 5501-01TE0512B | #1 B R HSA Temp.. | 0 | 200 | ℃ | %Z094112 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  | 5501-01TE0512B | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 12 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1- | [9 empty] | 2017.11.9修改
459 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 12 | AAI143-H | 4-20mA | N | [6 empty] | %Z095112 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 12 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
571 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 12 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z097112 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD06 | 12 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 12A | 12B
12 | %%I5501-01PT3402 | 5501 | 5501-01PT3402 | #1 Boiler Primary&secondary air fan and fluidization fan inlet main pipe water pressure 1 #1锅炉一次风机、二次风机、流化风机冷却水进水母管压力1 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 13 | AAI143-H | 4-20mA | N |  | 5501-01PT3402 | #1 B P&SAF IN MP W Pre1 | 0 | 1 | Mpa | %Z011113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT3402 | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 13A | 13B
28 | %%I5501-01PT3403 | 5501 | 5501-01PT3403 | #1 Boiler Primary&secondary air fan and fluidization fan inlet main pipe water pressure 2 #1锅炉一次风机、二次风机、流化风机冷却水进水母管压力2 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 13 | AAI143-H | 4-20mA | N |  | 5501-01PT3403 | #1 B P&SAF IN MP W Pre2 | 0 | 1 | Mpa | %Z012113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT3403 | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 13A | 13B
44 | %%I5501-01LT0301 | 5501 | 5501-01LT0301 | #1 Boiler continuous blowdown flash tank level #1锅炉连续排污扩容器液位 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 13 | AAI143-H | 4-20mA | Y |  | 5501-01LT0301 | #1 B CB flash tank L | 0 | 600 | mmH2O | %Z021113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01LT0301 | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 13A | 13B
108 | %%I5501-01CV0601-06 | 5501 | 5501-01CV0601-06 | #1 Boiler burner oil supply main pipe control valve position #1锅炉床上燃烧器供油母管气动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 13 | AAI143-H | 4-20mA | Y |  | 5501-01CV0601-06 | #1 B Burn OSMP CV ZF | 0 | 100 | % | %Z023113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0601-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 13B | 13A
236 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z025113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 13 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
492 | %%O5501-01CV0601-05 | 5501 | 5501-01CV0601-05 | #1 Boiler burner oil supply main pipe control valve control command #1锅炉床上燃烧器供油母管气动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 13 | AAI543-H | 4-20mA | Y |  | 5501-01CV0601-05 | #1 B Burn OSMP CV CO | 0 | 100 | % | %Z027113 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0601-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 13A | 13B
60 | %%I5501-01FT1102 | 5501 | 5501-01FT1102 | #1 Boiler urea solution flow #1锅炉尿素溶液流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 13 | AAI143-H | 4-20mA | Y |  | 5501-01FT1102 | #1 B ures SOL flow | 0 | 0.5 | m3/h | %Z031113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT1102 | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 13A | 13B
124 | %%I5501-01CV0401-06 | 5501 | 5501-01CV0401-06 | #1 Boiler soot blowing steam pressure control valve position #1锅炉吹灰蒸汽进汽调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 13 | AAI143-H | 4-20mA | Y |  | 5501-01CV0401-06 | #1 B SBS PCV ZF | 0 | 100 | % | %Z033113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0401-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 13B | 13A
252 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z035113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 13 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
508 | %%O5501-01CV0401-05 | 5501 | 5501-01CV0401-05 | #1 Boiler soot blowing steam pressure control valve control command #1锅炉吹灰蒸汽进汽调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 13 | AAI543-H | 4-20mA | Y |  | 5501-01CV0401-05 | #1 B SBS PCV CO | 0 | 100 | % | %Z037113 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV0401-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 13A | 13B
76 | %%I5501-01LT0902 | 5501 | 5501-01LT0902 | #1 Boiler buffer material level #1锅炉中间料仓料位 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 13 | AAI143-H | 4-20mA | Y |  | 5501-01LT0902 | #1 B buffer Lev. | 0 |  | m | %Z041113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01LT0902 | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 13A | 13B
140 | %%I5501-01CV2331-06 | 5501 | 5501-01CV2331-06 | #1 Boiler slag cooler inlet water pneumatic control valve position #1锅炉冷渣器进水气动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 13 | AAI143-H | 4-20mA | Y |  | 5501-01CV2331-06 | #1 B SC IN WPCV ZF | 0 | 100 | % | %Z043113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV2331-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD08 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 13B | 13A
268 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z045113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 13 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
524 | %%O5501-01CV2331-05 | 5501 | 5501-01CV2331-05 | #1 Boiler slag cooler inlet water pneumatic control valve control command #1锅炉冷渣器进水气动调节阀控制指令 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 13 | AAI543-H | 4-20mA | Y |  | 5501-01CV2331-05 | #1 B SC IN WPCV CO | 0 | 100 | % | %Z047113 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-01CV2331-05 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 13A | 13B
92 | %%I5501-01Y01D-M06 | 5501 | 5501-01Y01D-M06 | #1炉给煤机D频率反馈 #1 Boiler coal feeder D frequency |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 13 | AAI143-H | 4-20mA | Y |  | 5501-01Y01D-M06 | #1 B coal feed D Freq |  |  |  | %Z051113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 01-Y-01D(M)-06 | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 13A | 13B
156 | %%I5501-01ST0556B | 5501 | 5501-01ST0556B | #1 Boiler secondary air fan B speed #1锅炉二次风机B转速 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 13 | AAI143-H | 4-20mA | Y |  | 5501-01ST0556B | #1 B SAF B speed | 0 | 1500 | rpm | %Z053113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01ST0556B | [7 empty] | 5501-01DCS-AMC-01 | SPD10 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 13A | 13B
284 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z055113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 13 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
540 | %%O5501-01Y01D-M15 | 5501 | 5501-01Y01D-M15 | #1炉给煤机D速度调节 #1 Boiler coal feeder D speed control |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 13 | AAI543-H | 4-20mA | Y |  | 5501-01Y01D-M15 | #1 B coal feed D Ins C | 0 | 100 | % | %Z057113 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 01-Y-01D(M)-15 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 13A | 13B
172 | %%I5501-01PT0601 | 5501 | 5501-01PT0601 | #1 Boiler burner cooling air pressure #1锅炉燃烧器冷却风压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 13 | AAI143-H | 4-20mA | Y |  | 5501-01PT0601 | #1 B burner CA Pre. | 0 | 1 | MPa | %Z061113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0601 | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 13A | 13B
300 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z063113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 13 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
364 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z064113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 13 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
556 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 13 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z067113 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 13A | 13B
652 | 5501-01CV0571A-07 | 5501 | 5501-01CV0571A-07 | #1 Boiler induced draft fan A coupler fault #1锅炉引风机A液偶执行器执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 13 | ADV151-P | SI | Y |  | 5501-01CV0571A-07 | #1 B IDF A coupler F |  |  |  | %Z065113 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0571A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 13A | 13B
188 | %%I5501-00PT0301 | 5501 | 5501-00PT0301 | #1 、#2 Boiler intermittent blowdown flash tank pressure #1、#2锅炉定期排污扩容器压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 13 | AAI143-H | 4-20mA | Y |  | 5501-00PT0301 | #1 #2 B IBFTPre. | 0 | 1 | MPa | %Z071113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-00PT0301 | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 13A | 13B
316 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z073113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 13 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
380 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z074113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 13 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
428 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z075113 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 13 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
588 | 5501-01CV0515C-07 | 5501 | 5501-01CV0515C-07 | #1 Boiler back wall upper layer secondary air inlet motor damper 3 fault #1锅炉后墙上层二次风入口电动调节风门3执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 13 | ADV151-P | SI | N |  | 5501-01CV0515C-07 | #1 B BWUL SAIN MD 3 F |  |  |  | %Z076113 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0515C-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 13A | 13B
204 | %%I5501-01FT0301 | 5501 | 5501-01FT0301 | #1 Boiler continuous blowdown flow #1锅炉连续排污流量 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 13 | AAI143-H | 4-20mA | Y |  | 5501-01FT0301 | #1 Boiler CB flow | 0 | 6 | t/h | %Z081113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01FT0301 | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 13A | 13B
332 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z083113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 13 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
396 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z084113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 13 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
444 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z085113 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 13 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
620 | 5501-01CV0516C-07 | 5501 | 5501-01CV0516C-07 | #1 Boiler back wall down layer secondary air inlet motor damper 3 fault #1锅炉后墙下层二次风入口电动调节风门3执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 13 | ADV151-P | SI | N |  | 5501-01CV0516C-07 | #1 B BWDL SAIN MD 3 F |  |  |  | %Z086113 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0516C-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 13A | 13B
220 | %%I5501-43E101B-M18 | 5501 | 5501-43E101B-M18 | #1炉冷渣机B电机B转速反馈 #1 Boiler slag cooler B motor speed (4-20mA) |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 13 | AAI143-H | 4-20mA | Y |  | 5501-43E101B-M18 | #1 B SC B motor SPD |  |  |  | %Z091113 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 43-E101B(M)-18 | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 13A | 13B
348 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z093113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 13 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
412 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z094113 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 13 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
460 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 13 | AAI143-H | 4-20mA | N | [6 empty] | %Z095113 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 13 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
572 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 13 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z097113 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD06 | 13 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 13A | 13B
13 | %%I5501-01PT0524A | 5501 | 5501-01PT0524A | #1 Boiler left seal pot fiuidizing air main pipe pressure #1锅炉左侧回料器流化风母管压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 14 | AAI143-H | 4-20mA | N |  | 5501-01PT0524A | #1 B L SP FAMP Pre. | 0 | 80 | kPa | %Z011114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0524A | [7 empty] | 5501-01DCS-AMC-02 | SPD07 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 14A | 14B | [9 empty] | 2018.4.17新增
29 | %%I5501-01PT0524B | 5501 | 5501-01PT0524B | #1 Boiler right seal pot fiuidizing air main pipe pressure #1锅炉右侧回料器流化风母管压力 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 14 | AAI143-H | 4-20mA | N |  | 5501-01PT0524B | #1 B R SP FAMP Pre. | 0 | 80 | kPa | %Z012114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01PT0524B | [7 empty] | 5501-01DCS-AMC-02 | SPD08 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 14A | 14B | [9 empty] | 2018.4.17新增
45 | %%I5501-01Y01A-M06 | 5501 | 5501-01Y01A-M06 | #1炉给煤机A频率反馈 #1 Boiler coal feeder A frequency |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 14 | AAI143-H | 4-20mA | Y |  | 5501-01Y01A-M06 | #1 B coal feed A Freq |  |  |  | %Z021114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 01-Y-01A(M)-06 | [7 empty] | 5501-01DCS-AMC-01 | SPD01 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 14A | 14B
109 | %%I5501-01ST0541A | 5501 | 5501-01ST0541A | #1 Boiler primary air fan A speed #1锅炉一次风机A转速 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 14 | AAI143-H | 4-20mA | Y |  | 5501-01ST0541A | #1 B PAF A speed | 0 | 1500 | rpm | %Z023114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01ST0541A | [7 empty] | 5501-01DCS-AMC-01 | SPD02 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 14A | 14B
237 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z025114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 14 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
493 | %%O5501-01Y01A-M15 | 5501 | 5501-01Y01A-M15 | #1炉给煤机A速度调节 #1 Boiler coal feeder A speed control |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 14 | AAI543-H | 4-20mA | Y |  | 5501-01Y01A-M15 | #1 B coal feed A Ins C | 0 | 100 | % | %Z027114 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 01-Y-01A(M)-15 | [7 empty] | 5501-01DCS-AMC-01 | SPD05 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 14A | 14B
61 | %%I5501-01Y01B-M06 | 5501 | 5501-01Y01B-M06 | #1炉给煤机B频率反馈 #1 Boiler coal feeder B frequency |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 14 | AAI143-H | 4-20mA | Y |  | 5501-01Y01B-M06 | #1 B coal feed B Freq |  |  |  | %Z031114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 01-Y-01B(M)-06 | [7 empty] | 5501-01DCS-AMC-01 | SPD03 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 14A | 14B
125 | %%I5501-01ST0541B | 5501 | 5501-01ST0541B | #1 Boiler primary air fan B speed #1锅炉一次风机B转速 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 14 | AAI143-H | 4-20mA | Y |  | 5501-01ST0541B | #1 B PAF B speed | 0 | 1500 | rpm | %Z033114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01ST0541B | [7 empty] | 5501-01DCS-AMC-01 | SPD04 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 14A | 14B
253 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z035114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 14 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
509 | %%O5501-01Y01B-M15 | 5501 | 5501-01Y01B-M15 | #1炉给煤机B速度调节 #1 Boiler coal feeder B speed control |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 14 | AAI543-H | 4-20mA | Y |  | 5501-01Y01B-M15 | #1 B coal feed B Ins C | 0 | 100 | % | %Z037114 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 01-Y-01B(M)-15 | [7 empty] | 5501-01DCS-AMC-01 | SPD06 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 14A | 14B
77 | %%I5501-01Y01C-M06 | 5501 | 5501-01Y01C-M06 | #1炉给煤机C频率反馈 #1 Boiler coal feeder C frequency |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 14 | AAI143-H | 4-20mA | Y |  | 5501-01Y01C-M06 | #1 B coal feed C Freq |  |  |  | %Z041114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 01-Y-01C(M)-06 | [7 empty] | 5501-01DCS-AMC-01 | SPD07 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 14A | 14B
141 | %%I5501-01ST0556A | 5501 | 5501-01ST0556A | #1 Boiler secondary air fan A speed #1锅炉二次风机A转速 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 14 | AAI143-H | 4-20mA | Y |  | 5501-01ST0556A | #1 B SAF A speed | 0 | 1500 | rpm | %Z043114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01ST0556A | [7 empty] | 5501-01DCS-AMC-01 | SPD08 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 14A | 14B
269 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z045114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 14 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
525 | %%O5501-01Y01C-M15 | 5501 | 5501-01Y01C-M15 | #1炉给煤机C速度调节 #1 Boiler coal feeder C speed control |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 14 | AAI543-H | 4-20mA | Y |  | 5501-01Y01C-M15 | #1 B coal feed C Ins C | 0 | 100 | % | %Z047114 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 01-Y-01C(M)-15 | [7 empty] | 5501-01DCS-AMC-01 | SPD11 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPB11 | A1BA4D-05 | 14A | 14B
93 | %%I5501-45S101-12 | 5501 | 5501-45S101-12 | #1 Electric feeder frequencyfeedback #1电动给料机频率反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 14 | AAI143-H | 4-20mA | Y |  | 5501-45S101-12 | #1 Electric feeder ZF | 0 | 50 | HZ | %Z051114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-45-S101-12 | [7 empty] | 5501-01DCS-AMC-01 | SPD09 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 14A | 14B | [9 empty] | 2017.12.19删除20181120增加
157 | %%I5501-01ST0571B | 5501 | 5501-01ST0571B | #1 Boiler induced draft fan B speed #1锅炉引风机B转速 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 14 | AAI143-H | 4-20mA | Y |  | 5501-01ST0571B | #1 B IDF B speed | 0 | 1500 | rpm | %Z053114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01ST0571B | [7 empty] | 5501-01DCS-AMC-01 | SPD10 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 14A | 14B
285 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z055114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 14 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
541 | %%O5501-45S101-11 | 5501 | 5501-45S101-11 | #1 Electric feeder frequency command #1电动给料机频率给定 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 14 | AAI543-H | 4-20mA | Y |  | 5501-45S101-11 | #1 Electric feeder CO | 0 | 50 | Hz | %Z057114 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO |  |  |  | 5501-45-S101-11 | [7 empty] | 5501-01DCS-AMC-01 | SPD12 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPB12 | A1BA4D-05 | 14A | 14B | [9 empty] | 20181120增加
173 | %%I5501-43E101A-M18 | 5501 | 5501-43E101A-M18 | #1炉冷渣机A电机A转速反馈 #1 Boiler slag cooler A motor speed (4-20mA) |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 14 | AAI143-H | 4-20mA | Y |  | 5501-43E101A-M18 | #1 B SC A motor SPD |  |  |  | %Z061114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 43-E101A(M)-18 | [7 empty] | 5501-01DCS-AMC-02 | SPD01 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 14A | 14B
301 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z063114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 14 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
365 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z064114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 14 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
557 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 14 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z067114 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD05 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPB05 | A1BA4D-05 | 14A | 14B
653 | 5501-01CV0571B-07 | 5501 | 5501-01CV0571B-07 | #1 Boiler induced draft fan A coupler fault #1锅炉引风机B液偶执行器执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 14 | ADV151-P | SI | Y |  | 5501-01CV0571B-07 | #1 B IDF B coupler F |  |  |  | %Z065114 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0571B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 14A | 14B
189 | %%I5501-00LT0301 | 5501 | 5501-00LT0301 | #1 、#2 Boiler intermittent blowdown flash tank level #1、#2锅炉定期排污扩容器液位 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 14 | AAI143-H | 4-20mA | Y |  | 5501-00LT0301 | #1 #2 B IBFTlevel | 0 | 600 | mmH2O | %Z071114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-00LT0301 | [7 empty] | 5501-01DCS-AMC-02 | SPD02 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 14A | 14B | [9 empty] | 2018.4.17增加
317 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z073114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 14 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
381 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z074114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 14 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
429 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z075114 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD06 | 14 | 4 | 5 | 6 | 1 | 2 | 3 | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
589 | 5501-01CV0515D-07 | 5501 | 5501-01CV0515D-07 | #1 Boiler back wall upper layer secondary air inlet motor damper 4 fault #1锅炉后墙上层二次风入口电动调节风门4执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 14 | ADV151-P | SI | N |  | 5501-01CV0515D-07 | #1 B BWUL SAIN MD 4 F |  |  |  | %Z076114 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0515D-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 14A | 14B
205 | %%I5501-01CV0621A-06 | 5501 | 5501-01CV0621A-06 | #1 Boiler In-duct burner A oil supply control valve position #1锅炉风道燃烧器A供油气动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 14 | AAI143-H | 4-20mA | Y |  | 5501-01CV0621A-06 | #1 B IDB A oil valve ZF | 0 | 100 | % | %Z081114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01CV0621A-06 | [7 empty] | 5501-01DCS-AMC-02 | SPD03 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 14A | 14B | [9 empty] | 2017.12.11新增
333 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z083114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 14 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
397 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z084114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 14 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
445 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z085114 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD07 | 14 | 4 | 5 | 6 | 1 | 2 | 3 | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
621 | 5501-01CV0516D-07 | 5501 | 5501-01CV0516D-07 | #1 Boiler back wall down layer secondary air inlet motor damper 4 fault #1锅炉后墙下层二次风入口电动调节风门4执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 14 | ADV151-P | SI | N |  | 5501-01CV0516D-07 | #1 B BWDL SAIN MD 4 F |  |  |  | %Z086114 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0516D-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 14A | 14B
221 | %%I5501-01CV0621B-06 | 5501 | 5501-01CV0621B-06 | #1 Boiler In-duct burner B oil supply control valve position #1锅炉风道燃烧器B供油气动调节阀阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 14 | AAI143-H | 4-20mA | Y |  | 5501-01CV0621B-06 | #1 B IDB B oil valve ZF | 0 | 100 | % | %Z091114 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01CV0621B-06 | [7 empty] | 5501-01DCS-AMC-02 | SPD04 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 14A | 14B | [9 empty] | 2017.12.11新增
349 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z093114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 14 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
413 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z094114 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 14 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
461 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 14 | AAI143-H | 4-20mA | N | [6 empty] | %Z095114 |  |  |  | DCS | Y | RTD Surge protective device RTD防雷栅 | Y | RTD Safety barrier RTD安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD08 | 14 | 4 | 5 | 6 | 1 | 2 | 3 | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
573 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 14 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z097114 |  |  |  | DCS | Y | AO Surge protective device AO防雷栅 | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | SPD06 | 14 | 1+ | 2- |  | 3+ | 4- |  | TPB06 | A1BA4D-05 | 14A | 14B
14 | %%I5501-01TE0913A | 5501 | 5501-01TE0913A | #1 Boiler #1 roller slag cooler inlet temperature #1锅炉#1冷渣器进渣温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 15 | AAI143-H | 4-20mA | N |  | 5501-01TE0913A | #1 B #1 RSC IN Temp. | 0 | 1300 | ℃ | %Z011115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01TE0913A | 4w | [6 empty] | 5501-01DCS-AMC-02 | SPD07 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 15A | 15B | [9 empty] | 20190318修改
30 | %%I5501-01TE0913B | 5501 | 5501-01TE0913B | #1 Boiler #2 roller slag cooler inlet temperature #1锅炉#2冷渣器进渣温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 15 | AAI143-H | 4-20mA | N |  | 5501-01TE0913B | #1 B #2 RSC IN Temp. | 0 | 1300 | ℃ | %Z012115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01TE0913B | 4w | [6 empty] | 5501-01DCS-AMC-02 | SPD08 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 15A | 15B | [9 empty] | 20190318修改
46 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 15 | AAI143-H | 4-20mA | Y | [6 empty] | %Z021115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD01 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 15A | 15B | [9 empty] | 2017.12.19删除
110 | %%I5501-01CV0303-06 | 5501 | 5501-01CV0303-06 | #1 Boiler continuous blowdown flash tank electric control valve position #1锅炉汽包连续排污电动调节阀1阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 15 | AAI143-H | 4-20mA | Y |  | 5501-01CV0303-06 | #1B CBF tankECV 1 ZF | 0 | 100 | % | %Z023115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0303-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD02 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 15A | 15B | [9 empty] | 2017.11.23新增
238 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z025115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 15 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
494 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 15 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z027115 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-01 | [8 empty] | TPB05 | A1BA4D-05 | 15A | 15B
62 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 15 | AAI143-H | 4-20mA | Y | [6 empty] | %Z031115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD03 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 15A | 15B | [9 empty] | 2017.12.19删除
126 | %%I5501-01CV0304-06 | 5501 | 5501-01CV0304-06 | #1 Boiler continuous blowdown flash tank electric control valve position #1锅炉汽包连续排污电动调节阀2阀位反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 15 | AAI143-H | 4-20mA | Y |  | 5501-01CV0304-06 | #1B CBF tankECV 2 ZF | 0 | 100 | % | %Z033115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV0304-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD04 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 15A | 15B | [9 empty] | 2017.11.23新增
254 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z035115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 15 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
510 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 15 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z037115 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-01 | [8 empty] | TPB06 | A1BA4D-05 | 15A | 15B
78 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 15 | AAI143-H | 4-20mA | Y | [6 empty] | %Z041115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD07 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 15A | 15B | [9 empty] | 2017.12.19删除
142 | %%I5501-01ST0571A | 5501 | 5501-01ST0571A | #1 Boiler induced draft fan A speed #1锅炉引风机A转速 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 15 | AAI143-H | 4-20mA | Y |  | 5501-01ST0571A | #1 B IDF A speed | 0 | 1500 | rpm | %Z043115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01ST0571A | [7 empty] | 5501-01DCS-AMC-01 | SPD08 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 15A | 15B
270 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z045115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 15 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
526 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 15 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z047115 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-01 | [8 empty] | TPB11 | A1BA4D-05 | 15A | 15B
94 | %%I5501-01TE2101 | 5501 | 5501-01TE2101 | #1 Boiler superheater outlet header steam temperature #1锅炉高过出口集箱蒸汽温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 15 | AAI143-H | 4-20mA | Y |  | 5501-01TE2101 | #1 B SUPER OUT HS Temp. | 0 | 600 | ℃ | %Z051115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01TE2101 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD09 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 15A | 15B | [9 empty] | 20190222删除一分二安全栅
158 | %%I5501-01CV1102-06 | 5501 | 5501-01CV1102-06 | #1 Boiler urea solution outlet electic control valve positon #1锅炉尿素溶液出口电动调节阀位置反馈 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 15 | AAI143-H | 4-20mA | Y |  | 5501-01CV1102-06 | #1 B US OUT ECV ZF | 0 | 100 | % | %Z053115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  | Power Supply 外供电 |  | 5501-01CV1102-06 | 4w | [6 empty] | 5501-01DCS-AMC-01 | SPD10 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 15B | 15A
286 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z055115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 15 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
542 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 15 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z057115 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-01 | [8 empty] | TPB12 | A1BA4D-05 | 15A | 15B
174 | %%I5501-01TE0914A | 5501 | 5501-01TE0914A | #1 Boiler #1 roller slag cooler outlet temperature #1锅炉#1冷渣器出渣温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 15 | AAI143-H | 4-20mA | Y |  | 5501-01TE0914A | #1 B #1 RSC OUT Temp. | 0 | 450 | ℃ | %Z061115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01TE0914A | 4w | [6 empty] | 5501-01DCS-AMC-02 | SPD01 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 15A | 15B | [9 empty] | 20190318修改
302 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z063115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 15 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
366 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z064115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 15 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
558 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 15 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z067115 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | [8 empty] | TPB05 | A1BA4D-05 | 15A | 15B
654 | 5501-01TCH4403 | 5501 | 5501-01TCH4403 | #1 Boiler economizer inlet temperature #1锅炉省煤器入口温度 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 15 | ADV151-P | SI | Y |  | 5501-01TCH4403 | #1 Boiler eco.inlet T |  |  |  | %Z065115 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01TCH4403 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 15A | 15B
190 | %%I5501-01TE0914B | 5501 | 5501-01TE0914B | #1 Boiler #2 roller slag cooler outlet temperature #1锅炉#2冷渣器出渣温度 |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 15 | AAI143-H | 4-20mA | Y |  | 5501-01TE0914B | #1 B #2 RSC OUT Temp. | 0 | 450 | ℃ | %Z071115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI |  |  |  | 5501-01TE0914B | 4w | [6 empty] | 5501-01DCS-AMC-02 | SPD02 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 15A | 15B | [9 empty] | 20190318修改
318 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z073115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 15 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
382 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z074115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 15 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
430 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z075115 |  |  |  | DCS | N |  | N |  | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | [8 empty] | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
590 | 5501-01CV0521A-07 | 5501 | 5501-01CV0521A-07 | #1 Boiler left seal pot fiuidizing air main damper 1 fault #1锅炉左侧回料器流化风电动调节风门1执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 15 | ADV151-P | SI | N |  | 5501-01CV0521A-07 | #1 B L SPFA MD 1 F |  |  |  | %Z076115 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0521A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 15A | 15B
206 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 15 | AAI143-H | 4-20mA | Y | [6 empty] | %Z081115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD03 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 15A | 15B
334 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z083115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 15 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
398 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z084115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 15 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
446 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z085115 |  |  |  | DCS | N |  | N |  | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | [8 empty] | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
622 | 5501-01CV0521B-07 | 5501 | 5501-01CV0521B-07 | #1 Boiler right seal pot fiuidizing air main damper 1 fault #1锅炉右侧回料器流化风电动调节风门1执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 15 | ADV151-P | SI | N |  | 5501-01CV0521B-07 | #1 B R SPFA MD 1 F |  |  |  | %Z086115 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0521B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 15A | 15B
222 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 15 | AAI143-H | 4-20mA | Y | [6 empty] | %Z091115 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD04 | 15 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 15A | 15B
350 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z093115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 15 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
414 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z094115 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 15 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
462 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 15 | AAI143-H | 4-20mA | N | [6 empty] | %Z095115 |  |  |  | DCS | N |  | N |  | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | [8 empty] | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
574 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 15 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z097115 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | [8 empty] | TPB06 | A1BA4D-05 | 15A | 15B
15 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 1 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z011116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD07 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 16A | 16B
31 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 1 | 2 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z012116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD08 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 16A | 16B
47 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 1 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z021116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD01 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 16A | 16B
111 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 3 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z023116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD02 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 16A | 16B
239 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 5 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z025116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD01 | 16 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
495 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 2 | 7 | 16 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z027116 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-01 | [8 empty] | TPB05 | A1BA4D-05 | 16A | 16B
63 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 1 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z031116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD03 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 16A | 16B
127 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 3 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z033116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD04 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 16A | 16B
255 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 5 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z035116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD02 | 16 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
511 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 3 | 7 | 16 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z037116 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-01 | [8 empty] | TPB06 | A1BA4D-05 | 16A | 16B
79 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 1 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z041116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD07 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA07 | A1BA4D-05 | 16A | 16B
143 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 3 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z043116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD08 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA08 | A1BA4D-05 | 16A | 16B
271 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 5 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z045116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD03 | 16 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
527 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 4 | 7 | 16 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z047116 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-01 | [8 empty] | TPB11 | A1BA4D-05 | 16A | 16B
95 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 1 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z051116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD09 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA09 | A1BA4D-05 | 16A | 16B
159 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 3 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z053116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-01 | SPD10 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA10 | A1BA4D-05 | 16A | 16B
287 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 5 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z055116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD04 | 16 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
543 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 5 | 7 | 16 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z057116 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-01 | [8 empty] | TPB12 | A1BA4D-05 | 16A | 16B
175 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 1 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z061116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD01 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA01 | A1BA4D-05 | 16A | 16B
303 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 3 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z063116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD06 | 16 | 4 | 5 |  | 1 | 2 |  | TPB06 | CPY-C3-RAI141 | 3+ | 1-
367 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 4 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z064116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD01 | 16 | 4 | 5 |  | 1 | 2 |  | TPB01 | CPY-C3-RAI141 | 3+ | 1-
559 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 7 | 16 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z067116 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | [8 empty] | TPB05 | A1BA4D-05 | 16A | 16B
655 | 5501-01TCH4404 | 5501 | 5501-01TCH4404 | #1 Boiler water temperature #1锅炉炉水温度 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 16 | ADV151-P | SI | Y |  | 5501-01TCH4404 | #1 Boiler water temp. |  |  |  | %Z065116 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01TCH4404 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 16A | 16B
191 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 1 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z071116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD02 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA02 | A1BA4D-05 | 16A | 16B
319 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 3 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z073116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD07 | 16 | 4 | 5 |  | 1 | 2 |  | TPB07 | CPY-C3-RAI141 | 3+ | 1-
383 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 4 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z074116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD02 | 16 | 4 | 5 |  | 1 | 2 |  | TPB02 | CPY-C3-RAI141 | 3+ | 1-
431 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 5 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z075116 |  |  |  | DCS | N |  | N |  | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | [8 empty] | TPB06 | CPY-C3-RAI141 | 3+ | 1- | 4-
591 | 5501-01CV0522A-07 | 5501 | 5501-01CV0522A-07 | #1 Boiler left seal pot fiuidizing air main damper 2 fault #1锅炉左侧回料器流化风电动调节风门2执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 16 | ADV151-P | SI | N |  | 5501-01CV0522A-07 | #1 B L SPFA MD 2 F |  |  |  | %Z076116 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0522A-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 16A | 16B
207 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 1 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z081116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD03 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA03 | A1BA4D-05 | 16A | 16B
335 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 3 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z083116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD08 | 16 | 4 | 5 |  | 1 | 2 |  | TPB08 | CPY-C3-RAI141 | 3+ | 1-
399 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 4 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z084116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD03 | 16 | 4 | 5 |  | 1 | 2 |  | TPB03 | CPY-C3-RAI141 | 3+ | 1-
447 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 5 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z085116 |  |  |  | DCS | N |  | N |  | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | [8 empty] | TPB07 | CPY-C3-RAI141 | 3+ | 1- | 4-
623 | 5501-01CV0522B-07 | 5501 | 5501-01CV0522B-07 | #1 Boiler right seal pot fiuidizing air main damper 2 fault #1锅炉右侧回料器流化风电动调节风门2执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 16 | ADV151-P | SI | N |  | 5501-01CV0522B-07 | #1 B R SPFA MD 2 F |  |  |  | %Z086116 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0522B-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 16A | 16B
223 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 1 | 16 | AAI143-H | 4-20mA | Y | [6 empty] | %Z091116 |  |  |  | DCS | Y | AI Surge protective device AI防雷栅 | N |  | AI | [11 empty] | 5501-01DCS-AMC-02 | SPD04 | 16 | 1+ | 2- |  | 3+ | 4- |  | TPA04 | A1BA4D-05 | 16A | 16B
351 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 3 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z093116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-01 | SPD09 | 16 | 4 | 5 |  | 1 | 2 |  | TPB09 | CPY-C3-RAI141 | 3+ | 1-
415 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 4 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z094116 |  |  |  | DCS | Y | TC Surge protective device TC防雷栅 | Y | TC Safety barrier TC安全栅 | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | SPD04 | 16 | 4 | 5 |  | 1 | 2 |  | TPB04 | CPY-C3-RAI141 | 3+ | 1-
463 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 5 | 16 | AAI143-H | 4-20mA | N | [6 empty] | %Z095116 |  |  |  | DCS | N |  | N |  | AI |  |  |  |  | 4w | [6 empty] | 5501-01DCS-SBC-02 | [8 empty] | TPB08 | CPY-C3-RAI141 | 3+ | 1- | 4-
575 |  | 5501 |  |  |  | Typ_1 | 5501-01DCS-SYS-01 | FCS0701 | 9 | 7 | 16 | AAI543-H | 4-20mA | Y |  |  |  | 0 | 100 | % | %Z097116 |  |  |  | DCS | N |  | N |  | AO | [11 empty] | 5501-01DCS-AMC-02 | [8 empty] | TPB06 | A1BA4D-05 | 16A | 16B
656 | 5501-01TCH4405 | 5501 | 5501-01TCH4405 | #1 Boiler saturated steam temperature #1锅炉饱和蒸汽温度 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 17 | ADV151-P | SI | Y |  | 5501-01TCH4405 | #1Boiler sa.steam temp. |  |  |  | %Z065117 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01TCH4405 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 17 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 17A | 17B
592 | 5501-01CV0301-07 | 5501 | 5501-01CV0301-07 | #1 Boiler continuous blowdown flash tank electric control valve fault #1锅炉连续排污扩容器电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 17 | ADV151-P | SI | N |  | 5501-01CV0301-07 | #1 B CBF tank EV F |  |  |  | %Z076117 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0301-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 17 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 17A | 17B
624 | 5501-01CV0302-07 | 5501 | 5501-01CV0302-07 | #1 Boiler periodic blowdown header blowdown electric control valve fault #1锅炉定期排污母管集箱排污电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 17 | ADV151-P | SI | N |  | 5501-01CV0302-07 | #1 Boiler PBHB EV F |  |  |  | %Z086117 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0302-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 17 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 17A | 17B
657 | 5501-01TCH4406 | 5501 | 5501-01TCH4406 | #1 Boiler superheated steam temperature #1锅炉过热蒸汽温度 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 18 | ADV151-P | SI | Y |  | 5501-01TCH4406 | #1Boiler su.steam temp. |  |  |  | %Z065118 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01TCH4406 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 18 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 18A | 18B
593 | 5501-01PS2331A | 5501 | 5501-01PS2331A | #1 Boiler slag cooler A water inlet pressure #1锅炉冷渣器A进水压力 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 18 | ADV151-P | SI | N |  | 5501-01PS2331A | #1 B SC A W IN Pre |  |  |  | %Z076118 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01PS2331A | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 18 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 18A | 18B
625 | 5501-01PS2331B | 5501 | 5501-01PS2331B | #1 Boiler slag cooler B water inlet pressure #1锅炉冷渣器B进水压力 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 18 | ADV151-P | SI | N |  | 5501-01PS2331B | #1 B SC B W IN Pre |  |  |  | %Z086118 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01PS2331B | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 18 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 18A | 18B
658 | 5501-01TSH4401 | 5501 | 5501-01TSH4401 | #1 Boiler high temperature sampling rack main pipe of cooling water temperature H #1锅炉高温取样架冷却水母管温度高 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 19 | ADV151-P | SI | Y |  | 5501-01TSH4401 | #1Boiler HTSMP of CW T H |  |  |  | %Z065119 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01TSH4401 | [7 empty] | 5501-01DCS-DMC-01 | SPD01 | 19 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 19A | 19B
594 | 5501-01CV0303-07 | 5501 | 5501-01CV0303-07 | #1 Boiler continuous blowdown flash tank electric control valve fault #1锅炉汽包连续排污电动调节阀1执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 19 | ADV151-P | SI | N |  | 5501-01CV0303-07 | #1B CBF tankECV 1 fault |  |  |  | %Z076119 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0303-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 19 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 19A | 19B | [9 empty] | 2017.11.23新增
626 | 5501-01CV1102-07 | 5501 | 5501-01CV1102-07 | #1 Boiler urea solution outlet electic control valve fault #1锅炉尿素溶液出口电动调节阀执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 19 | ADV151-P | SI | N |  | 5501-01CV1102-07 | #1 B US OUT ECV Fault |  |  |  | %Z086119 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV1102-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 19 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 19A | 19B
659 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 20 | ADV151-P | SI | Y | [6 empty] | %Z065120 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 20 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 20A | 20B
595 | 5501-01E101A001DCS | 5501 | 5501-01E101A001DCS | #1 Boiler slag cooler A water inlet pressure #1锅炉#1冷渣器断水超温报警 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 20 | ADV151-P | SI | N |  | 5501-01E101A001DCS | #1 B SCA water in pre |  |  |  | %Z076120 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01E101A001DCS | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 20 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 20A | 20B | [9 empty] | 20190318新增
627 | 5501-01CV0304-07 | 5501 | 5501-01CV0304-07 | #1 Boiler continuous blowdown flash tank electric control valve fault #1锅炉汽包连续排污电动调节阀2执行机构故障 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 20 | ADV151-P | SI | N |  | 5501-01CV0304-07 | #1B CBF tankECV 2 fault |  |  |  | %Z086120 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01CV0304-07 | [7 empty] | 5501-01DCS-DMC-01 | SPD03 | 20 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 20A | 20B | [9 empty] | 2017.11.23新增
660 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 21 | ADV151-P | SI | Y | [6 empty] | %Z065121 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 21 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 21A | 21B
596 | 5501-01E101B001DCS | 5501 | 5501-01E101B001DCS | #1 Boiler slag cooler B water inlet pressure #1锅炉#2冷渣器断水超温报警 |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 21 | ADV151-P | SI | N |  | 5501-01E101B001DCS | #1 B SCB water in pre |  |  |  | %Z076121 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI |  |  |  | 5501-01E101B001DCS | [7 empty] | 5501-01DCS-DMC-01 | SPD02 | 21 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 21A | 21B | [9 empty] | 20190318新增
628 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 21 | ADV151-P | SI | N | [6 empty] | %Z086121 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 21 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 21A | 21B
661 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 22 | ADV151-P | SI | Y | [6 empty] | %Z065122 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 22 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 22A | 22B
597 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 22 | ADV151-P | SI | N | [6 empty] | %Z076122 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 22 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 22A | 22B
629 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 22 | ADV151-P | SI | N | [6 empty] | %Z086122 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 22 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 22A | 22B
662 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 23 | ADV151-P | SI | Y | [6 empty] | %Z065123 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 23 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 23A | 23B
598 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 23 | ADV151-P | SI | N | [6 empty] | %Z076123 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 23 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 23A | 23B
630 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 23 | ADV151-P | SI | N | [6 empty] | %Z086123 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 23 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 23A | 23B
663 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 24 | ADV151-P | SI | Y | [6 empty] | %Z065124 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 24 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 24A | 24B
599 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 24 | ADV151-P | SI | N | [6 empty] | %Z076124 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 24 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 24A | 24B
631 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 24 | ADV151-P | SI | N | [6 empty] | %Z086124 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 24 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 24A | 24B
664 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 25 | ADV151-P | SI | Y | [6 empty] | %Z065125 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 25 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 25A | 25B
600 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 25 | ADV151-P | SI | N | [6 empty] | %Z076125 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 25 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 25A | 25B
632 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 25 | ADV151-P | SI | N | [6 empty] | %Z086125 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 25 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 25A | 25B
665 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 26 | ADV151-P | SI | Y | [6 empty] | %Z065126 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 26 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 26A | 26B
601 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 26 | ADV151-P | SI | N | [6 empty] | %Z076126 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 26 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 26A | 26B
633 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 26 | ADV151-P | SI | N | [6 empty] | %Z086126 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 26 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 26A | 26B
666 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 27 | ADV151-P | SI | Y | [6 empty] | %Z065127 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 27 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 27A | 27B
602 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 27 | ADV151-P | SI | N | [6 empty] | %Z076127 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 27 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 27A | 27B
634 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 27 | ADV151-P | SI | N | [6 empty] | %Z086127 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 27 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 27A | 27B
667 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 28 | ADV151-P | SI | Y | [6 empty] | %Z065128 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 28 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 28A | 28B
603 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 28 | ADV151-P | SI | N | [6 empty] | %Z076128 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 28 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 28A | 28B
635 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 28 | ADV151-P | SI | N | [6 empty] | %Z086128 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 28 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 28A | 28B
668 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 29 | ADV151-P | SI | Y | [6 empty] | %Z065129 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 29 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 29A | 29B
604 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 29 | ADV151-P | SI | N | [6 empty] | %Z076129 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 29 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 29A | 29B
636 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 29 | ADV151-P | SI | N | [6 empty] | %Z086129 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 29 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 29A | 29B
669 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 30 | ADV151-P | SI | Y | [6 empty] | %Z065130 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 30 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 30A | 30B
605 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 30 | ADV151-P | SI | N | [6 empty] | %Z076130 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 30 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 30A | 30B
637 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 30 | ADV151-P | SI | N | [6 empty] | %Z086130 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 30 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 30A | 30B
670 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 31 | ADV151-P | SI | Y | [6 empty] | %Z065131 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 31 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 31A | 31B
606 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 31 | ADV151-P | SI | N | [6 empty] | %Z076131 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 31 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 31A | 31B
638 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 31 | ADV151-P | SI | N | [6 empty] | %Z086131 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 31 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 31A | 31B
671 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 6 | 5 | 32 | ADV151-P | SI | Y | [6 empty] | %Z065132 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD01 | 32 | 1+ | 2- |  | 3+ | 4- |  | TPD01 | ARM15A-000 | 32A | 32B
607 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 7 | 6 | 32 | ADV151-P | SI | N | [6 empty] | %Z076132 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD02 | 32 | 1+ | 2- |  | 3+ | 4- |  | TPD02 | ARM15A-000 | 32A | 32B
639 |  | 5501 |  |  |  | Typ_2 | 5501-01DCS-SYS-01 | FCS0701 | 8 | 6 | 32 | ADV151-P | SI | N | [6 empty] | %Z086132 |  |  |  | DCS | Y | DI Surge protective device DI防雷栅 | N |  | DI | [11 empty] | 5501-01DCS-DMC-01 | SPD03 | 32 | 1+ | 2- |  | 3+ | 4- |  | TPD03 | ARM15A-000 | 32A | 32B
472
473
474
475
476
477
478
479