## COVER
Tianjin Bohua Development Co., Ltd. 天津渤化发展有限公司
TJBH Petrochemical Project
天津渤化化工项目
LOCATION: 天津
位置: 天津
DCS IO list DCS IO清单
PP装置
Document No: TJBH-YCN-PP-LST-0001
REV | DATE | REASONS FOR ISSUE | BY | CHKD | YKGW APPD
0 | 2019-07-23 | First Issue | 冯超 | 杨忠强 | 张锋

## 使用说明
说明：
1 | 列项颜色说明：
设计提供信息项
横河硬件设计项
横河软件设计项
FAT相关
2
3

## FCS0304_Analog
1 | NO. | AREA | PID_TAG | PIDTAG |  | COMMENT | RANGE | ENG_UNITS | ENG_LO | ENG_HI | Station | NODE | SLOT | Channel | IOMODULE | IO_type | DUPLEX | SIGNAL | FC/FO | DIR_REV | DRWNO | BIDNO | LOOP | TYPNO | Address | DIOTAG | DCSTAG | TGCOMM | ENG_LO | ENG_HI | ENG_UNITS | ALARM_HH | ALARM_HI | ALARM_LO | ALARM_LL | 信号类型 | 安全栅 | remark | signal_origin | FCS_Comp_Name | SB-Surge | SB-Surge Detial | IS_Non_IS | IS_Non_IS Detial | Signal_Location | Signal_Detail | TAG.NO. 1 | 2/3/4 WIRE 2 | J.B.NAME | JB_CABLE_NM | Core.No._Tot | CHANNEL 4 | JB_CABLE_PAIR | MRP_COMP_Name 5 | TS_Name 6 | TS_Channel | TS1 7 | TS2 8 | TS3 9 | TS 10 | TS 11 | TS 12 | SC_Channel | TS 13 | TS 14 | TS 15 | TS 16 | RL_Channel | TS 17 | TS 18 | TS 19 | TS 20 | TB No. 13 | TB Model 14 | TP_TS1 12 | TP_TS2 13 | TP_TS3 14 | Signal | Y_REV_NO | Y_REV_COMMENT | Remarks | 安全栅型号 | 防雷栅 | LOOP NO | DCSTAG2
1 | 1 | 1840 | 18-PT-62302 |  | - | 李强测试 |  |  |  |  | FCS0304 | 1 | 1 | 1 | AAI143-H |  | Y | 4~20mA | [8 empty] | 18-PISA-62302 | 李强测试1 |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-001 | 18-40-001-iSC | [33 empty] | 1840 | PISA
2 | 2 | 1840 | 18-FT-62301 |  | - | LLS TO ET-6203 FLOW | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-FICA-62301 |  |  |  |  | 0 | 0.1 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-001 | 18-40-001-iSC | [33 empty] | 1840 | FICA
3 | 3 | 1840 | 18-FT-62101 |  | - | C3 HCS TO TA-6201 FLOW | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-FIC-62101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-002 | 18-40-002-iSC | [33 empty] | 1840 | FIC
4 | 4 | 1840 | 18-FT-62103 |  | - | C3 HCS TO TA-6201 REFL. FLOW | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-FIC-62103 |  |  |  |  | 0 | 0.1 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-002 | 18-40-002-iSC | [33 empty] | 1840 | FIC
5 | 5 | 1840 | 18-LT-62201 |  | - | VE-6201 LEVEL INDIC., ALA., INTERL. | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-LISA-62201 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-002 | 18-40-002-iSC | [33 empty] | 1840 | LISA
6 | 6 | 1840 | 18-LT-62301 |  | - | VE-6203 LEVEL INDIC., CON. ALA.INTERL. | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-LICSA-62301 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-002 | 18-40-002-iSC | [33 empty] | 1840 | LICSA
7 | 7 | 1840 | 18-TT-62205 |  | - | PR TO PC-6201 TEMP. INDIC., ALA., INTERL. | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-TISA-62205 |  |  |  |  | 0 | 0.2 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-005 | 18-40-005-iSC | [33 empty] | 1840 | TISA
8 | 8 | 1840 | 18-PT-61108 |  | - | LLS TO ET-6101 PRES. INDI., ALA., INTER. | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-PISA-61108 |  |  |  |  | 0 | 0.2 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-005 | 18-40-005-iSC | [33 empty] | 1840 | PISA
9 | 9 | 1840 | 18-FT-61103 |  | - | GC TO TA-6101 FLOW | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-FICA-61103 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-005 | 18-40-005-iSC | [33 empty] | 1840 | FICA
10 | 10 | 1840 | 18-FT-61104 |  | - | LLS TO ET-6101 FLOW | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-FICA-61104 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-005 | 18-40-005-iSC | [33 empty] | 1840 | FICA
11 | 11 | 1840 | 18-LT-61103 |  | - | TA-6101 LEVEL INDIC., CONTR., ALA., INTERL. | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-LICSA-61103 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-005 | 18-40-005-iSC | [33 empty] | 1840 | LICSA
12 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site | [38 empty] | 1830
13 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
14 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
15 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
16 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
17 | 1 | 1840 | 18-PV-62301 |  | - | P TO OSBL PRES. CONTR. | [5 empty] | 1 | 3 | 1 | AAI543-H |  | Y | 4~20mA | [8 empty] | 18-PV-62301 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-008 | 18-40-008-iSC | [33 empty] | 1840 | PV
18 | 2 | 1840 | 18-FXV-61103 |  | - | GC TO TA-6101 FLOW CONTROL | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-FV-61103 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-008 | 18-40-008-iSC | [33 empty] | 1840 | FV
19 | 3 | 1840 | 18-FXV-61104 |  | - | LLS TO ET-6101 FLOW CONTROL | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-FV-61104 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-008 | 18-40-008-iSC | [33 empty] | 1840 | FV
20 | 4 | 1840 | 18-FXV-62101 |  | - | C3 TO TA-6201 FLOW CONTROL | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-FV-62101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-008 | 18-40-008-iSC | [33 empty] | 1840 | FV
21 | 5 | 1840 | 18-FV-62103 |  | - | C3 TO TA-6201 REFLUX FLOW CONTROL | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-FV-62103 | [8 empty] | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-008 | 18-40-008-iSC | [33 empty] | 1840 | FV
22 | 6 | 1840 | 18-FV-62104 |  | - | PROPANE FROM TA-6201 FLOW CONTROL | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-FV-62104 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-008 | 18-40-008-iSC | [33 empty] | 1840 | FV
23 | 7 | 1840 | 18-FV-62105 |  | - | PR TO OSBL TANK FLOW CONTR. | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-FV-62105 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-008 | 18-40-008-iSC | [33 empty] | 1840 | FV
24 | 8 | 1840 | 18-FV-62301 |  | - | LLS TO ET-6203 FLOW CONTROL | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-FV-62301 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-008 | 18-40-008-iSC | [33 empty] | 1840 | FV
25 | 9 | 1840 | 18-TV-62202 |  | - | CWR FROM ET-61202 FOR PR TEMP. CONTR. | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-TV-62202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-017 | 18-40-017-iSC | [33 empty] | 1840 | TV
26 | 10 | 1840 | 18-PXV-61103A |  | 6 | GC TO TA-6101 PRESSURE CONTROL | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-PV-61103A |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-017 | 18-40-017-iSC | [33 empty] | 1840 | PV
27 | 11 | 1840 | 18-PV-63104B |  | 6 | COOL. TO FLARE FOR VE-6303 PESS. CONTR. | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-PV-63104B |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-017 | 18-40-017-iSC | [33 empty] | 1840 | PV
28 | 12 | 1840 | 18-LV-61202 |  | - | COOL. TO ET-6102 LEVEL CONTR. | [7 empty] | 12 |  |  |  | 4~20mA | [8 empty] | 18-LV-61202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-017 | 18-40-017-iSC | [33 empty] | 1840 | LV
29 | 13 | 1840 | 18-LV-61203 |  | - | C2 OFFSPEC TO OSBL FOR VE-6103 LEVEL CONTR. | [7 empty] | 13 |  |  |  | 4~20mA | [8 empty] | 18-LV-61203 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-017 | 18-40-017-iSC | [33 empty] | 1840 | LV
30 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
31 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
32 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
33 | 1 | 1840 | 18-PT-62202 |  | - | PR TO VE-6201 PRES. INDIC., CONTR. ALA., INTERL. | [5 empty] | 2 | 1 | 1 | AAI143-H |  | Y | 4~20mA | [8 empty] | 18-PICSA-62202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-006 | 18-40-006-iSC | [33 empty] | 1840 | PICSA
34 | 2 | 1840 | 18-PDT-62108 |  | - | PR TO ET-3101 PRES.DIFFER. INDIC., ALA., INTERL. | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-PDISA-62108 |  |  |  |  | 0 | 0.8 | 0.05 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-006 | 18-40-006-iSC | [33 empty] | 1840 | PDISA
35 | 3 | 1840 | 18-LT-61203 |  | - | VE-6103 LEVEL INDIC., CONTR., ALA., INTERL. | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-LICSA-61203 |  |  |  |  | 0 | 0.8 | 0.05 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-006 | 18-40-006-iSC | [33 empty] | 1840 | LICSA
36 | 4 | 1840 | 18-LT-62105 |  | - | VE-6202 LEVEL INDIC., CON., ALA., INTERL. | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-LICSA-62105 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-006 | 18-40-006-iSC | [33 empty] | 1840 | LICSA
37 | 5 | 1840 | 18-TT-61207 |  | - | TA-6102 TEMP. INDIC., CONTR., ALARM | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-TICA-61207 |  |  |  |  | 0 | 0.8 | 0.05 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-007 | 18-40-007-iSC | [33 empty] | 1840 | TICA
38 | 6 | 1840 | 18-FT-61201 |  | - | RECO. ETHY. TO TA-6102 FLOW | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-FIC-61201 |  |  |  |  | 0 | 0.8 | 0.05 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-007 | 18-40-007-iSC | [33 empty] | 1840 | FIC
39 | 7 | 1840 | 18-LT-61101 |  | - | 18-VE-6101 | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-LICSA-61101 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-007 | 18-40-007-iSC | [33 empty] | 1840 | LICSA
40 | 8 | 1840 | 18-LT-61205 |  | - | VE-6102 LEVEL INDIC., CONT., ALA., INTERL. | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-LICSA-61205 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-007 | 18-40-007-iSC | [33 empty] | 1840 | LICSA
41 | 9 | 1840 | 18-TT-62202 |  | - | PR TO ET-6201 TEMP. INDIC., CONTR. | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-TIC-62202 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-010 | 18-40-010-iSC | [33 empty] | 1840 | TIC
42 | 10 | 1840 | 18-PT-61210 |  | - | COOL. FROM ET-6104 PRES. INDIC., CONTR. | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-PIC-61210 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-010 | 18-40-010-iSC | [33 empty] | 1840 | PIC
43 | 11 | 1840 | 18-LT-61201 |  | - | ET-6104 LEVEL INDIC., CONTR., ALA. | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-LICA-61201 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-010 | 18-40-010-iSC | [33 empty] | 1840 | LICA
44 | 12 | 1840 | 18-LT-62101 |  | - | TA-6201 LEVEL INDIC., CON., ALA., INTERL. | [7 empty] | 12 |  |  |  | 4~20mA | [8 empty] | 18-LICSA-62101 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-010 | 18-40-010-iSC | [33 empty] | 1840 | LICSA
45 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
46 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
47 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
48 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
49 | 1 | 1840 | 18-PV-61103B |  | 6 | CWS FOR TA-6101 PRES. CONTROL | [5 empty] | 2 | 3 | 1 | AAI543-H |  | Y | 4~20mA | [8 empty] | 18-PV-61103B |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-012 | 18-40-012-iSC | [33 empty] | 1840 | PV
50 | 2 | 1840 | 18-PV-61109 |  | - | GC TO FLARE FOR GC TO ET-6106 PRES. CONTR. | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-PV-61109 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-012 | 18-40-012-iSC | [33 empty] | 1840 | PV
51 | 3 | 1840 | 18-PV-61202 |  | - | COOL. FROM ET-6102 FOR PRES. CONTR. | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-PV-61202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-012 | 18-40-012-iSC | [33 empty] | 1840 | PV
52 | 4 | 1840 | 18-PV-61204 |  | - | HCS TO ET-6105 FOR ET-6102 PRES. CONTR. | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-PV-61204 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-012 | 18-40-012-iSC | [33 empty] | 1840 | PV
53 | 5 | 1840 | 18-PV-61210 |  | - | COOL. FROM ET-6104 FOR ET-6104 PRES. CONTR. | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-PV-61210 | [8 empty] | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-012 | 18-40-012-iSC | [33 empty] | 1840 | PV
54 | 6 | 1840 | 18-PV-62104 |  | - | PRE TO FLARE FOR VE-6202 PRES. CONTR. | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-PV-62104 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-012 | 18-40-012-iSC | [33 empty] | 1840 | PV
55 | 7 | 1840 | 18-PV-63104A |  | 6 | COOL. TO VE-6303 FOR PESS. CONTR. | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-PV-63104A |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-012 | 18-40-012-iSC | [33 empty] | 1840 | PV
56 | 8 | 1840 | 18-FV-61201 |  | - | RECOV. ETHY. TO TA-6102 FLOW CONTROL | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-FV-61201 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-012 | 18-40-012-iSC | [33 empty] | 1840 | FV
57 | 9 | 1840 | 18-FV-61202 |  | - | HCS TO TA-6101 REFLUX FLOW CONTROL | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-FV-61202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-012 | 18-40-012-iSC | [33 empty] | 1840 | FV
58 | 10 | 1840 | 18-LV-61201 |  | - | COOL. TO ET-6104 LEVEL CONTROL | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-LV-61201 | [8 empty] | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-012 | 18-40-012-iSC | [33 empty] | 1840 | LV
59 | 11 |  |  |  |  | Spare | [7 empty] | 11 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
60 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
61 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
62 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
63 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
64 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
65 | 1 | 1840 | 18-PT-61109 |  | - | GC TO TA-6106 PRES. INDIC., CONTR., ALA. | [5 empty] | 3 | 1 | 1 | AAI143-H |  | Y | 4~20mA | [8 empty] | 18-PICA-61109 |  |  |  |  | 0 | 95 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-011 | 18-40-011-iSC | [33 empty] | 1840 | PICA
66 | 2 | 1840 | 18-PT-61202 |  | - | COOL. FROM ET-6102 PRES. INDIC., CONTR. | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-PIC-61202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-011 | 18-40-011-iSC | [33 empty] | 1840 | PIC
67 | 3 | 1840 | 18-PT-61204 |  | - | GC ENDS TO ET-6105 PRES. INDIC., CONTR. | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-PIC-61204 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-011 | 18-40-011-iSC | [33 empty] | 1840 | PIC
68 | 4 | 1840 | 18-PT-62104 |  | - | VE-6202 TOP PRES. INDIC., CONTR., ALA. | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-PICA-62104 |  |  |  |  | 0 | 2720 | 680 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-011 | 18-40-011-iSC | [33 empty] | 1840 | PICA
69 | 5 | 1840 | 18-FT-61202 |  | - | HCS TO TA-6101 FLOW | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-FIC-61202 |  |  |  |  | 0 | 2720 | 680 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-011 | 18-40-011-iSC | [33 empty] | 1840 | FIC
70 | 6 | 1840 | 18-TT-61105 |  | - | TA-6101 TEMP. INDIC., CONTR. | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-TIC-61105 |  |  |  |  | 0 | 2400 | 600 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-015 | 18-40-015-iSC | [33 empty] | 1840 | TIC
71 | 7 | 1840 | 18-PT-61103 |  | - | GC TO TA-6101 PRES. INDIC., CONTR., ALA. | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-PICA-61103 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-015 | 18-40-015-iSC | [33 empty] | 1840 | PICA
72 | 8 | 1840 | 18-PT-63104 |  | - | VE-6303 PRES. INDIC., CONTR. ALA. | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-PICA-63104 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-016 | 18-40-016-iSC | [33 empty] | 1840 | PICA
73 | 9 | 1840 | 18-LT-61202 |  | - | ET-6102 LEVEL INDIC., CONTR., ALA. | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-LICA-61202 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-016 | 18-40-016-iSC | [33 empty] | 1840 | LICA
74 | 10 | 1840 | 18-PT-62301 |  | - | VE-6203 TO P PRES. INDIC.,CONTR. ALA. | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-PICSA-62301 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  |  | 无电缆信息 | [33 empty] | 1840 | PICSA
75 | 11 | 1830 | 18-LT-66101 |  | - | 18-VE-6601X | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-LISA-66101 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-6601-DJB-0003 | DCS | [33 empty] | 1830 | LISA
76 | 12 | 1830 | 18-LT-23103 |  | - | 18-PA-2301 | [7 empty] | 12 |  |  |  | 4~20mA | [8 empty] | 18-LISA-23103 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-PA2301-DJB-0001 | DCS | [33 empty] | 1830 | LISA
77 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
78 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
79 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
80 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
81 | 1 | 1812 | 18-PV-17106A |  | 1 | LP NITROGEN TO VE-1701 | [5 empty] | 3 | 3 | 1 | AAI543-H |  | Y | 4~20mA | [8 empty] | 18-PV-17106A |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-001 | 18-12-001-iSC | [33 empty] | 1812 | PV
82 | 2 | 1812 | 18-PV-17106B |  | 1 | LP NITROGEN TO VE-1702 | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-PV-17106B |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-001 | 18-12-001-iSC | [33 empty] | 1812 | PV
83 | 3 | 1812 | 18-PV-17301 |  | - | White Oil return to VE-1701 | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-PV-17301 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-001 | 18-12-001-iSC | [33 empty] | 1812 | PV
84 | 4 | 1812 | 18-PV-17302A |  | 1 | LP NITROGEN TO VE-1703 | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-PV-17302A |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-001 | 18-12-001-iSC | [33 empty] | 1812 | PV
85 | 5 | 1812 | 18-PV-17302B |  | 1 | NITROGEN/White Oil TO FLARE | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-PV-17302B |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-001 | 18-12-001-iSC | [33 empty] | 1812 | PV
86 | 6 | 1812 | 18-FI-17105B |  | 1 | ISOPROPANOL TO VE-1705 | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-FI-17105B |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-007 | 18-12-007-iSC | [33 empty] | 1812 | FI
87 | 7 | 1812 | 18-LI-17102 |  | - | VE-1701 | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-LI-17102 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-007 | 18-12-007-iSC | [33 empty] | 1812 | LI
88 | 8 | 1812 | 18-LI-17103 |  | - | VE-1702 | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-LI-17103 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-007 | 18-12-007-iSC | [33 empty] | 1812 | LI
89 | 9 | 1812 | 18-LI-17104B |  | 1 | VE-1702 | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-LI-17104B | [8 empty] | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-007 | 18-12-007-iSC | [33 empty] | 1812 | LI
90 | 10 | 1830 | 18-TI-21101 |  | - | PEROXIDE DOSING ROOM | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-TI-21101 | [8 empty] | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-021 | 18-30-021-iSC | [33 empty] | 1830 | TI
91 | 11 | 1830 | 18-LI-21101 |  | - | 18-VE-2101 | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-LI-21101 | [8 empty] | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-021 | 18-30-021-iSC | [33 empty] | 1830 | LI
92 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
93 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
94 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
95 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
96 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
97 | 1 | 1812 | 18-TT-17104 |  | - | VE-1705 | [5 empty] | 4 | 1 | 1 | AAI143-H |  | Y | 4~20mA | [8 empty] | 18-TISA-17104 |  |  |  |  | 105 | 100 | 80 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-002 | 18-12-002-iSC | [33 empty] | 1812 | TISA
98 | 2 | 1812 | 18-LT-17104 |  | - | VE-1705 | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-LISA-17104 |  |  |  |  | 95 | 85 | 60 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-002 | 18-12-002-iSC | [33 empty] | 1812 | LISA
99 | 3 | 1812 | 18-LT-17109 |  | - | PA-1705 | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-LISA-17109 |  |  |  |  | 0 | 65 | 50 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-002 | 18-12-002-iSC | [33 empty] | 1812 | LISA
100 | 4 | 1812 | 18-LT-17301 |  | - | VE-1703 | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-LISA-17301 |  |  |  |  | 110 | 105 | 85 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-002 | 18-12-002-iSC | [33 empty] | 1812 | LISA
101 | 5 | 1812 | 18-PT-17106 |  | - | LP NITROGEN TO VE-1701 / VE-1702 | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-PICSA-17106 |  |  |  |  | 105 | 100 | 80 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-003 | 18-12-003-iSC | [33 empty] | 1812 | PICSA
102 | 6 | 1812 | 18-PT-17301 |  | - | PP-1704 DISCHARGE | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-PIC-17301 |  |  |  |  | 95 | 85 | 60 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-003 | 18-12-003-iSC | [33 empty] | 1812 | PIC
103 | 7 | 1812 | 18-PT-17302 |  | - | LP NITROGEN/WHITE OIL TO FLARE | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-PICA-17302 |  |  |  |  | 0 | 65 | 50 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-003 | 18-12-003-iSC | [33 empty] | 1812 | PICA
104 | 8 | 1812 | 18-FT-17108 |  | - | NITROGEN TO TEA CONTAINER | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-FQISA-17108 |  |  |  |  | 110 | 105 | 85 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-003 | 18-12-003-iSC | [33 empty] | 1812 | FQISA
105 | 9 | 1812 | 18-LT-17101 |  | - | VE-1701 | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-LISA-17101 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-003 | 18-12-003-iSC | [33 empty] | 1812 | LISA
106 | 10 | 1812 | 18-LT-17102 |  | - | VE-1701 | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-LISA-17102 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-003 | 18-12-003-iSC | [33 empty] | 1812 | LISA
107 | 11 | 1812 | 18-LT-17103 |  | - | VE-1702 | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-LISA-17103 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-003 | 18-12-003-iSC | [33 empty] | 1812 | LISA
108 | 12 | 1830 | 18-PI-35204 |  | - | 输送氮气出口冷却器EM-3502X出口压力显示 | [7 empty] | 12 |  |  |  | 4~20mA | [8 empty] | 18-PI-35204 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  |  | 无电缆信息 | [33 empty] | 1830 | PI
109 | 13 | 1830 | 18-PI-35205 |  | - | 输送氮气风机入口压力显示 | [7 empty] | 13 |  |  |  | 4~20mA | [8 empty] | 18-PI-35205 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  |  | 无电缆信息 | [33 empty] | 1830 | PI
110 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
111 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
112 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
113 | 1 | 1830 | 18-PV-24101A |  | 2 | LP NITROGEN TO VE-2401 | [5 empty] | 4 | 3 | 1 | AAI543-H |  | Y | 4~20mA | [8 empty] | 18-PV-24101A |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-001 | 18-30-001-iSC | [33 empty] | 1830 | PV
114 | 2 | 1830 | 18-PV-24101B |  | 2 | LP NITROGEN LIQUID ADDITIVE DRUM | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-PV-24101B |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-001 | 18-30-001-iSC | [33 empty] | 1830 | PV
115 | 3 | 1830 | 18-FV-36103 |  | - | DEMINERALIZED WATER FROM HEADER TO UP-3601 | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-FV-36103 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-001 | 18-30-001-iSC | [33 empty] | 1830 | FV
116 | 4 | 1830 | 18-LV-66202 |  | - | WASTE WATER TO VP-9201 | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-LV-66202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-001 | 18-30-001-iSC | [33 empty] | 1830 | LV
117 | 5 | 1830 | 18-HV-36105 |  | - | PEROXIDE FROM PP-2101 TO UP-3601 | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-HIC-36105 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-001 | 18-30-001-iSC | [33 empty] | 1830 | HIC
118 | 6 | 1830 | 18-PV-21110 |  | - | PEROXIDE TO VE-2101 | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-PV-21110 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-012 | 18-30-012-iSC | [33 empty] | 1830 | PV
119 | 7 | 1830 | 18-FV-21103A |  | 2 | PEROXIDE TO UP-3601 | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-FV-21103A |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-012 | 18-30-012-iSC | [33 empty] | 1830 | FV
120 | 8 | 1830 | 18-FV-21103B |  | 2 | PEROXIDE TO UP-3601 | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-FV-21103B |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-012 | 18-30-012-iSC | [33 empty] | 1830 | FV
121 | 9 | 1830 | 18-PV-23101A |  | 2 | LP NITROGEN TO VE-2301 | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-PV-23101A |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-014 | 18-30-014-iSC | [33 empty] | 1830 | PV
122 | 10 | 1830 | 18-PV-23101B |  | 2 | NITROGEN TO ATM. | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-PV-23101B |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-014 | 18-30-014-iSC | [33 empty] | 1830 | PV
123 | 11 | 1830 | 18-PV-66102 |  | - | VACUMM OFFGAS TO OSBL | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-PV-66102 | [8 empty] | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-014 | 18-30-014-iSC | [33 empty] | 1830 | PV
124 | 12 | 1830 | 18-HV-66102 |  | - | OFFGAS TO ATM AT SAFE LOCATION | [7 empty] | 12 |  |  |  | 4~20mA | [8 empty] | 18-HIC-66102 | [8 empty] | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-014 | 18-30-014-iSC | [33 empty] | 1830 | HIC
125 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
126 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
127 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
128 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
129 | 1 | 1830 | 18-TT-21102 |  | - | PEROXIDE FROM PP-2101 | [5 empty] | 5 | 1 | 1 | AAI143-H |  | Y | 4~20mA | [8 empty] | 18-TISA-21102 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-005 | 18-30-005-iSC | [33 empty] | 1830 | TISA
130 | 2 | 1830 | 18-TT-21104 |  | - | VE-2101 | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-TISA-21104 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-005 | 18-30-005-iSC | [33 empty] | 1830 | TISA
131 | 3 | 1830 | 18-PT-21103 |  | - | PEROXIDE FROM PP-2102 | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-PISA-21103 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-005 | 18-30-005-iSC | [33 empty] | 1830 | PISA
132 | 4 | 1830 | 18-PT-21105 |  | - | PEROXIDE FROM PP-2101 | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-PISA-21105 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-005 | 18-30-005-iSC | [33 empty] | 1830 | PISA
133 | 5 | 1830 | 18-PT-21108 |  | - | PEROXIDE FROM PP-2101 | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-PISA-21108 |  |  |  |  | 0 | 0.8 | 0.05 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-005 | 18-30-005-iSC | [33 empty] | 1830 | PISA
134 | 6 | 1830 | 18-PT-21110 |  | - | PEROXIDE FROM PP-2101 | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-PICSA-21110 |  |  |  |  | 0 | 0.8 | 0.05 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-005 | 18-30-005-iSC | [33 empty] | 1830 | PICSA
135 | 7 | 1830 | 18-LT-66202 |  | - | 18-VE-6602 | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-LICA-66202 |  |  |  |  | 0 | 0.8 | 0.05 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-006 | 18-30-006-iSC | [33 empty] | 1830 | LICA
136 | 8 | 1830 | 18-FT-21102 |  | - | LP NITROGEN TO VE-2101 | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-FISA-21102 |  |  |  |  | 0 | 0.8 | 0.05 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-007 | 18-30-007-iSC | [33 empty] | 1830 | FISA
137 | 9 | 1830 | 18-FT-21109 |  | - | LP NITROGEN TO PEROXIDE DRUM | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-FISA-21109 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-007 | 18-30-007-iSC | [33 empty] | 1830 | FISA
138 | 10 | 1830 | 18-LT-21101 |  | - | 18-VE-2101 | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-LISA-21101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-007 | 18-30-007-iSC | [33 empty] | 1830 | LISA
139 | 11 | 1830 | 18-LT-92101 |  | - | VP-9201 SURFACE WATER COLLECTION | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-LISA-92101 |  |  |  |  | 0 | 0.4 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-007 | 18-30-007-iSC | [33 empty] | 1830 | LISA
140 | 12 | 1830 | 18-PIA-35108 |  | - | UP-3501系统循环线输送压力显示 | [7 empty] | 12 |  |  |  | 4~20mA | [8 empty] | 18-PI-35108 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0017 | DCS | [33 empty] | 1830 | PI
141 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
142 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
143 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
144 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
145 | 1 | 1830 | 18-PY-35201 |  | - | 输送氮气风机入口排气调节阀定位器 | [5 empty] | 5 | 3 | 1 | AAI543-H |  | Y | 4~20mA | [8 empty] | 18-PY-35201 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0010 | DCS | [33 empty] | 1830 | PY
146 | 2 | 1830 | 18-PY-35205 |  | - | 输送氮气风机入口补气调节阀定位器 | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-PY-35205 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0010 | DCS | [33 empty] | 1830 | PY
147 | 3 | 1830 | 18-FI-35201 |  | - | 输送氮气风机入口补气流量显示 | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-FI-35201 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0009 | DCS | [33 empty] | 1830 | FI
148 | 4 | 1830 | 18-PV-66101 |  | - | By-pass pressure control valve | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-PV-66101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-6601-DJB-0003 | DCS | [33 empty] | 1830 | PV
149 | 5 | 1830 | 18-LI-23101 |  | - | 18-VE-2301 | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-LI-23101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 单拉 | 18-30-024-SC | [33 empty] | 1830 | LI
150 | 6 | 1830 | 18-LI-24101 |  | - | 18-VE-2401 | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-LI-24101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 单拉 | 18-30-024-SC | [33 empty] | 1830 | LI
151 | 7 |  |  |  |  | Spare | [7 empty] | 7 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
152 | 8 |  |  |  |  | Spare | [7 empty] | 8 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
153 | 9 |  |  |  |  | Spare | [7 empty] | 9 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
154 | 10 |  |  |  |  | Spare | [7 empty] | 10 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
155 | 11 |  |  |  |  | Spare | [7 empty] | 11 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
156 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
157 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
158 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
159 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
160 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
161 | 1 | 1830 | 18-PT-24101 |  | - | NITROGEN TO VE-2401 | [5 empty] | 6 | 1 | 1 | AAI143-H |  | Y | 4~20mA | [8 empty] | 18-PICA-24101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-010 | 18-30-010-iSC | [33 empty] | 1830 | PICA
162 | 2 | 1830 | 18-LT-23101 |  | - | 18-VE-2301 | [7 empty] | 2 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-LISA-23101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-010 | 18-30-010-iSC | [33 empty] | 1830 | LISA
163 | 3 | 1830 | 18-LT-23102 |  | - | 18-VE-2302 | [7 empty] | 3 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-LISA-23102 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-010 | 18-30-010-iSC | [33 empty] | 1830 | LISA
164 | 4 | 1830 | 18-LT-24101 |  | - | 18-VE-2401 | [7 empty] | 4 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-LISA-24101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-010 | 18-30-010-iSC | [33 empty] | 1830 | LISA
165 | 5 | 1830 | 18-PT-23101 |  | - | LP NITROGEN TO VE-2301 | [7 empty] | 5 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-PICA-23101 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-015 | 18-30-015-iSC | [33 empty] | 1830 | PICA
166 | 6 | 1830 | 18-PT-66101 |  | - | OFFGAS TO ET-6602 | [7 empty] | 6 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-PICA-66101 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-015 | 18-30-015-iSC | [33 empty] | 1830 | PICA
167 | 7 | 1830 | 18-PT-66102 |  | - | OFFGAS TO ATM AT SAFE LOCATION | [7 empty] | 7 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-PICA-66102 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-015 | 18-30-015-iSC | [33 empty] | 1830 | PICA
168 | 8 | 1830 | 18-PI-35201A |  | 3 | 风机18-PB-3501AX入口压力显示 | [7 empty] | 8 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-PI-35201A | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0009 | DCS | [33 empty] | 1830 | PI
169 | 9 | 1830 | 18-PI-35201B |  | 3 | 风机18-PB-3501AX入口压力显示 | [7 empty] | 9 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-PI-35201B | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0009 | DCS | [33 empty] | 1830 | PI
170 | 10 | 1830 | 18-PI-35211A |  | 3 | 风机18-PB-3501BX入口压力显示 | [7 empty] | 10 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-PI-35211A | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0009 | DCS | [33 empty] | 1830 | PI
171 | 11 | 1830 | 18-PI-35211B |  | 3 | 风机18-PB-3501BX入口压力显示 | [7 empty] | 11 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-PI-35211B | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0009 | DCS | [33 empty] | 1830 | PI
172 | 12 | 1830 | 18-TI-35201 |  | - | 输送氮气风机出口温度显示 | [7 empty] | 12 | AAI143-H |  |  | 4~20mA | [8 empty] | 18-TI-35201 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0009 | DCS | [33 empty] | 1830 | TI
173 | 13 |  |  |  |  | Spare | [7 empty] | 13 | AAI143-H |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
174 | 14 |  |  |  |  | Spare | [7 empty] | 14 | AAI143-H |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
175 | 15 |  |  |  |  | Spare | [7 empty] | 15 | AAI143-H |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
176 | 16 |  |  |  |  | Spare | [7 empty] | 16 | AAI143-H |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
177 | 1 | 1812 | 18-SC-17201 |  | - | PP-1701A SPEED CONTROL | [5 empty] | 6 | 3 | 1 | AAI543-H |  | Y | 4~20mA | [8 empty] | 18-SC-17201 | [8 empty] | DCS-AO | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1812 | SC
178 | 2 | 1812 | 18-SC-17202 |  | - | PP-1701B SPEED CONTROL | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-SC-17202 | [8 empty] | DCS-AO | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1812 | SC
179 | 3 | 1812 | 18-SC-17203 |  | - | PP-1702A SPEED CONTROL | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-SC-17203 |  |  |  |  | 0 | 0.05 | 0 | 0 | DCS-AO | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1812 | SC
180 | 4 | 1812 | 18-SC-17204 |  | - | PP-1702B SPEED CONTROL | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-SC-17204 |  |  |  |  | 0 | 0.05 | 0 | 0 | DCS-AO | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1812 | SC
181 | 5 | 1812 | 18-SC-17301 |  | - | PP-1704 SPEED CONTROL | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-SC-17301 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1812 | SC
182 | 6 |  |  |  |  | Spare | [7 empty] | 6 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
183 | 7 |  |  |  |  | Spare | [7 empty] | 7 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
184 | 8 |  |  |  |  | Spare | [7 empty] | 8 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
185 | 9 |  |  |  |  | Spare | [7 empty] | 9 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
186 | 10 |  |  |  |  | Spare | [7 empty] | 10 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
187 | 11 |  |  |  |  | Spare | [7 empty] | 11 |  |  |  | 4-20mA | [13 empty] | 0 | 1.2 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
188 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [13 empty] | 0 | 1.2 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
189 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
190 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
191 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
192 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
193 | 1 | 1840 | 18-FT-62104 |  | - | P TO VE-6203 FLOW | [5 empty] | 7 | 1 | 1 | AAI143-H |  | Y | 4~20mA | [8 empty] | 18-FICQA-62104 |  |  |  |  | 0 | 0.05 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 18-EJB-40-003 | 18-40-003-SC | [33 empty] | 1840 | FICQA
194 | 2 | 1840 | 18-FT-62105 |  | - | PR TO ET-3101 FLOW | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-FICQ-62105 |  |  |  |  | 0 | 0.05 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 18-EJB-40-003 | 18-40-003-SC | [33 empty] | 1840 | FICQ
195 | 3 | 1830 | 18-FT-21103 |  | - | PEROXIDE TO PJ-3601X | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-FICSA-21103 |  |  |  |  | 0 | 0.6 | 0.4 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 单拉 | 单拉 | [33 empty] | 1830 | FICSA
196 | 4 | 1830 | 18-FT-23101 |  | - | MELTABLE ADDITIVES TO PJ-3601X | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-FICA-23101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 18-EJB-30-009 | 18-30-009-EC | [33 empty] | 1830 | FICA
197 | 5 | 1830 | 18-FT-24101 |  | - | LIQUID ADDITIVES TO PJ-3601X | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-FICA-24101 |  |  |  |  | 0 | 7600 | 1900 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 18-EJB-30-009 | 18-30-009-EC | [33 empty] | 1830 | FICA
198 | 6 | 1830 | 18-FT-36103 |  | - | DEMIN. WATER TO PJ-3601X | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-FICSA-36103 |  |  |  |  | 0 | 7600 | 1900 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 18-EJB-30-009 | 18-30-009-EC | [33 empty] | 1830 | FICSA
199 | 7 | 1830 | 18-AT-66101 |  | - | O2 IN OFFGAS FROM UP-6601 | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-AISA-66101 |  |  |  |  | 0 | 7600 | 1900 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 220VAC |  |  | 单拉 | 18-30-024-SC | [33 empty] | 1830 | AISA
200 | 8 | 1830 | 18-AI-35201 |  | - | 输送氮气风机入口烃含量显示 | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-AI-35201 |  |  |  |  | 0 | 7600 | 1900 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 220VAC |  |  | 单拉 | SIS | [33 empty] | 1830 | AI
201 | 9 | 1830 | 18-AI-35202 |  | - | 输送氮气风机入口氧含量显示 | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-AI-35202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 220VAC |  |  |  | 无电缆信息 | [33 empty] | 1830 | AI
202 | 10 |  |  |  |  | Spare | [7 empty] | 10 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
203 | 11 |  |  |  |  | Spare | [7 empty] | 11 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
204 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
205 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
206 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
207 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
208 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
209 | 1 | 1830 | 18-SC-23101 |  | - | 18-PP-2301A CONTROL | [5 empty] | 7 | 3 | 1 | AAI543-H |  | Y | 4~20mA | [8 empty] | 18-SC-23101 |  |  |  |  | 0 | 100 | 60 | 0 | DCS-AO | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1830 | SC
210 | 2 | 1830 | 18-SC-23102 |  | - | 18-PP-2301B SPEED CONTROL | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-SC-23102 |  |  |  |  | 0 | 100 | 60 | 0 | DCS-AO | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1830 | SC
211 | 3 | 1830 | 18-SC-23105 |  | - | 18-PA-2301 SPEED CONTROL | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-SC-23105 |  |  |  |  | 0 | 0 | 0.55 | 0 | DCS-AO | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1830 | SC
212 | 4 | 1830 | 18-SC-24101 |  | - | 18-PP-2401 SPEED CONTROL | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-SC-24101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1830 | SC
213 | 5 | 1830 | 18-SC-35101 |  | - | 粉料仓旋转阀18-PF-3501X的速度控制 | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-SC-35101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AO | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1830 | SC
214 | 6 |  |  |  |  | Spare | [7 empty] | 6 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
215 | 7 |  |  |  |  | Spare | [7 empty] | 7 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
216 | 8 |  |  |  |  | Spare | [7 empty] | 8 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | NIS |  | DCS | [5 empty] | Site
217 | 9 |  |  |  |  | Spare | [7 empty] | 9 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
218 | 10 |  |  |  |  | Spare | [7 empty] | 10 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
219 | 11 |  |  |  |  | Spare | [7 empty] | 11 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
220 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
221 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
222 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
223 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
224 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
225 | 1 | 1840 | 18-TT-62302 |  | - | P FROM VE-6203 TEMP. INDIC. | [5 empty] | 8 | 1 | 1 | AAI143-H |  | N | 4~20mA | [8 empty] | 18-TI-62302 |  |  |  |  | 0 | 4.5 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-001 | 18-40-001-iSC | [33 empty] | 1840 | TI
226 | 2 | 1840 | 18-PT-62303 |  | - | P TO POSM PRES. INDIC. | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-PI-62303 |  |  |  |  | 0 | 80 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-001 | 18-40-001-iSC | [33 empty] | 1840 | PI
227 | 3 | 1840 | 18-PT-61281A |  | - | 18-PP-6102A | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-PIA-61281A |  |  |  |  | 0 | 120 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-001 | 18-40-001-iSC | [33 empty] | 1840 | PIA
228 | 4 | 1840 | 18-PT-61281B |  | - | 18-PP-6102B | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-PIA-61281B |  |  |  |  | 0 | 4.5 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-001 | 18-40-001-iSC | [33 empty] | 1840 | PIA
229 | 5 | 1840 | 18-PT-61283 |  | - | 18-PP-6103 | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-PIA-61283 |  |  |  |  | 0 | 0 | 5 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-001 | 18-40-001-iSC | [33 empty] | 1840 | PIA
230 | 6 | 1840 | 18-PT-62181A |  | - | 18-PP-6202A | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-PIA-62181A |  |  |  |  | 0 | 75000 | 50000 | 45000 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-001 | 18-40-001-iSC | [33 empty] | 1840 | PIA
231 | 7 | 1840 | 18-PT-62181B |  | - | 18-PP-6202B | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-PIA-62181B |  |  |  |  | 0 | 8500 | 6500 | 6000 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-001 | 18-40-001-iSC | [33 empty] | 1840 | PIA
232 | 8 | 1840 | 18-TT-61110 |  | - | HCS FROM TA-6101 BOTTOM TEMP. INDIC. | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-TI-61110 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-002 | 18-40-002-iSC | [33 empty] | 1840 | TI
233 | 9 | 1840 | 18-TT-62301 |  | - | VE-6203 TEMP. INDIC. | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-TI-62301 |  |  |  |  | 0 | 6 | 3 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-002 | 18-40-002-iSC | [33 empty] | 1840 | TI
234 | 10 | 1840 | 18-TT-61102 |  | - | GC TO TA-6101 TEMP. INDIC. | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-TI-61102 |  |  |  |  | 0 | 98 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-005 | 18-40-005-iSC | [33 empty] | 1840 | TI
235 | 11 | 1840 | 18-TT-61109 |  | - | GC FROM ET-6101 TEMP. INDIC. | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-TI-61109 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-005 | 18-40-005-iSC | [33 empty] | 1840 | TI
236 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
237 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
238 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
239 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
240 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
241 | 1 | 1840 | 18-TT-61203 |  | - | ETH TO VE-6103 TEMP. INDIC. | [5 empty] | 8 | 2 | 1 | AAI143-H |  | N | 4~20mA | [8 empty] | 18-TI-61203 |  |  |  |  | 30 | 25 | 0 | 0 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  | 18-IJB-40-006 | 18-40-006-iSC | [33 empty] | 1840 | TI
242 | 2 | 1840 | 18-TT-62107 |  | - | PR TO VE-6202 TEMP. INDIC. | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-TI-62107 |  |  |  |  | 0 | 40 | 0.5 | 0 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  | 18-IJB-40-006 | 18-40-006-iSC | [33 empty] | 1840 | TI
243 | 3 | 1840 | 18-TT-62108 |  | - | P TO VE-6203 TEMP. INDIC. | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-TI-62108 |  |  |  |  | 25 | 22 | -5 | -10 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  | 18-IJB-40-006 | 18-40-006-iSC | [33 empty] | 1840 | TI
244 | 4 | 1840 | 18-TT-62203 |  | - | PR TO VE-6201 TEMP. INDIC. | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-TI-62203 |  |  |  |  | 0 | 40 | 0.5 | 0 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  | 18-IJB-40-006 | 18-40-006-iSC | [33 empty] | 1840 | TI
245 | 5 | 1840 | 18-FT-62201 |  | - | PR TO PC-6201 FLOW INDICA. | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-FI-62201 |  |  |  |  | 30 | 25 | 0 | 0 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  | 18-IJB-40-006 | 18-40-006-iSC | [33 empty] | 1840 | FI
246 | 6 | 1840 | 18-LT-63103 |  | - | VE-6303 LEVEL INDIC., ALAR. | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-LIA-63103 |  |  |  |  | 0 | 60 | 45 | 0 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  | 18-IJB-40-006 | 18-40-006-iSC | [33 empty] | 1840 | LIA
247 | 7 | 1840 | 18-TT-61205 |  | - | TA-6102 TEMP. INDIC. | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-TI-61205 |  |  |  |  | 0 | 100 | 50 | 0 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  | 18-IJB-40-007 | 18-40-007-iSC | [33 empty] | 1840 | TI
248 | 8 | 1840 | 18-TT-61206 |  | - | TA-6102 TEMP. INDIC. | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-TI-61206 |  |  |  |  | 0 | 15 | 0 | 0 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  | 18-IJB-40-007 | 18-40-007-iSC | [33 empty] | 1840 | TI
249 | 9 | 1840 | 18-TT-63101 |  | - | COOL. TO ET-6301 TEMP. INDIC., ALARM | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-TIA-63101 |  |  |  |  | 0 | 4.5 | 0 | 0 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  | 18-IJB-40-010 | 18-40-010-iSC | [33 empty] | 1840 | TIA
250 | 10 | 1840 | 18-PT-62103 |  | - | TA-6201 BOTTOM PRES. INDIC. | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-PI-62103 |  |  |  |  | 0 | 80 | 0 | 0 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  | 18-IJB-40-010 | 18-40-010-iSC | [33 empty] | 1840 | PI
251 | 11 | 1840 | 18-PDT-61104 |  | - | TA-6101 PRES.DIFFER. INDIC., ALARNM | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-PDIA-61104 |  |  |  |  | 0 | 120 | 0 | 0 | DCS-AI | IS | [5 empty] | Y |  |  | - |  |  |  | 防雷仪表 | [33 empty] | 1840 | PDIA
252 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [13 empty] | 0 | 4.5 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
253 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [13 empty] | 0 | 0 | 0 | 0 |  | IS |  | DCS | [5 empty] | Site
254 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
255 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
256 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
257 | 1 | 1840 | 18-TT-61107 |  | - | TA-6101 TEMP. INDIC. | [5 empty] | 8 | 3 | 1 | AAI143-H |  | N | 4~20mA | [8 empty] | 18-TI-61107 |  |  |  |  | 0 | 1000 | 260 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-011 | 18-40-011-iSC | [33 empty] | 1840 | TI
258 | 2 | 1840 | 18-TT-61108 |  | - | TA-6101 TEMP. INDIC. | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-TI-61108 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-011 | 18-40-011-iSC | [33 empty] | 1840 | TI
259 | 3 | 1840 | 18-TT-61208 |  | - | GC TO OSBL TEMP. INDIC., ALARM | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-TIA-61208 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-011 | 18-40-011-iSC | [33 empty] | 1840 | TIA
260 | 4 | 1840 | 18-FT-61101 |  | - | GC TO TA-6101 FLOW | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-FIA-61101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-011 | 18-40-011-iSC | [33 empty] | 1840 | FIA
261 | 5 | 1840 | 18-TT-61104 |  | - | TA-6101 TEMP. INDIC. | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-TI-61104 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-015 | 18-40-015-iSC | [33 empty] | 1840 | TI
262 | 6 | 1840 | 18-TT-61106 |  | - | TA-6101 TEMP. INDIC. | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-TI-61106 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-015 | 18-40-015-iSC | [33 empty] | 1840 | TI
263 | 7 | 1840 | 18-TT-62101 |  | - | TA-6201 TEMP. INDIC. | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-TI-62101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-015 | 18-40-015-iSC | [33 empty] | 1840 | TI
264 | 8 | 1840 | 18-TT-62102 |  | - | TA-6201 TEMP. INDIC. | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-TI-62102 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-015 | 18-40-015-iSC | [33 empty] | 1840 | TI
265 | 9 | 1840 | 18-TT-62103 |  | - | TA-6201 TEMP. INDIC. | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-TI-62103 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-015 | 18-40-015-iSC | [33 empty] | 1840 | TI
266 | 10 | 1840 | 18-TT-62104 |  | - | TA-6201 TEMP. INDIC. | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-TI-62104 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-015 | 18-40-015-iSC | [33 empty] | 1840 | TI
267 | 11 | 1840 | 18-PDT-62101 |  | - | TA-6201 PRES.DIFFER. INDIC., ALARM | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-PDIA-62101 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  |  | 防雷仪表 | [33 empty] | 1840 | PDIA
268 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
269 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
270 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
271 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
272 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
273 | 1 | 1840 | 18-TT-61103 |  | - | GC FROM TA-6101 TOP TEMP. INDIC. | [5 empty] | 8 | 4 | 1 | AAI143-H |  | N | 4~20mA | [8 empty] | 18-TI-61103 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-016 | 18-40-016-iSC | [33 empty] | 1840 | TI
274 | 2 | 1840 | 18-TT-61201 |  | - | ETH TO ET-6103 TEMP. INDIC. | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-TI-61201 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-016 | 18-40-016-iSC | [33 empty] | 1840 | TI
275 | 3 | 1840 | 18-TT-61209 |  | - | ETH FROM ET-6103 TEMP. NDIC., ALARM | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-TIA-61209 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-016 | 18-40-016-iSC | [33 empty] | 1840 | TIA
276 | 4 | 1840 | 18-PDT-61211 |  | - | TA-6102 PRES.DIFFER. INDIC., ALARM | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-PDIA-61211 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-016 | 18-40-016-iSC | [33 empty] | 1840 | PDIA
277 | 5 | 1840 | 18-FT-62202 |  | - | PR TO PC-6201 BYPASS FLOW | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-FI-62202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-40-016 | 18-40-016-iSC | [33 empty] | 1840 | FI
278 | 6 | 1812 | 18-PT-17202 |  | - | TEA FROM PP-1701A | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-PIA-17202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-002 | 18-12-002-iSC | [33 empty] | 1812 | PIA
279 | 7 | 1812 | 18-PT-17204 |  | - | TEA FROM PP-1702A | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-PIA-17204 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-002 | 18-12-002-iSC | [33 empty] | 1812 | PIA
280 | 8 | 1812 | 18-PT-17206 |  | - | TEA FROM PP-1701B | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-PIA-17206 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-002 | 18-12-002-iSC | [33 empty] | 1812 | PIA
281 | 9 | 1812 | 18-PT-17208 |  | - | TEA FROM PP-1702B | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-PIA-17208 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-002 | 18-12-002-iSC | [33 empty] | 1812 | PIA
282 | 10 | 1812 | 18-LT-17107 |  | - | VE-1706 | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-LIA-17107 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-12-002 | 18-12-002-iSC | [33 empty] | 1812 | LIA
283 | 11 |  |  |  |  | Spare | [7 empty] | 11 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
284 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
285 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
286 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
287 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
288 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
289 | 1 | 1830 | 18-TT-21101 |  | - | PEROXIDE DOSING ROOM | [5 empty] | 9 | 1 | 1 | AAI143-H |  | N | 4~20mA | [8 empty] | 18-TIA-21101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-005 | 18-30-005-iSC | [33 empty] | 1830 | TIA
290 | 2 | 1830 | 18-TT-36102 |  | - | COOLING WATER TO PX PIPE | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-TIA-36102 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-005 | 18-30-005-iSC | [33 empty] | 1830 | TIA
291 | 3 | 1830 | 18-TT-92101 |  | - | WASTE WATER TO OSBL | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-TI-92101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-005 | 18-30-005-iSC | [33 empty] | 1830 | TI
292 | 4 | 1830 | 18-TT-92102 |  | - | VP-9201 SURFACE WATER COLLECTION | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-TIA-92102 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-005 | 18-30-005-iSC | [33 empty] | 1830 | TIA
293 | 5 | 1830 | 18-PDT-23105 |  | - | FL-2301A/B | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-PDIA-23105 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-006 | 18-30-006-iSC | [33 empty] | 1830 | PDIA
294 | 6 | 1830 | 18-PDT-24103 |  | - | FL-2401 | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-PDIA-24103 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-006 | 18-30-006-iSC | [33 empty] | 1830 | PDIA
295 | 7 | 1830 | 18-LT-66203 |  | - | 18-VE-6602 | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-LIA-66203 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-006 | 18-30-006-iSC | [33 empty] | 1830 | LIA
296 | 8 | 1830 | 18-PT-92101 |  | - | WASTE WATER TO OSBL | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-PI-92101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-007 | 18-30-007-iSC | [33 empty] | 1830 | PI
297 | 9 | 1830 | 18-FT-21107 |  | - | COOLING WATER | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-FIA-21107 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-007 | 18-30-007-iSC | [33 empty] | 1830 | FIA
298 | 10 | 1830 | 18-TT-23102 |  | - | VE-2302 | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-TIA-23102 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-010 | 18-30-010-iSC | [33 empty] | 1830 | TIA
299 | 11 | 1830 | 18-TT-66101 |  | - | OFFGAS FROM ET-6602 | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-TIA-66101 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-IJB-30-015 | 18-30-015-iSC | [33 empty] | 1830 | TIA
300 | 12 | 1830 | 18-TT-23101 |  | - | VE-2301 | [7 empty] | 12 |  |  |  | 4~20mA | [8 empty] | 18-TIA-23101 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 单拉 | 18-30-017-iSC | [33 empty] | 1830 | TIA
301 | 13 | 1830 | 18-TT-66104 |  | - | ET-6601X outlet | [7 empty] | 13 |  |  |  | 4~20mA | [8 empty] | 18-TIA-66104 | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-6601-DJB-0003 | DCS | [33 empty] | 1830 | TIA
302 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
303 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
304 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
305 | 1 | 1830 | 18-PDI-35102 |  | - | 排气过滤器18-FL-3501X差压显示 | [5 empty] | 9 | 2 | 1 | AAI143-H |  | N | 4~20mA | [8 empty] | 18-PDI-35102 |  |  |  |  | 0 | 1000 | 260 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0019 | DCS | [33 empty] | 1830 | PDI
306 | 2 | 1830 | 18-PI-35101 |  | - | 粉料料仓18-VS-3501X顶部压力显示 | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-PI-35101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-3501-DJB-0019 | DCS | [33 empty] | 1830 | PI
307 | 3 | 1830 | 18-TI-35204A |  | 3 | 输送氮气风机18-PB-3501AX主电机定子温度显示 | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-TI-35204A |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-LP-KM-3501AX | DCS | [33 empty] | 1830 | TI
308 | 4 | 1830 | 18-TI-35204B |  | 3 | 输送氮气风机18-PB-3501AX主电机定子温度显示 | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-TI-35204B |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-LP-KM-3501AX | DCS | [33 empty] | 1830 | TI
309 | 5 | 1830 | 18-TI-35204C |  | 3 | 输送氮气风机18-PB-3501AX主电机定子温度显示 | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-TI-35204C |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-LP-KM-3501AX | DCS | [33 empty] | 1830 | TI
310 | 6 | 1830 | 18-TI-35204D |  | 3 | 输送氮气风机18-PC-3501AX主电机轴承温度显示 | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-TI-35204D |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-LP-KM-3501AX | DCS | [33 empty] | 1830 | TI
311 | 7 | 1830 | 18-TI-35204E |  | 3 | 输送氮气风机18-PC-3501AX主电机轴承温度显示 | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-TI-35204E |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-LP-KM-3501AX | DCS | [33 empty] | 1830 | TI
312 | 8 | 1830 | 18-TI-35214A |  | 3 | 输送氮气风机18-PB-3501BX主电机定子温度显示 | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-TI-35214A |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-LP-KM-3501BX | DCS | [33 empty] | 1830 | TI
313 | 9 | 1830 | 18-TI-35214B |  | 3 | 输送氮气风机18-PB-3501BX主电机定子温度显示 | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-TI-35214B |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-LP-KM-3501BX | DCS | [33 empty] | 1830 | TI
314 | 10 | 1830 | 18-TI-35214C |  | 3 | 输送氮气风机18-PB-3501BX主电机定子温度显示 | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-TI-35214C | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-LP-KM-3501BX | DCS | [33 empty] | 1830 | TI
315 | 11 | 1830 | 18-TI-35214D |  | 3 | 输送氮气风机18-PC-3501BX主电机轴承温度显示 | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-TI-35214D | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-LP-KM-3501BX | DCS | [33 empty] | 1830 | TI
316 | 12 | 1830 | 18-TI-35214E |  | 3 | 输送氮气风机18-PC-3501BX主电机轴承温度显示 | [7 empty] | 12 |  |  |  | 4~20mA | [8 empty] | 18-TI-35214E | [8 empty] | DCS-AI | IS |  | DCS |  |  |  | Y |  | Site | - |  |  | 18-LP-KM-3501BX | DCS | [33 empty] | 1830 | TI
317 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
318 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
319 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
320 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | IS |  | DCS | [5 empty] | Site
321 | 1 | 1840 | 18-FT-61205 |  | - | GC TO ET-6105 FLOW INDICA., ALARM | [5 empty] | 10 | 1 | 1 | AAI143-H |  | N | 4~20mA | [8 empty] | 18-FIA-61205 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 18-EJB-40-003 | 18-40-003-SC | [33 empty] | 1840 | FIA
322 | 2 | 1840 | 18-FT-61206 |  | - | C2 OFFSPEC TO OSBL FLOW | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-FI-61206 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 18-EJB-40-003 | 18-40-003-SC | [33 empty] | 1840 | FI
323 | 3 | 1812 | 18-FT-17101 |  | - | TEA TO VE-1701 | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-FQIA-17101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 18-EJB-12-003 | 18-12-001-EC | [33 empty] | 1812 | FQIA
324 | 4 | 1812 | 18-FT-17105 |  | - | ISOPROPANOL TO VE-1705 | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-FI-17105 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 18-EJB-12-003 | 18-12-001-EC | [33 empty] | 1812 | FI
325 | 5 | 1812 | 18-FT-17114 |  | - | WHITE OIL FLUSH FROM PP-1703 | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-FQI-17114 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 18-EJB-12-003 | 18-12-001-EC | [33 empty] | 1812 | FQI
326 | 6 | 1830 | 18-FT-92102 |  | - | WASTE W ATER TO OSBL | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-FQI-92102 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 24VDC |  |  | 单拉 | 单拉 | [33 empty] | 1830 | FQI
327 | 7 | 1830 | 18-WI-35101 |  | - | 粉料料仓18-VS-3501X物料重量显示 | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-WI-35101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | 220VAC |  |  | 18-LP-3501X | DCS | [33 empty] | 1830 | WI
328 | 8 | 1840 | 18-II-62101 |  | - | 18-PP-6202A CURRENT | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-II-62101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1840 | II
329 | 9 | 1840 | 18-II-62102 |  | - | 18-PP-6202B CURRENT | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-II-62102 | [8 empty] | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1840 | II
330 | 10 | 1830 | 18-II-23105 |  | - | 18-PA-2301 CURRENT | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-II-23105 | [8 empty] | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - | [37 empty] | 1830 | II
331 | 11 | 1830 | 18-II-35201 |  | - | 输送氮气风机18-PB-3501AX主电机电流显示 | [7 empty] | 11 |  |  |  | 4~20mA | [8 empty] | 18-II-35201 | [8 empty] | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - | [37 empty] | 1830 | II
332 | 12 | 1830 | 18-II-35202 |  | - | 输送氮气风机18-PB-3501BX主电机电流显示 | [7 empty] | 12 |  |  |  | 4~20mA | [8 empty] | 18-II-35202 | [8 empty] | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - | [37 empty] | 1830 | II
333 | 13 | 1830 | 18-II-35101 |  | - | 粉料仓旋转阀18-PF-3501X的电流显示 | [7 empty] | 13 |  |  |  | 4~20mA | [8 empty] | 18-II-35101 | [8 empty] | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - | [37 empty] | 1830 | II
334 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
335 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
336 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
337 | 1 | 1812 | 18-SI-17201 |  | - | PP-1701A SPEED | [5 empty] | 10 | 2 | 1 | AAI143-H |  | N | 4~20mA | [8 empty] | 18-SI-17201 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1812 | SI
338 | 2 | 1812 | 18-SI-17202 |  | - | PP-1701B SPEED | [7 empty] | 2 |  |  |  | 4~20mA | [8 empty] | 18-SI-17202 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1812 | SI
339 | 3 | 1812 | 18-SI-17203 |  | - | PP-1702A SPEED | [7 empty] | 3 |  |  |  | 4~20mA | [8 empty] | 18-SI-17203 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1812 | SI
340 | 4 | 1812 | 18-SI-17204 |  | - | PP-1702B SPEED | [7 empty] | 4 |  |  |  | 4~20mA | [8 empty] | 18-SI-17204 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1812 | SI
341 | 5 | 1812 | 18-SI-17301 |  | - | PP-1704 SPEED | [7 empty] | 5 |  |  |  | 4~20mA | [8 empty] | 18-SI-17301 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - |  |  |  | MCC | [33 empty] | 1812 | SI
342 | 6 | 1830 | 18-SI-23101 |  | - | 18-PP-2301A SPEED | [7 empty] | 6 |  |  |  | 4~20mA | [8 empty] | 18-SI-23101 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - | [37 empty] | 1830 | SI
343 | 7 | 1830 | 18-SI-23102 |  | - | 18-PP-2301B SPEED | [7 empty] | 7 |  |  |  | 4~20mA | [8 empty] | 18-SI-23102 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - | [37 empty] | 1830 | SI
344 | 8 | 1830 | 18-SI-23105 |  | - | 18-PA-2301 SPEED | [7 empty] | 8 |  |  |  | 4~20mA | [8 empty] | 18-SI-23105 |  |  |  |  | 0 | 0 | 0 | 0 | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - | [37 empty] | 1830 | SI
345 | 9 | 1830 | 18-SI-24101 |  | - | 18-PP-2401 SPEED | [7 empty] | 9 |  |  |  | 4~20mA | [8 empty] | 18-SI-24101 | [8 empty] | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - | [37 empty] | 1830 | SI
346 | 10 | 1830 | 18-SI-35101 |  | - | 粉料仓旋转阀18-PF-3501X的速度显示 | [7 empty] | 10 |  |  |  | 4~20mA | [8 empty] | 18-SI-35101 | [8 empty] | DCS-AI | NIS |  | DCS |  |  |  | N |  | Site | - | [37 empty] | 1830 | SI
347 | 11 |  |  |  |  | Spare | [7 empty] | 11 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
348 | 12 |  |  |  |  | Spare | [7 empty] | 12 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
349 | 13 |  |  |  |  | Spare | [7 empty] | 13 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
350 | 14 |  |  |  |  | Spare | [7 empty] | 14 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
351 | 15 |  |  |  |  | Spare | [7 empty] | 15 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site
352 | 16 |  |  |  |  | Spare | [7 empty] | 16 |  |  |  | 4-20mA | [18 empty] | NIS |  | DCS | [5 empty] | Site

## FCS0304_Digital
1 | NO. | AREA | PID_TAG | COMMENT | Station | NODE | SLOT | Channel | IOMODULE | IO_type | POWER | NO/NC | DUPLEX | DRWNO | BIDNO | LOOP | TYPNO | Address | DIOTAG | DCSTAG | TGCOMM | Remark | signal_origin | FCS_Comp_Name | SB-Surge | SB-Surge Detial | IS_Non_IS | IS_Non_IS Detial | DIR_REV | CACTN | Signal_Location | Signal_Detail | TAG.NO. 1 | POWER | J.B.NAME | JB_CABLE_NM | Core.No._Tot | CHANNEL 4 | JB_CABLE_PAIR | MRP_COMP_Name 5 | TS_Name 6 | TS_Channel | TS1 7 | TS2 8 | TS3 9 | TS 10 | TS 11 | TS 12 | SC_Channel | TS 13 | TS 14 | TS 15 | TS 16 | RL_Channel | TS 17 | TS 18 | TS 19 | TS 20 | TB No. 13 | TB Model 14 | TP_TS1 12 | TP_TS2 13 | TP_TS3 14 | Signal | Y_REV_NO | Y_REV_COMMENT | Remarks |  | LOOP NO
2 | 1 | 1830 | 18-LS-36202 | 18-VE-3620211 | FCS0304 | 1 | 5 | 1 | ADV151-P |  |  |  | Y | [6 empty] | 18-LSL-36202 |  | MI | DCS | [11 empty] | 18-IJB-30-003 | 18-30-003-iCC | [31 empty] | - | 1830
3 | 2 |  |  | Spare |  |  |  | 2 | [13 empty] | MI | DCS
4 | 3 |  |  | Spare |  |  |  | 3 | [13 empty] | MI | DCS
5 | 4 |  |  | Spare |  |  |  | 4 | [13 empty] | MI | DCS
6 | 5 |  |  | Spare |  |  |  | 5 | [13 empty] | MI | DCS | [46 empty] | LOOP NO
7 | 6 |  |  | Spare |  |  |  | 6 | [13 empty] | MI | DCS
8 | 7 |  |  | Spare |  |  |  | 7 | [13 empty] | MI | DCS
9 | 8 |  |  | Spare |  |  |  | 8 | [13 empty] | MI | DCS
10 | 9 |  |  | Spare |  |  |  | 9 | [13 empty] | MI | DCS
11 | 10 |  |  | Spare |  |  |  | 10 | [13 empty] | MI | DCS
12 | 11 |  |  | Spare |  |  |  | 11 | [13 empty] | MI | DCS
13 | 12 |  |  | Spare |  |  |  | 12 | [13 empty] | MI | DCS
14 | 13 |  |  | Spare |  |  |  | 13 | [13 empty] | MI | DCS
15 | 14 |  |  | Spare |  |  |  | 14 | [13 empty] | MI | DCS
16 | 15 |  |  | Spare |  |  |  | 15 | [13 empty] | MI | DCS
17 | 16 |  |  | Spare |  |  |  | 16 | [13 empty] | MI | DCS
18 | 17 |  |  | Spare |  |  |  | 17 | [13 empty] | MI | DCS
19 | 18 |  |  | Spare |  |  |  | 18 | [13 empty] | MI | DCS
20 | 19 |  |  | Spare |  |  |  | 19 | [13 empty] | MI | DCS
21 | 20 |  |  | Spare |  |  |  | 20 | [13 empty] | MI | DCS
22 | 21 |  |  | Spare |  |  |  | 21 | [13 empty] | MI | DCS
23 | 22 |  |  | Spare |  |  |  | 22 | [13 empty] | MI | DCS
24 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | MI | DCS
25 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | MI | DCS
26 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | MI | DCS
27 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | MI | DCS
28 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | MI | DCS
29 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | MI | DCS
30 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | MI | DCS
31 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | MI | DCS
32 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | MI
33 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | MI
34 | 1 | 1830 | 18-LAHH-35102 | 料仓18-VS-3501X高高报 |  | 2 | 5 | 1 | ADV151-P |  |  |  | N | [6 empty] | 18-LAHH-35102 |  | IS | DCS | [11 empty] | 18-3501-DJB-0018 | DCS | [31 empty] | - | 1830
35 | 2 | 1830 | 18-LAHH-35103 | 料仓18-VS-3501X低低报 |  |  |  | 2 | [11 empty] | 18-LAHH-35103 |  | IS | DCS | [11 empty] | 18-3501-DJB-0015 | DCS | [31 empty] | - | 1830
36 | 3 |  |  | Spare |  |  |  | 3 | [13 empty] | IS | DCS
37 | 4 |  |  | Spare |  |  |  | 4 | [13 empty] | IS | DCS
38 | 5 |  |  | Spare |  |  |  | 5 | [13 empty] | IS | DCS
39 | 6 |  |  | Spare |  |  |  | 6 | [13 empty] | IS | DCS
40 | 7 |  |  | Spare |  |  |  | 7 | [13 empty] | IS | DCS
41 | 8 |  |  | Spare |  |  |  | 8 | [13 empty] | IS | DCS
42 | 9 |  |  | Spare |  |  |  | 9 | [13 empty] | IS | DCS
43 | 10 |  |  | Spare |  |  |  | 10 | [13 empty] | IS | DCS
44 | 11 |  |  | Spare |  |  |  | 11 | [13 empty] | IS | DCS
45 | 12 |  |  | Spare |  |  |  | 12 | [13 empty] | IS | DCS
46 | 13 |  |  | Spare |  |  |  | 13 | [13 empty] | IS | DCS
47 | 14 |  |  | Spare |  |  |  | 14 | [13 empty] | IS | DCS
48 | 15 |  |  | Spare |  |  |  | 15 | [13 empty] | IS | DCS
49 | 16 |  |  | Spare |  |  |  | 16 | [13 empty] | IS | DCS
50 | 17 |  |  | Spare |  |  |  | 17 | [13 empty] | IS | DCS
51 | 18 |  |  | Spare |  |  |  | 18 | [13 empty] | IS | DCS
52 | 19 |  |  | Spare |  |  |  | 19 | [13 empty] | IS | DCS
53 | 20 |  |  | Spare |  |  |  | 20 | [13 empty] | IS | DCS
54 | 21 |  |  | Spare |  |  |  | 21 | [13 empty] | IS | DCS
55 | 22 |  |  | Spare |  |  |  | 22 | [13 empty] | IS | DCS
56 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | IS | DCS
57 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | IS | DCS
58 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | IS | DCS
59 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | IS | DCS
60 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | IS | DCS
61 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | IS | DCS
62 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | IS | DCS
63 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | IS | DCS
64 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | IS | DCS
65 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | IS | DCS
66 | 1 | 1840 | 18-XZSH-62301 | LLS TO ET-6203 VALVE ON |  | 2 | 7 | 1 | ADV151-P |  |  |  | N | [6 empty] | 18-XZSH-62301 |  | MI | DCS | [11 empty] | 18-IJB-40-003 | 18-40-003-iCC | [31 empty] | - | 1840
67 | 2 | 1840 | 18-XZSL-62301 | LLS TO ET-6203 VALVE OFF |  |  |  | 2 | [11 empty] | 18-XZSL-62301 |  | MI | DCS | [11 empty] | 18-IJB-40-003 | 18-40-003-iCC | [31 empty] | - | 1840
68 | 3 | 1840 | 18-XZSH-62302 | LLSCformET-6203 VALVE ON |  |  |  | 3 | [11 empty] | 18-XZSH-62302 |  | MI | DCS | [11 empty] | 18-IJB-40-003 | 18-40-003-iCC | [31 empty] | - | 1840
69 | 4 | 1840 | 18-XZSL-62302 | LLSCformET-6203VALVE OFF |  |  |  | 4 | [11 empty] | 18-XZSL-62302 |  | MI | DCS | [11 empty] | 18-IJB-40-003 | 18-40-003-iCC | [31 empty] | - | 1840
70 | 5 | 1840 | 18-XZSH-62303 | P TO POSM VALVE ON |  |  |  | 5 | [11 empty] | 18-XZSH-62303 |  | MI | DCS | [11 empty] | 18-IJB-40-003 | 18-40-003-iCC | [31 empty] | - | 1840
71 | 6 | 1840 | 18-XZSL-62303 | P TO POSM VALVE OFF |  |  |  | 6 | [11 empty] | 18-XZSL-62303 |  | MI | DCS | [11 empty] | 18-IJB-40-003 | 18-40-003-iCC | [31 empty] | - | 1840
72 | 7 | 1840 | 18-FZSL-61103 | LIQUID FEED TO TA-6101 |  |  |  | 7 | [11 empty] | 18-FZSL-61103 |  | MI | DCS | [11 empty] | 18-IJB-40-004 | 18-40-004-iCC | [31 empty] | - | 1840
73 | 8 | 1840 | 18-FZSL-62101 | C3 TO TA-6201 |  |  |  | 8 | [11 empty] | 18-FZSL-62101 |  | MI | DCS | [11 empty] | 18-IJB-40-004 | 18-40-004-iCC | [31 empty] | - | 1840
74 | 9 | 1840 | 18-XZSH-61105 | LLSC FROM ET-6101 |  |  |  | 9 | [11 empty] | 18-XZSH-61105 |  | MI | DCS | [11 empty] | 18-IJB-40-004 | 18-40-004-iCC | [31 empty] | - | 1840
75 | 10 | 1840 | 18-XZSL-61105 | LLSC FROM ET-6101 |  |  |  | 10 | [11 empty] | 18-XZSL-61105 |  | MI | DCS | [11 empty] | 18-IJB-40-004 | 18-40-004-iCC | [31 empty] | - | 1840
76 | 11 | 1840 | 18-XZSH-62101 | C3 TO TA-6201 |  |  |  | 11 | [11 empty] | 18-XZSH-62101 |  | MI | DCS | [11 empty] | 18-IJB-40-004 | 18-40-004-iCC | [31 empty] | - | 1840
77 | 12 | 1840 | 18-XZSL-62101 | C3 TO TA-6201 |  |  |  | 12 | [11 empty] | 18-XZSL-62101 |  | MI | DCS | [11 empty] | 18-IJB-40-004 | 18-40-004-iCC | [31 empty] | - | 1840
78 | 13 | 1840 | 18-FZSL-61104 | LLP STEAM TO ET-6101 |  |  |  | 13 | [11 empty] | 18-FZSL-61104 |  | MI | DCS | [11 empty] | 18-IJB-40-009 | 18-40-009-iCC | [31 empty] | - | 1840
79 | 14 | 1840 | 18-FZSL-62104 | PROPANEformTA-6201 FLOW |  |  |  | 14 | [11 empty] | 18-FZSL-62104 |  | MI | DCS | [11 empty] | 18-IJB-40-009 | 18-40-009-iCC | [31 empty] | - | 1840
80 | 15 | 1840 | 18-FZSL-62105 | PR TO OSBL TANK FLOW |  |  |  | 15 | [11 empty] | 18-FZSL-62105 |  | MI | DCS | [11 empty] | 18-IJB-40-009 | 18-40-009-iCC | [31 empty] | - | 1840
81 | 16 | 1840 | 18-XZSH-61104 | LLP STEAM TO ET-6101 |  |  |  | 16 | [11 empty] | 18-XZSH-61104 |  | MI | DCS | [11 empty] | 18-IJB-40-009 | 18-40-009-iCC | [31 empty] | - | 1840
82 | 17 | 1840 | 18-XZSL-61104 | LLP STEAM TO ET-6101 |  |  |  | 17 | [11 empty] | 18-XZSL-61104 |  | MI | DCS | [11 empty] | 18-IJB-40-009 | 18-40-009-iCC | [31 empty] | - | 1840
83 | 18 | 1840 | 18-XZSH-62105 | PRTO ET-3101 VALVE ON |  |  |  | 18 | [11 empty] | 18-XZSH-62105 |  | MI | DCS | [11 empty] | 18-IJB-40-009 | 18-40-009-iCC | [31 empty] | - | 1840
84 | 19 | 1840 | 18-XZSL-62105 | PRTO ET-3101 VALVE OFF |  |  |  | 19 | [11 empty] | 18-XZSL-62105 |  | MI | DCS | [11 empty] | 18-IJB-40-009 | 18-40-009-iCC | [31 empty] | - | 1840
85 | 20 | 1840 | 18-XZSH-62106 | RECO.PR FROM VE-6202 ON |  |  |  | 20 | [11 empty] | 18-XZSH-62106 |  | MI | DCS | [11 empty] | 18-IJB-40-009 | 18-40-009-iCC | [31 empty] | - | 1840
86 | 21 | 1840 | 18-XZSL-62106 | RECO.PR FROM VE-6202 OFF |  |  |  | 21 | [11 empty] | 18-XZSL-62106 |  | MI | DCS | [11 empty] | 18-IJB-40-009 | 18-40-009-iCC | [31 empty] | - | 1840
87 | 22 | 1812 | 18-LS-17108 | VE-1705 |  |  |  | 22 | [11 empty] | 18-LAH-17108 |  | MI | DCS | [11 empty] | 18-IJB-12-006 | 18-12-006-iCC | [31 empty] | - | 1812
88 | 23 | 1812 | 18-XZSH-17108 | WWO.FROM VE-1705 TO DRUM |  |  |  | 23 | [11 empty] | 18-XZSH-17108 |  | MI | DCS | [11 empty] | 18-IJB-12-006 | 18-12-006-iCC | [31 empty] | - | 1812
89 | 24 | 1812 | 18-XZSL-17108 | WWO.FROM VE-1705 TO DRUM |  |  |  | 24 | [11 empty] | 18-XZSL-17108 |  | MI | DCS | [11 empty] | 18-IJB-12-006 | 18-12-006-iCC | [31 empty] | - | 1812
90 | 25 | 1812 | 18-XZSH-17111 | White Oil to VE-1701 |  |  |  | 25 | [11 empty] | 18-XZSH-17111 |  | MI | DCS | [11 empty] | 18-IJB-12-006 | 18-12-006-iCC | [31 empty] | - | 1812
91 | 26 | 1812 | 18-XZSL-17111 | White Oil to VE-1701 |  |  |  | 26 | [11 empty] | 18-XZSL-17111 |  | MI | DCS | [11 empty] | 18-IJB-12-006 | 18-12-006-iCC | [31 empty] | - | 1812
92 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | MI | DCS
93 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | MI | DCS
94 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | MI | DCS
95 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | MI | DCS
96 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | MI | DCS
97 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | MI | DCS
98 | 1 | 1840 | 18-PZSL-61103A | CARRIER GAS TO TA-6101 |  | 2 | 8 | 1 | ADV151-P |  |  |  | N | [6 empty] | 18-PZSL-61103A |  | MI | DCS | [11 empty] | 18-IJB-40-013 | 18-40-013-iCC | [31 empty] | 6 | 1840
99 | 2 | 1840 | 18-PZSL-61202 | COOL.FROM ET-6102 PRES. |  |  |  | 2 | [11 empty] | 18-PZSL-61202 |  | MI | DCS | [11 empty] | 18-IJB-40-013 | 18-40-013-iCC | [31 empty] | - | 1840
100 | 3 | 1840 | 18-PZSL-61204 | HCS TO ET-6105 PRES. |  |  |  | 3 | [11 empty] | 18-PZSL-61204 |  | MI | DCS | [11 empty] | 18-IJB-40-013 | 18-40-013-iCC | [31 empty] | - | 1840
101 | 4 | 1840 | 18-PZSL-61210 | COOL.FROM ET-6104 PRES. |  |  |  | 4 | [11 empty] | 18-PZSL-61210 |  | MI | DCS | [11 empty] | 18-IJB-40-013 | 18-40-013-iCC | [31 empty] | - | 1840
102 | 5 | 1840 | 18-PZSL-62104 | HCS TO ET-6105 PRES. |  |  |  | 5 | [11 empty] | 18-PZSL-62104 |  | MI | DCS | [11 empty] | 18-IJB-40-013 | 18-40-013-iCC | [31 empty] | - | 1840
103 | 6 | 1840 | 18-FZSL-61201 | RECOV.ETHYtoTA-6102 FLOW |  |  |  | 6 | [11 empty] | 18-FZSL-61201 |  | MI | DCS | [11 empty] | 18-IJB-40-013 | 18-40-013-iCC | [31 empty] | - | 1840
104 | 7 | 1840 | 18-FZSL-61202 | HCS TO TA-6101 RE FLOW |  |  |  | 7 | [11 empty] | 18-FZSL-61202 |  | MI | DCS | [11 empty] | 18-IJB-40-013 | 18-40-013-iCC | [31 empty] | - | 1840
105 | 8 | 1840 | 18-LZSL-61201 | COOL.TO ET-6104 LEVEL |  |  |  | 8 | [11 empty] | 18-LZSL-61201 |  | MI | DCS | [11 empty] | 18-IJB-40-013 | 18-40-013-iCC | [31 empty] | - | 1840
106 | 9 | 1840 | 18-LZSL-61202 | COOL.TO ET-6102 LEVEL |  |  |  | 9 | [11 empty] | 18-LZSL-61202 |  | MI | DCS | [11 empty] | 18-IJB-40-013 | 18-40-013-iCC | [31 empty] | - | 1840
107 | 10 | 1840 | 18-LZSL-61203 | C2 OFFSPEC TO OSBL LEVEL |  |  |  | 10 | [11 empty] | 18-LZSL-61203 |  | MI | DCS | [11 empty] | 18-IJB-40-013 | 18-40-013-iCC | [31 empty] | - | 1840
108 | 11 | 1840 | 18-XZSH-61102 | RECOV. MONOMERS UP-6501 |  |  |  | 11 | [11 empty] | 18-XZSH-61102 |  | MI | DCS | [11 empty] | 18-IJB-40-014 | 18-40-014-iCC | [31 empty] | - | 1840
109 | 12 | 1840 | 18-XZSL-61102 | RECOV. MONOMERS UP-6501 |  |  |  | 12 | [11 empty] | 18-XZSL-61102 |  | MI | DCS | [11 empty] | 18-IJB-40-014 | 18-40-014-iCC | [31 empty] | - | 1840
110 | 13 | 1840 | 18-XZSH-61103 | LIQUID BLEED PP-3201 |  |  |  | 13 | [11 empty] | 18-XZSH-61103 |  | MI | DCS | [11 empty] | 18-IJB-40-014 | 18-40-014-iCC | [31 empty] | - | 1840
111 | 14 | 1840 | 18-XZSL-61103 | LIQUID BLEED PP-3201 |  |  |  | 14 | [11 empty] | 18-XZSL-61103 |  | MI | DCS | [11 empty] | 18-IJB-40-014 | 18-40-014-iCC | [31 empty] | - | 1840
112 | 15 | 1840 | 18-XZSH-61106 | CARRIER GAS TO ET-6106 |  |  |  | 15 | [11 empty] | 18-XZSH-61106 |  | MI | DCS | [11 empty] | 18-IJB-40-014 | 18-40-014-iCC | [31 empty] | - | 1840
113 | 16 | 1840 | 18-XZSL-61106 | CARRIER GAS TO ET-6106 |  |  |  | 16 | [11 empty] | 18-XZSL-61106 |  | MI | DCS | [11 empty] | 18-IJB-40-014 | 18-40-014-iCC | [31 empty] | - | 1840
114 | 17 | 1840 | 18-XZSH-61201 | RECOV.ETHY.TO VE-6103 ON |  |  |  | 17 | [11 empty] | 18-XZSH-61201 |  | MI | DCS | [11 empty] | 18-IJB-40-014 | 18-40-014-iCC | [31 empty] | - | 1840
115 | 18 | 1840 | 18-XZSL-61201 | RECOV.ETHY.TO VE-6103OFF |  |  |  | 18 | [11 empty] | 18-XZSL-61201 |  | MI | DCS | [11 empty] | 18-IJB-40-014 | 18-40-014-iCC | [31 empty] | - | 1840
116 | 19 | 1840 | 18-XZSH-61206 | C2 OFFSPEC TO OSBL ON |  |  |  | 19 | [11 empty] | 18-XZSH-61206 |  | MI | DCS | [11 empty] | 18-IJB-40-014 | 18-40-014-iCC | [31 empty] | - | 1840
117 | 20 | 1840 | 18-XZSL-61206 | C2 OFFSPEC TO OSBL OFF |  |  |  | 20 | [11 empty] | 18-XZSL-61206 |  | MI | DCS | [11 empty] | 18-IJB-40-014 | 18-40-014-iCC | [31 empty] | - | 1840
118 | 21 | 1812 | 18-XZSH-17101 | LP N2 FROM HEADER |  |  |  | 21 | [11 empty] | 18-XZSH-17101 |  | MI | DCS | [11 empty] | 18-IJB-12-004 | 18-12-004-iCC | [31 empty] | - | 1812
119 | 22 | 1812 | 18-XZSL-17101 | LP N2 FROM HEADER |  |  |  | 22 | [11 empty] | 18-XZSL-17101 |  | MI | DCS | [11 empty] | 18-IJB-12-004 | 18-12-004-iCC | [31 empty] | - | 1812
120 | 23 | 1812 | 18-XZSH-17102 | LP NITROGEN TO VE-1701 |  |  |  | 23 | [11 empty] | 18-XZSH-17102 |  | MI | DCS | [11 empty] | 18-IJB-12-004 | 18-12-004-iCC | [31 empty] | - | 1812
121 | 24 | 1812 | 18-XZSL-17102 | LP NITROGEN TO VE-1701 |  |  |  | 24 | [11 empty] | 18-XZSL-17102 |  | MI | DCS | [11 empty] | 18-IJB-12-004 | 18-12-004-iCC | [31 empty] | - | 1812
122 | 25 | 1812 | 18-XZSH-17103 | LP NITROGEN TO VE-1702 |  |  |  | 25 | [11 empty] | 18-XZSH-17103 |  | MI | DCS | [11 empty] | 18-IJB-12-004 | 18-12-004-iCC | [31 empty] | - | 1812
123 | 26 | 1812 | 18-XZSL-17103 | LP NITROGEN TO VE-1702 |  |  |  | 26 | [11 empty] | 18-XZSL-17103 |  | MI | DCS | [11 empty] | 18-IJB-12-004 | 18-12-004-iCC | [31 empty] | - | 1812
124 | 27 | 1812 | 18-XZSH-17105 | TEA CONTAINER ON |  |  |  | 27 | [11 empty] | 18-XZSH-17105 |  | MI | DCS | [11 empty] | 18-IJB-12-004 | 18-12-004-iCC | [31 empty] | - | 1812
125 | 28 | 1812 | 18-XZSL-17105 | TEA CONTAINER OFF |  |  |  | 28 | [11 empty] | 18-XZSL-17105 |  | MI | DCS | [11 empty] | 18-IJB-12-004 | 18-12-004-iCC | [31 empty] | - | 1812
126 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | MI | DCS
127 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | MI | DCS
128 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | MI | DCS
129 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | MI | DCS
130 | 1 | 1812 | 18-XZSH-17104 | TEA TO VE-1701 |  | 3 | 7 | 1 | ADV151-P |  |  |  | N | [6 empty] | 18-XZSH-17104 |  | MI | DCS | [11 empty] | 18-IJB-12-005 | 18-12-005-iCC | [31 empty] | - | 1812
131 | 2 | 1812 | 18-XZSL-17104 | TEA TO VE-1701 |  |  |  | 2 | [11 empty] | 18-XZSL-17104 |  | MI | DCS | [11 empty] | 18-IJB-12-005 | 18-12-005-iCC | [31 empty] | - | 1812
132 | 3 | 1812 | 18-XZSH-17106 | FLUSHING TO VE-1705 |  |  |  | 3 | [11 empty] | 18-XZSH-17106 |  | MI | DCS | [11 empty] | 18-IJB-12-005 | 18-12-005-iCC | [31 empty] | - | 1812
133 | 4 | 1812 | 18-XZSL-17106 | FLUSHING TO VE-1705 |  |  |  | 4 | [11 empty] | 18-XZSL-17106 |  | MI | DCS | [11 empty] | 18-IJB-12-005 | 18-12-005-iCC | [31 empty] | - | 1812
134 | 5 | 1812 | 18-XZSH-17107 | ISOPROPANOL TO VE-1705 |  |  |  | 5 | [11 empty] | 18-XZSH-17107 |  | MI | DCS | [11 empty] | 18-IJB-12-005 | 18-12-005-iCC | [31 empty] | - | 1812
135 | 6 | 1812 | 18-XZSL-17107 | ISOPROPANOL TO VE-1705 |  |  |  | 6 | [11 empty] | 18-XZSL-17107 |  | MI | DCS | [11 empty] | 18-IJB-12-005 | 18-12-005-iCC | [31 empty] | - | 1812
136 | 7 | 1830 | 18-XZSH-21101 | - |  |  |  | 7 | [11 empty] | 18-HZSH-21101 |  | MI | DCS | [11 empty] | 18-IJB-30-002 | 18-30-002-iCC | [31 empty] | - | 1830
137 | 8 | 1830 | 18-XZSL-21101 | - |  |  |  | 8 | [11 empty] | 18-HZSL-21101 |  | MI | DCS | [11 empty] | 18-IJB-30-002 | 18-30-002-iCC | [31 empty] | - | 1830
138 | 9 | 1830 | 18-XZSH-21103 | - |  |  |  | 9 | [11 empty] | 18-HZSH-21103 |  | MI | DCS | [11 empty] | 18-IJB-30-002 | 18-30-002-iCC | [31 empty] | - | 1830
139 | 10 | 1830 | 18-XZSL-21103 | - |  |  |  | 10 | [11 empty] | 18-HZSL-21103 |  | MI | DCS | [11 empty] | 18-IJB-30-002 | 18-30-002-iCC | [31 empty] | - | 1830
140 | 11 | 1830 | 18-XZSH-21104 | - |  |  |  | 11 | [11 empty] | 18-HZSH-21104 |  | MI | DCS | [11 empty] | 18-IJB-30-002 | 18-30-002-iCC | [31 empty] | - | 1830
141 | 12 | 1830 | 18-XZSL-21104 | - |  |  |  | 12 | [11 empty] | 18-HZSL-21104 |  | MI | DCS | [11 empty] | 18-IJB-30-002 | 18-30-002-iCC | [31 empty] | - | 1830
142 | 13 | 1830 | 18-XZSH-36101 | - |  |  |  | 13 | [11 empty] | 18-XZSH-36101 |  | MI | DCS | [11 empty] | 18-IJB-30-003 | 18-30-003-iCC | [31 empty] | - | 1830
143 | 14 | 1830 | 18-XZSL-36101 | - |  |  |  | 14 | [11 empty] | 18-XZSL-36101 |  | MI | DCS | [11 empty] | 18-IJB-30-003 | 18-30-003-iCC | [31 empty] | - | 1830
144 | 15 | 1830 | 18-XZSH-36102 | - |  |  |  | 15 | [11 empty] | 18-XZSH-36102 |  | MI | DCS | [11 empty] | 18-IJB-30-003 | 18-30-003-iCC | [31 empty] | - | 1830
145 | 16 | 1830 | 18-XZSL-36102 | - |  |  |  | 16 | [11 empty] | 18-XZSL-36102 |  | MI | DCS | [11 empty] | 18-IJB-30-003 | 18-30-003-iCC | [31 empty] | - | 1830
146 | 17 | 1830 | 18-XZSH-23101 | - |  |  |  | 17 | [11 empty] | 18-XZSH-23101 |  | MI | DCS | [11 empty] | 18-IJB-30-013 | 18-30-013-iCC | [31 empty] | - | 1830
147 | 18 | 1830 | 18-XZSL-23101 | - |  |  |  | 18 | [11 empty] | 18-HZSL-23101 |  | MI | DCS | [11 empty] | 18-IJB-30-013 | 18-30-013-iCC | [31 empty] | - | 1830
148 | 19 | 1830 | 18-XZSH-24102 | - |  |  |  | 19 | [11 empty] | 18-XZSH-24102 |  | MI | DCS | [11 empty] | 18-IJB-30-013 | 18-30-013-iCC | [31 empty] | - | 1830
149 | 20 | 1830 | 18-XZSL-24102 | - |  |  |  | 20 | [11 empty] | 18-XZSL-24102 |  | MI | DCS | [11 empty] | 18-IJB-30-013 | 18-30-013-iCC | [31 empty] | - | 1830
150 | 21 | 1830 | 18-PZSL-66102 | - |  |  |  | 21 | [11 empty] | 18-PZSL-66102 |  | MI | DCS | [11 empty] | 18-IJB-30-016 | 18-30-016-iCC | [31 empty] | - | 1830
151 | 22 | 1830 | 18-HZSH-66102 | - |  |  |  | 22 | [11 empty] | 18-HZSH-66102 |  | MI | DCS | [11 empty] | 18-IJB-30-016 | 18-30-016-iCC | [31 empty] | - | 1830
152 | 23 | 1830 | 18-HZSL-66102 | - |  |  |  | 23 | [11 empty] | 18-HZSL-66102 |  | MI | DCS | [11 empty] | 18-IJB-30-016 | 18-30-016-iCC | [31 empty] | - | 1830
153 | 24 | 1830 | 18-XZSH-66101 | - |  |  |  | 24 | [11 empty] | 18-XZSH-66101 |  | MI | DCS | [11 empty] | 18-IJB-30-016 | 18-30-016-iCC | [31 empty] | - | 1830
154 | 25 | 1830 | 18-XZSL-66101 | - |  |  |  | 25 | [11 empty] | 18-XZSL-66101 |  | MI | DCS | [11 empty] | 18-IJB-30-016 | 18-30-016-iCC | [31 empty] | - | 1830
155 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | MI | DCS
156 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | MI | DCS
157 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | MI | DCS
158 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | MI | DCS
159 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | MI | DCS
160 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | MI | DCS
161 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | MI | DCS
162 | 1 | 1830 | 18-XZSH-66105 | - |  | 3 | 8 | 1 | ADV151-P |  |  |  | N | [6 empty] | 18-XZSH-66105 |  | MI | DCS | [11 empty] | 18-6601-DJB-0001 | DCS | [31 empty] | - | 1830
163 | 2 | 1830 | 18-XZSL-66105 | - |  |  |  | 2 | [11 empty] | 18-XZSL-66105 |  | MI | DCS | [11 empty] | 18-6601-DJB-0001 | DCS | [31 empty] | - | 1830
164 | 3 | 1830 | 18-XZSH-66106 | - |  |  |  | 3 | [11 empty] | 18-XZSH-66106 |  | MI | DCS | [11 empty] | 18-6601-DJB-0001 | DCS | [31 empty] | - | 1830
165 | 4 | 1830 | 18-XZSL-66106 | - |  |  |  | 4 | [11 empty] | 18-XZSL-66106 |  | MI | DCS | [11 empty] | 18-6601-DJB-0001 | DCS | [31 empty] | - | 1830
166 | 5 | 1830 | 18-XZH-35201 | 气动蝶阀18-XV-35201已开 |  |  |  | 5 | [11 empty] | 18-XZH-35201 |  | MI | DCS | [11 empty] | 18-3501-DJB-0011 | DCS | [31 empty] | - | 1830
167 | 6 | 1830 | 18-XZL-35201 | 气动蝶阀18-XV-35201已关 |  |  |  | 6 | [11 empty] | 18-XZL-35201 |  | MI | DCS | [11 empty] | 18-3501-DJB-0011 | DCS | [31 empty] | - | 1830
168 | 7 | 1830 | 18-XZH-35202 | 气动蝶阀18-XV-35202已开 |  |  |  | 7 | [11 empty] | 18-XZH-35202 |  | MI | DCS | [11 empty] | 18-3501-DJB-0011 | DCS | [31 empty] | - | 1830
169 | 8 | 1830 | 18-XZL-35202 | 气动蝶阀18-XV-35202已关 |  |  |  | 8 | [11 empty] | 18-XZL-35202 |  | MI | DCS | [11 empty] | 18-3501-DJB-0011 | DCS | [31 empty] | - | 1830
170 | 9 | 1830 | 18-XZH-35203 | 气动蝶阀18-XV-35203已开 |  |  |  | 9 | [11 empty] | 18-XZH-35203 |  | MI | DCS | [11 empty] | 18-3501-DJB-0011 | DCS | [31 empty] | - | 1830
171 | 10 | 1830 | 18-XZL-35203 | 气动蝶阀18-XV-35203已关 |  |  |  | 10 | [11 empty] | 18-XZL-35203 |  | MI | DCS | [11 empty] | 18-3501-DJB-0011 | DCS | [31 empty] | - | 1830
172 | 11 | 1830 | 18-XZH-35204 | 气动蝶阀18-XV-35204已开 |  |  |  | 11 | [11 empty] | 18-XZH-35204 |  | MI | DCS | [11 empty] | 18-3501-DJB-0011 | DCS | [31 empty] | - | 1830
173 | 12 | 1830 | 18-XZL-35204 | 气动蝶阀18-XV-35204已关 |  |  |  | 12 | [11 empty] | 18-XZL-35204 |  | MI | DCS | [11 empty] | 18-3501-DJB-0011 | DCS | [31 empty] | - | 1830
174 | 13 | 1830 | 18-XZH-35206 | 气动蝶阀18-XV-35206已开 |  |  |  | 13 | [11 empty] | 18-XZH-35206 |  | MI | DCS | [11 empty] | 18-3501-DJB-0011 | DCS | [31 empty] | - | 1830
175 | 14 | 1830 | 18-XZL-35206 | 气动蝶阀18-XV-35206已关 |  |  |  | 14 | [11 empty] | 18-XZL-35206 |  | MI | DCS | [11 empty] | 18-3501-DJB-0011 | DCS | [31 empty] | - | 1830
176 | 15 | 1830 | 18-XZH-35102 | 气动滑板阀18-XV35102已开 |  |  |  | 15 | [11 empty] | 18-XZH-35102 |  | MI | DCS | [11 empty] | 18-3501-DJB-0015 | DCS | [31 empty] | - | 1830
177 | 16 | 1830 | 18-XZL-35102 | 气动滑板阀18-XV35102已关 |  |  |  | 16 | [11 empty] | 18-XZL-35102 |  | MI | DCS | [11 empty] | 18-3501-DJB-0015 | DCS | [31 empty] | - | 1830
178 | 17 | 1830 | 18-XZH-35107 | 气动蝶阀18-XV-35107已开 |  |  |  | 17 | [11 empty] | 18-XZH-35107 |  | MI | DCS | [11 empty] | 18-3501-DJB-0015 | DCS | [31 empty] | - | 1830
179 | 18 | 1830 | 18-XZL-35107 | 气动蝶阀18-XV-35107已关 |  |  |  | 18 | [11 empty] | 18-XZL-35107 |  | MI | DCS | [11 empty] | 18-3501-DJB-0015 | DCS | [31 empty] | - | 1830
180 | 19 | 1830 | 18-XZH-35103 | 手动蝶阀18-BV-35103已开 |  |  |  | 19 | [11 empty] | 18-XZH-35103 |  | MI | DCS | [11 empty] | 18-3501-DJB-0018 | DCS | [31 empty] | - | 1830
181 | 20 | 1830 | 18-XZL-35103 | 手动蝶阀18-BV-35103已关 |  |  |  | 20 | [11 empty] | 18-XZL-35103 |  | MI | DCS | [11 empty] | 18-3501-DJB-0018 | DCS | [31 empty] | - | 1830
182 | 21 | 1830 | 18-XZH-35101 | 气动滑板阀18-XV35101已开 |  |  |  | 21 | [11 empty] | 18-XZH-35101 |  | MI | DCS | [12 empty] | 无电缆信息 | [31 empty] | - | 1830
183 | 22 | 1830 | 18-XZL-35101 | 气动滑板阀18-XV35101已关 |  |  |  | 22 | [11 empty] | 18-XZL-35101 |  | MI | DCS | [12 empty] | 无电缆信息 | [31 empty] | - | 1830
184 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | MI | DCS
185 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | MI | DCS
186 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | MI | DCS
187 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | MI | DCS
188 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | MI | DCS
189 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | MI | DCS
190 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | MI | DCS
191 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | MI | DCS
192 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | MI | DCS
193 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | MI | DCS
194 | 1 | 1812 | 18-YS-17101 | WHITE OIL DRUM |  | 4 | 7 | 1 | ADV151-P |  |  |  | Y | [6 empty] | 18-YSA-17101 |  | IS | DCS | [11 empty] | 18-EJB-12-003 | 18-12-001-EC | [31 empty] | - | 1812
195 | 2 | 1812 | 18-YS-17102 | TEA CONTAINER |  |  |  | 2 | [11 empty] | 18-YSA-17102 |  | IS | DCS | [11 empty] | 18-EJB-12-003 | 18-12-001-EC | [31 empty] | - | 1812
196 | 3 | 1830 | 18-YS-24103 | LIQUID ADDITIVE DRUM |  |  |  | 3 | [11 empty] | 18-YSA-24103 |  | IS | DCS | [11 empty] | 18-IJB-30-013 | 18-30-013-iCC | [31 empty] | - | 1830
197 | 4 |  |  | Spare |  |  |  | 4 | [13 empty] | IS | DCS
198 | 5 |  |  | Spare |  |  |  | 5 | [13 empty] | IS | DCS
199 | 6 |  |  | Spare |  |  |  | 6 | [13 empty] | IS | DCS
200 | 7 |  |  | Spare |  |  |  | 7 | [13 empty] | IS | DCS
201 | 8 |  |  | Spare |  |  |  | 8 | [13 empty] | IS | DCS
202 | 9 |  |  | Spare |  |  |  | 9 | [13 empty] | IS | DCS
203 | 10 |  |  | Spare |  |  |  | 10 | [13 empty] | IS | DCS
204 | 11 |  |  | Spare |  |  |  | 11 | [13 empty] | IS | DCS
205 | 12 |  |  | Spare |  |  |  | 12 | [13 empty] | IS | DCS
206 | 13 |  |  | Spare |  |  |  | 13 | [13 empty] | IS | DCS
207 | 14 |  |  | Spare |  |  |  | 14 | [13 empty] | IS | DCS
208 | 15 |  |  | Spare |  |  |  | 15 | [13 empty] | IS | DCS
209 | 16 |  |  | Spare |  |  |  | 16 | [13 empty] | IS | DCS
210 | 17 |  |  | Spare |  |  |  | 17 | [13 empty] | IS | DCS
211 | 18 |  |  | Spare |  |  |  | 18 | [13 empty] | IS | DCS
212 | 19 |  |  | Spare |  |  |  | 19 | [13 empty] | IS | DCS
213 | 20 |  |  | Spare |  |  |  | 20 | [13 empty] | IS | DCS
214 | 21 |  |  | Spare |  |  |  | 21 | [13 empty] | IS | DCS
215 | 22 |  |  | Spare |  |  |  | 22 | [13 empty] | IS | DCS
216 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | IS | DCS
217 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | IS | DCS
218 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | IS | DCS
219 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | IS | DCS
220 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | IS | DCS
221 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | IS | DCS
222 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | IS | DCS
223 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | IS | DCS
224 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | IS | DCS
225 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | IS | DCS
226 | 1 | 1840 | 18-LS-61207 | PP-6103 INLET LEVEL |  | 5 | 7 | 1 | ADV151-P |  |  |  | Y | [6 empty] | 18-LSL-61207 |  | RE | DCS | [12 empty] | 单拉 | [31 empty] | - | 1840
227 | 2 | 1812 | 18-PS-17211 | 18-PP-1701A DIAPHRAGM |  |  |  | 2 | [11 empty] | 18-PSH-17211 |  | RE | DCS | [11 empty] | 18-EJB-12-004 | 18-12-004-CC | [31 empty] | - | 1812
228 | 3 | 1812 | 18-PS-17212 | 18-PP-1701B DIAPHRAGM |  |  |  | 3 | [11 empty] | 18-PSH-17212 |  | RE | DCS | [11 empty] | 18-EJB-12-004 | 18-12-004-CC | [31 empty] | - | 1812
229 | 4 | 1812 | 18-PS-17213 | 18-PP-1702A DIAPHRAGM |  |  |  | 4 | [11 empty] | 18-PSH-17213 |  | RE | DCS | [11 empty] | 18-EJB-12-004 | 18-12-004-CC | [31 empty] | - | 1812
230 | 5 | 1812 | 18-PS-17214 | 18-PP-1702B DIAPHRAGM |  |  |  | 5 | [11 empty] | 18-PSH-17214 |  | RE | DCS | [11 empty] | 18-EJB-12-004 | 18-12-004-CC | [31 empty] | - | 1812
231 | 6 | 1812 | 18-PS-17303 | 18-PP-1704 DIAPHRAGM |  |  |  | 6 | [11 empty] | 18-PSH-17303 |  | RE | DCS | [11 empty] | 18-EJB-12-004 | 18-12-004-CC | [31 empty] | - | 1812
232 | 7 | 1830 | 18-PS-21104 | 18-PP-2101 DIAPHRAGM |  |  |  | 7 | [11 empty] | 18-PSH-21104 |  | RE | DCS | [11 empty] | 单拉 | 单拉 | [31 empty] | - | 1830
233 | 8 | 1830 | 18-PS-21102 | 18-PP-2102 DIAPHRAGM |  |  |  | 8 | [11 empty] | 18-PSH-21102 |  | RE | DCS | [11 empty] | 单拉 | 单拉 | [31 empty] | - | 1830
234 | 9 |  |  | Spare |  |  |  | 9 | [13 empty] | RE | DCS
235 | 10 |  |  | Spare |  |  |  | 10 | [13 empty] | RE | DCS
236 | 11 |  |  | Spare |  |  |  | 11 | [13 empty] | RE | DCS
237 | 12 |  |  | Spare |  |  |  | 12 | [13 empty] | RE | DCS
238 | 13 |  |  | Spare |  |  |  | 13 | [13 empty] | RE | DCS
239 | 14 |  |  | Spare |  |  |  | 14 | [13 empty] | RE | DCS
240 | 15 |  |  | Spare |  |  |  | 15 | [13 empty] | RE | DCS
241 | 16 |  |  | Spare |  |  |  | 16 | [13 empty] | RE | DCS
242 | 17 |  |  | Spare |  |  |  | 17 | [13 empty] | RE | DCS
243 | 18 |  |  | Spare |  |  |  | 18 | [13 empty] | RE | DCS
244 | 19 |  |  | Spare |  |  |  | 19 | [13 empty] | RE | DCS
245 | 20 |  |  | Spare |  |  |  | 20 | [13 empty] | RE | DCS
246 | 21 |  |  | Spare |  |  |  | 21 | [13 empty] | RE | DCS
247 | 22 |  |  | Spare |  |  |  | 22 | [13 empty] | RE | DCS
248 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | RE | DCS
249 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | RE | DCS
250 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | RE | DCS
251 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | RE | DCS
252 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | RE | DCS
253 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | RE | DCS
254 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | RE | DCS
255 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | RE | DCS
256 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | RE | DCS
257 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | RE | DCS
258 | 1 | 1840 | 18-HS-61201P | 18-PP-6102A STOP |  | 6 | 7 | 1 | ADV551-P |  |  |  | Y | [6 empty] | 18-HS-61201P |  | dry | DCS | [12 empty] | MCC | [31 empty] | - | 1840
259 | 2 | 1840 | 18-HS-61202P | 18-PP-6102B STOP |  |  |  | 2 | [11 empty] | 18-HS-61202P |  | dry | DCS | [12 empty] | MCC | [31 empty] | - | 1840
260 | 3 | 1840 | 18-HS-61203P | 18-PP-6103 STOP |  |  |  | 3 | [11 empty] | 18-HS-61203P |  | dry | DCS | [12 empty] | MCC | [31 empty] | - | 1840
261 | 4 | 1840 | 18-HS-62101P | 18-PP-6202A STOP |  |  |  | 4 | [11 empty] | 18-HS-62101P |  | dry | DCS | [12 empty] | MCC | [31 empty] | - | 1840
262 | 5 | 1840 | 18-HS-62102P | 18-PP-6202B STOP |  |  |  | 5 | [11 empty] | 18-HS-62102P |  | dry | DCS | [12 empty] | MCC | [31 empty] | - | 1840
263 | 6 |  |  | Spare |  |  |  | 6 | [13 empty] | dry | DCS
264 | 7 |  |  | Spare |  |  |  | 7 | [13 empty] | dry | DCS
265 | 8 |  |  | Spare |  |  |  | 8 | [13 empty] | dry | DCS
266 | 9 |  |  | Spare |  |  |  | 9 | [13 empty] | dry | DCS
267 | 10 |  |  | Spare |  |  |  | 10 | [13 empty] | dry | DCS
268 | 11 |  |  | Spare |  |  |  | 11 | [13 empty] | dry | DCS
269 | 12 |  |  | Spare |  |  |  | 12 | [13 empty] | dry | DCS
270 | 13 |  |  | Spare |  |  |  | 13 | [13 empty] | dry | DCS
271 | 14 |  |  | Spare |  |  |  | 14 | [13 empty] | dry | DCS
272 | 15 |  |  | Spare |  |  |  | 15 | [13 empty] | dry | DCS
273 | 16 |  |  | Spare |  |  |  | 16 | [13 empty] | dry | DCS
274 | 17 |  |  | Spare |  |  |  | 17 | [13 empty] | dry | DCS
275 | 18 |  |  | Spare |  |  |  | 18 | [13 empty] | dry | DCS
276 | 19 |  |  | Spare |  |  |  | 19 | [13 empty] | dry | DCS
277 | 20 |  |  | Spare |  |  |  | 20 | [13 empty] | dry | DCS
278 | 21 |  |  | Spare |  |  |  | 21 | [13 empty] | dry
279 | 22 |  |  | Spare |  |  |  | 22 | [13 empty] | dry
280 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | dry
281 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | dry
282 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | dry
283 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | dry
284 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | dry
285 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | dry
286 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | dry
287 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | dry
288 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | dry
289 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | dry
290 | 1 | 1812 | 18-HS-17201P | PP-1701A STOP |  | 7 | 7 | 1 | ADV551-P |  |  |  | Y | [6 empty] | 18-HS-17201P |  | dry | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
291 | 2 | 1812 | 18-HS-17202P | PP-1701B STOP |  |  |  | 2 | [11 empty] | 18-HS-17202P |  | dry | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
292 | 3 | 1812 | 18-HS-17203P | PP-1702A STOP |  |  |  | 3 | [11 empty] | 18-HS-17203P |  | dry | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
293 | 4 | 1812 | 18-HS-17204P | PP-1702B STOP |  |  |  | 4 | [11 empty] | 18-HS-17204P |  | dry | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
294 | 5 | 1812 | 18-HS-17301P | PP-1704 STOP |  |  |  | 5 | [11 empty] | 18-HS-17301P |  | dry | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
295 | 6 | 1812 | 18-HS-17109P | PP-1705 STOP |  |  |  | 6 | [11 empty] | 18-HS-17109P |  | dry | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
296 | 7 |  |  | Spare |  |  |  | 7 | [13 empty] | dry | DCS
297 | 8 |  |  | Spare |  |  |  | 8 | [13 empty] | dry | DCS
298 | 9 |  |  | Spare |  |  |  | 9 | [13 empty] | dry | DCS
299 | 10 |  |  | Spare |  |  |  | 10 | [13 empty] | dry | DCS
300 | 11 |  |  | Spare |  |  |  | 11 | [13 empty] | dry | DCS
301 | 12 |  |  | Spare |  |  |  | 12 | [13 empty] | dry | DCS
302 | 13 |  |  | Spare |  |  |  | 13 | [13 empty] | dry | DCS
303 | 14 |  |  | Spare |  |  |  | 14 | [13 empty] | dry | DCS
304 | 15 |  |  | Spare |  |  |  | 15 | [13 empty] | dry | DCS
305 | 16 |  |  | Spare |  |  |  | 16 | [13 empty] | dry | DCS
306 | 17 |  |  | Spare |  |  |  | 17 | [13 empty] | dry | DCS
307 | 18 |  |  | Spare |  |  |  | 18 | [13 empty] | dry
308 | 19 |  |  | Spare |  |  |  | 19 | [13 empty] | dry
309 | 20 |  |  | Spare |  |  |  | 20 | [13 empty] | dry
310 | 21 |  |  | Spare |  |  |  | 21 | [13 empty] | dry
311 | 22 |  |  | Spare |  |  |  | 22 | [13 empty] | dry
312 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | dry
313 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | dry
314 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | dry
315 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | dry
316 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | dry
317 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | dry
318 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | dry
319 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | dry
320 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | dry
321 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | dry
322 | 1 | 1830 | 18-HS-21103P | 18-PP-2101 STOP |  | 8 | 7 | 1 | ADV551-P |  |  |  | Y | [6 empty] | 18-HS-21103P |  | dry | DCS | [44 empty] | 2 | 1830
323 | 2 | 1830 | 18-HS-21104P | 18-PP-2102 STOP |  |  |  | 2 | [11 empty] | 18-HS-21104P |  | dry | DCS | [44 empty] | 2 | 1830
324 | 3 | 1830 | 18-HS-21102P | 18-PB-2101 STOP |  |  |  | 3 | [11 empty] | 18-HS-21102P |  | dry | DCS | [44 empty] | 2 | 1830
325 | 4 | 1830 | 18-HS-23101P | 18-PP-2301A DCS STOP |  |  |  | 4 | [11 empty] | 18-HS-23101P |  | dry | DCS | [44 empty] | 2 | 1830
326 | 5 | 1830 | 18-HS-23102P | 18-PP-2301B STOP |  |  |  | 5 | [11 empty] | 18-HS-23102P |  | dry | DCS | [44 empty] | 2 | 1830
327 | 6 | 1830 | 18-HS-23105P | 18-PA-2301 STOP |  |  |  | 6 | [11 empty] | 18-HS-23105P |  | dry | DCS | [44 empty] | 2 | 1830
328 | 7 | 1830 | 18-HS-24101P | 18-PP-2401 STOP |  |  |  | 7 | [11 empty] | 18-HS-24101P |  | dry | DCS | [44 empty] | 2 | 1830
329 | 8 | 1830 | 18-HS-36106P | 18-PF-3606 STOP |  |  |  | 8 | [11 empty] | 18-HS-36106P |  | dry | DCS | [44 empty] | 3 | 1830
330 | 9 | 1830 | 18-HS-66101P | 18-PV-6601X STOP |  |  |  | 9 | [11 empty] | 18-HS-66101P |  | dry | DCS | [44 empty] | 6 | 1830
331 | 10 | 1830 | 18-HS-92101P | 18-PP-9201A STOP |  |  |  | 10 | [11 empty] | 18-HS-92101P |  | dry | DCS | [44 empty] | 9 | 1830
332 | 11 | 1830 | 18-HS-92102P | 18-PP-9201B STOP |  |  |  | 11 | [11 empty] | 18-HS-92102P |  | dry | DCS | [44 empty] | 9 | 1830
333 | 12 | 1830 | 18-HS-HEF102AS | 边墙风机102A/103A启动 |  |  |  | 12 | [11 empty] | 18-HS-HEF102AS |  | dry | DCS | [44 empty] | F | 1830
334 | 13 | 1830 | 18-HS-HEF102BS | 边墙风机102B/103B启动 |  |  |  | 13 | [11 empty] | 18-HS-HEF102BS |  | dry | DCS | [44 empty] | F | 1830
335 | 14 | 1830 | 18-HS-HEF104AS | 边墙风机104A启动 |  |  |  | 14 | [11 empty] | 18-HS-HEF104AS |  | dry | DCS | [44 empty] | F | 1830
336 | 15 | 1830 | 18-HS-HEF104BS | 边墙风机104B/105B启动 |  |  |  | 15 | [11 empty] | 18-HS-HEF104BS |  | dry | DCS | [44 empty] | F | 1830
337 | 16 | 1830 | 18-HS-35201P | 输送氮气风机3501AX停 |  |  |  | 16 | [11 empty] | 18-HS-35201P |  | dry | DCS | [44 empty] | 3 | 1830
338 | 17 | 1830 | 18-HS-35202P | 输送氮气风机3501BX停 |  |  |  | 17 | [11 empty] | 18-HS-35202P |  | dry | DCS | [44 empty] | 3 | 1830
339 | 18 | 1830 | 18-HS-35102P | 粉料循环旋转阀3502X的停 |  |  |  | 18 | [11 empty] | 18-HS-35102P |  | dry | DCS | [44 empty] | 3 | 1830
340 | 19 | 1830 | 18-HS-35101P | 粉料仓旋转阀13501X的停 |  |  |  | 19 | [11 empty] | 18-HS-35101P |  | dry | DCS | [44 empty] | 3 | 1830
341 | 20 |  |  | Spare |  |  |  | 20 | [13 empty] | dry | DCS
342 | 21 |  |  | Spare |  |  |  | 21 | [13 empty] | dry | DCS
343 | 22 |  |  | Spare |  |  |  | 22 | [13 empty] | dry | DCS
344 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | dry | DCS
345 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | dry | DCS
346 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | dry | DCS
347 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | dry | DCS
348 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | dry | DCS
349 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | dry | DCS
350 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | dry | DCS
351 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | dry | DCS
352 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | dry | DCS
353 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | dry | DCS
354 | 1 | 1840 | 18-HS-61101A | RUD |  | 9 | 3 | 1 | ADV151-P |  |  |  | N | [6 empty] | 18-HS-61101A |  | RE | DCS | [44 empty] | - | 1840
355 | 2 | 1840 | 18-HS-61101B | RUD |  |  |  | 2 | [11 empty] | 18-HS-61101B |  | RE | DCS | [12 empty] | 单拉 | [31 empty] | - | 1840
356 | 3 | 1840 | 18-HS-61102 | RUD RESET |  |  |  | 3 | [11 empty] | 18-HS-61102 |  | RE | DCS | [44 empty] | - | 1840
357 | 4 | 1840 | 18-YL-61201R | 18-PP-6102A RUN |  |  |  | 4 | [11 empty] | 18-YL-61201R |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
358 | 5 | 1840 | 18-YL-61201F | 18-PP-6102A FAULT |  |  |  | 5 | [11 empty] | 18-YL-61201F |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
359 | 6 | 1840 | 18-YL-61202R | 18-PP-6102B RUN |  |  |  | 6 | [11 empty] | 18-YL-61202R |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
360 | 7 | 1840 | 18-YL-61202F | 18-PP-6102B FAULT |  |  |  | 7 | [11 empty] | 18-YL-61202F |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
361 | 8 | 1840 | 18-YL-61203R | 18-PP-6103 RUN |  |  |  | 8 | [11 empty] | 18-YL-61203R |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
362 | 9 | 1840 | 18-YL-61203F | 18-PP-6103 FAULT |  |  |  | 9 | [11 empty] | 18-YL-61203F |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
363 | 10 | 1840 | 18-YL-62101L | 18-PP-6202A REMOTE |  |  |  | 10 | [11 empty] | 18-YL-62101L |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
364 | 11 | 1840 | 18-YL-62101R | 18-PP-6202A RUN |  |  |  | 11 | [11 empty] | 18-YL-62101R |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
365 | 12 | 1840 | 18-YL-62101F | 18-PP-6202A FAULT |  |  |  | 12 | [11 empty] | 18-YL-62101F |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
366 | 13 | 1840 | 18-YL-62102L | 18-PP-6202B REMOTE |  |  |  | 13 | [11 empty] | 18-YL-62102L |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
367 | 14 | 1840 | 18-YL-62102R | 18-PP-6202B RUN |  |  |  | 14 | [11 empty] | 18-YL-62102R |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
368 | 15 | 1840 | 18-YL-62102F | 18-PP-6202B FAULT |  |  |  | 15 | [11 empty] | 18-YL-62102F |  | RE | DCS | [12 empty] | MCC | [31 empty] | - | 1840
369 | 16 |  |  | Spare |  |  |  | 16 | [13 empty] | RE | DCS
370 | 17 | 1812 | 18-HS-17102B | TEA CONTAINER OFFLINE |  |  |  | 17 | [11 empty] | 18-HS-17102B |  | RE | DCS | [11 empty] | LCP-1 | 18-LCP-1-CC1 | [31 empty] | 1 | 1812
371 | 18 | 1812 | 18-HS-17103 | SYSTEM FLUSH |  |  |  | 18 | [11 empty] | 18-HS-17103 |  | RE | DCS | [11 empty] | LCP-1 | 18-LCP-1-CC1 | [31 empty] | - | 1812
372 | 19 | 1812 | 18-HS-17104 | SYSTEM PRESSURE |  |  |  | 19 | [11 empty] | 18-HS-17104 |  | RE | DCS | [11 empty] | LCP-1 | 18-LCP-1-CC1 | [31 empty] | - | 1812
373 | 20 | 1812 | 18-HS-17105 | SYSTEM DEPRESSURE |  |  |  | 20 | [11 empty] | 18-HS-17105 |  | RE | DCS | [11 empty] | LCP-1 | 18-LCP-1-CC1 | [31 empty] | - | 1812
374 | 21 | 1812 | 18-HS-17106 | TEA CONTAINER ONLINE |  |  |  | 21 | [11 empty] | 18-HS-17106 |  | RE | DCS | [11 empty] | LCP-1 | 18-LCP-1-CC1 | [31 empty] | - | 1812
375 | 22 | 1812 | 18-HS-17108 | XV-17105 RESET |  |  |  | 22 | [11 empty] | 18-HS-17108 |  | RE | DCS | [11 empty] | LCP-2 | 18-LCP-2-CC1 | [31 empty] | - | 1812
376 | 23 | 1812 | 18-XHSO-17106 | FLUSHING TO VE-1705 |  |  |  | 23 | [11 empty] | 18-XHSO-17106 |  | RE | DCS | [11 empty] | LCP-2 | 18-LCP-2-CC1 | [31 empty] | - | 1812
377 | 24 | 1812 | 18-XHSC-17106 | FLUSHING TO VE-1705 |  |  |  | 24 | [11 empty] | 18-XHSC-17106 |  | RE | DCS | [11 empty] | LCP-2 | 18-LCP-2-CC1 | [31 empty] | - | 1812
378 | 25 | 1812 | 18-XHSO-17107 | ISOPROPANOL TO VE-1705 |  |  |  | 25 | [11 empty] | 18-XHSO-17107 |  | RE | DCS | [11 empty] | LCP-2 | 18-LCP-2-CC1 | [31 empty] | - | 1812
379 | 26 | 1812 | 18-XHSC-17107 | ISOPROPANOL TO VE-1705 |  |  |  | 26 | [11 empty] | 18-XHSC-17107 |  | RE | DCS | [11 empty] | LCP-2 | 18-LCP-2-CC1 | [31 empty] | - | 1812
380 | 27 | 1812 | 18-HS-17109A | PA-1705 START |  |  |  | 27 | [11 empty] | 18-HS-17109A |  | RE | DCS | [11 empty] | LCP-2 | 18-LCP-2-CC1 | [31 empty] | 1 | 1812
381 | 28 | 1812 | 18-HS-17109B | PA-1705 STOP |  |  |  | 28 | [11 empty] | 18-HS-17109B |  | RE | DCS | [11 empty] | LCP-2 | 18-LCP-2-CC1 | [31 empty] | 1 | 1812
382 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | RE | DCS
383 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | RE | DCS
384 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | RE | DCS
385 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | RE | DCS
386 | 1 | 1812 | 18-XHSO-17111 | White Oil to VE-1701 |  | 9 | 4 | 1 | ADV151-P |  |  |  | N | [6 empty] | 18-XHSO-17111 |  | RE | DCS | [11 empty] | 18-EJB-12-004 | 18-12-004-CC | [31 empty] | - | 1812
387 | 2 | 1812 | 18-XHSC-17111 | White Oil to VE-1701 |  |  |  | 2 | [11 empty] | 18-XHSC-17111 |  | RE | DCS | [11 empty] | 18-EJB-12-004 | 18-12-004-CC | [31 empty] | - | 1812
388 | 3 | 1812 | 18-YL-17201R | PP-1701A RUN |  |  |  | 3 | [11 empty] | 18-YL-17201R |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
389 | 4 | 1812 | 18-YL-17201F | PP-1701A FAULT |  |  |  | 4 | [11 empty] | 18-YL-17201F |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
390 | 5 | 1812 | 18-YL-17202R | PP-1701B RUN |  |  |  | 5 | [11 empty] | 18-YL-17202R |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
391 | 6 | 1812 | 18-YL-17202F | PP-1701B FAULT |  |  |  | 6 | [11 empty] | 18-YL-17202F |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
392 | 7 | 1812 | 18-YL-17203R | PP-1702A RUN |  |  |  | 7 | [11 empty] | 18-YL-17203R |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
393 | 8 | 1812 | 18-YL-17203F | PP-1702A FAULT |  |  |  | 8 | [11 empty] | 18-YL-17203F |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
394 | 9 | 1812 | 18-YL-17204R | PP-1702B RUN |  |  |  | 9 | [11 empty] | 18-YL-17204R |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
395 | 10 | 1812 | 18-YL-17204F | PP-1702B FAULT |  |  |  | 10 | [11 empty] | 18-YL-17204F |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
396 | 11 | 1812 | 18-YL-17301R | PP-1704 RUN |  |  |  | 11 | [11 empty] | 18-YL-17301R |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
397 | 12 | 1812 | 18-YL-17301F | PP-1704 FAULT |  |  |  | 12 | [11 empty] | 18-YL-17301F |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
398 | 13 | 1812 | 18-YL-17109R | PP-1705 RUN |  |  |  | 13 | [11 empty] | 18-YL-17109R |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
399 | 14 | 1812 | 18-YL-17109F | PP-1705 FAULT |  |  |  | 14 | [11 empty] | 18-YL-17109F |  | RE | DCS | [12 empty] | MCC | [31 empty] | 1 | 1812
400 | 15 | 1830 | 18-XHSO-21101 | PEROXIDE FROM PP-2102 |  |  |  | 15 | [11 empty] | 18-XHSO-21101 |  | RE | DCS | [11 empty] | 18-EJB-30-023 | 18-30-023-CC | [31 empty] | - | 1830
401 | 16 | 1830 | 18-XHSC-21101 | PEROXIDE FROM PP-2102 |  |  |  | 16 | [11 empty] | 18-XHSC-21101 |  | RE | DCS | [11 empty] | 18-EJB-30-023 | 18-30-023-CC | [31 empty] | - | 1830
402 | 17 | 1830 | 18-XHSO-24102 | LIQUID ADDITIVES VE-2401 |  |  |  | 17 | [11 empty] | 18-XHSO-24102 |  | RE | DCS | [11 empty] | 18-EJB-30-025 | 18-30-025-CC | [31 empty] | - | 1830
403 | 18 | 1830 | 18-XHSC-24102 | LIQUID ADDITIVES VE-2401 |  |  |  | 18 | [11 empty] | 18-XHSC-24102 |  | RE | DCS | [11 empty] | 18-EJB-30-025 | 18-30-025-CC | [31 empty] | - | 1830
404 | 19 | 1830 | 18-XHSO-66101 | - |  |  |  | 19 | [11 empty] | 18-XHSO-66101 |  | RE | DCS | [11 empty] | 18-EJB-30-023 | 18-30-023-CC | [31 empty] | - | 1830
405 | 20 | 1830 | 18-XHSC-66101 | - |  |  |  | 20 | [11 empty] | 18-XHSC-66101 |  | RE | DCS | [11 empty] | 18-EJB-30-023 | 18-30-023-CC | [31 empty] | - | 1830
406 | 21 |  |  | Spare |  |  |  | 21 | [13 empty] | RE | DCS
407 | 22 |  |  | Spare |  |  |  | 22 | [13 empty] | RE | DCS
408 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | RE | DCS
409 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | RE | DCS
410 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | RE | DCS
411 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | RE | DCS
412 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | RE | DCS
413 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | RE | DCS
414 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | RE | DCS
415 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | RE | DCS
416 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | RE | DCS
417 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | RE | DCS
418 | 1 | 1840 | 18-PN-62104 | - |  | 9 | 7 | 1 | ADV551-P |  |  |  | Y | [6 empty] | 18-PN-62104 |  | 24V | DCS | [11 empty] | 18-EJB-40-001 | 18-40-001-CC | [31 empty] | - | 1840
419 | 2 | 1840 | 18-XN-61105 | - |  |  |  | 2 | [11 empty] | 18-XN-61105 |  | 24V | DCS | [11 empty] | 18-EJB-40-001 | 18-40-001-CC | [31 empty] | - | 1840
420 | 3 | 1840 | 18-XN-61201 | - |  |  |  | 3 | [11 empty] | 18-XN-61201 |  | 24V | DCS | [11 empty] | 18-EJB-40-001 | 18-40-001-CC | [31 empty] | - | 1840
421 | 4 | 1840 | 18-XN-61206 | - |  |  |  | 4 | [11 empty] | 18-XN-61206 |  | 24V | DCS | [11 empty] | 18-EJB-40-001 | 18-40-001-CC | [31 empty] | - | 1840
422 | 5 | 1840 | 18-XN-62106 | - |  |  |  | 5 | [11 empty] | 18-XN-62106 |  | 24V | DCS | [11 empty] | 18-EJB-40-001 | 18-40-001-CC | [31 empty] | - | 1840
423 | 6 | 1840 | 18-XN-62301 | - |  |  |  | 6 | [11 empty] | 18-XN-62301 |  | 24V | DCS | [11 empty] | 18-EJB-40-001 | 18-40-001-CC | [31 empty] | - | 1840
424 | 7 | 1840 | 18-XN-62302 | - |  |  |  | 7 | [11 empty] | 18-XN-62302 |  | 24V | DCS | [11 empty] | 18-EJB-40-001 | 18-40-001-CC | [31 empty] | - | 1840
425 | 8 | 1812 | 18-XN-17101 | LP N2 FROM HEADER |  |  |  | 8 | [11 empty] | 18-XN-17101 |  | 24V | DCS | [11 empty] | 18-EJB-12-002 | 18-12-002-CC | [31 empty] | - | 1812
426 | 9 | 1812 | 18-XN-17102 | LP NITROGEN TO VE-1701 |  |  |  | 9 | [11 empty] | 18-XN-17102 |  | 24V | DCS | [11 empty] | 18-EJB-12-002 | 18-12-002-CC | [31 empty] | - | 1812
427 | 10 | 1812 | 18-XN-17103 | LP NITROGEN TO VE-1702 |  |  |  | 10 | [11 empty] | 18-XN-17103 |  | 24V | DCS | [11 empty] | 18-EJB-12-002 | 18-12-002-CC | [31 empty] | - | 1812
428 | 11 | 1812 | 18-XN-17104 | TEA TO VE-1701 |  |  |  | 11 | [11 empty] | 18-XN-17104 |  | 24V | DCS | [11 empty] | 18-EJB-12-002 | 18-12-002-CC | [31 empty] | - | 1812
429 | 12 | 1812 | 18-XN-17105 | TEA CONTAINER |  |  |  | 12 | [11 empty] | 18-XN-17105 |  | 24V | DCS | [11 empty] | 18-EJB-12-002 | 18-12-002-CC | [31 empty] | - | 1812
430 | 13 | 1812 | 18-XN-17106 | FLUSHING TO VE-1705 |  |  |  | 13 | [11 empty] | 18-XN-17106 |  | 24V | DCS | [11 empty] | 18-EJB-12-002 | 18-12-002-CC | [31 empty] | - | 1812
431 | 14 | 1812 | 18-XN-17107 | ISOPROPANOL TO VE-1705 |  |  |  | 14 | [11 empty] | 18-XN-17107 |  | 24V | DCS | [11 empty] | 18-EJB-12-002 | 18-12-002-CC | [31 empty] | - | 1812
432 | 15 | 1812 | 18-XN-17111 | White Oil to VE-1701 |  |  |  | 15 | [11 empty] | 18-XN-17111 |  | 24V | DCS | [11 empty] | 18-EJB-12-002 | 18-12-002-CC | [31 empty] | - | 1812
433 | 16 | 1830 | 18-PN-66102 | VACUUM OFFGAS |  |  |  | 16 | [11 empty] | 18-PN-66102 |  | 24V | DCS | [11 empty] | 18-EJB-30-004 | 18-30-004-CC | [31 empty] | - | 1830
434 | 17 | 1830 | 18-XN-21101 | PX FROM PP-2102toVE-2101 |  |  |  | 17 | [11 empty] | 18-XN-21101 |  | 24V | DCS | [11 empty] | 18-EJB-30-018 | 18-30-018-CC | [31 empty] | - | 1830
435 | 18 | 1830 | 18-XN-21103 | PX FROM VE-2101toPP-2101 |  |  |  | 18 | [11 empty] | 18-XN-21103 |  | 24V | DCS | [11 empty] | 18-EJB-30-018 | 18-30-018-CC | [31 empty] | - | 1830
436 | 19 | 1830 | 18-XN-21104 | FIRE WATERtoPX DOSING |  |  |  | 19 | [11 empty] | 18-XN-21104 |  | 24V | DCS | [11 empty] | 18-EJB-30-018 | 18-30-018-CC | [31 empty] | - | 1830
437 | 20 | 1830 | 18-XN-23101 | ADD. VE-2301 TO VE-2302 |  |  |  | 20 | [11 empty] | 18-XN-23101 |  | 24V | DCS | [11 empty] | 18-EJB-30-004 | 18-30-004-CC | [31 empty] | - | 1830
438 | 21 | 1830 | 18-XN-24102 | PP-2402 DISCHARGE |  |  |  | 21 | [11 empty] | 18-XN-24102 |  | 24V | DCS | [11 empty] | 18-EJB-30-004 | 18-30-004-CC | [31 empty] | - | 1830
439 | 22 | 1830 | 18-XN-36101A | PEROXIDE TO PJ-3601X |  |  |  | 22 | [11 empty] | 18-XN-36101A |  | 24V | DCS | [11 empty] | 18-EJB-30-004 | 18-30-004-CC | [31 empty] | 3 | 1830
440 | 23 | 1830 | 18-XN-36102A | PEROXIDE TO PJ-3601X |  |  |  | 23 | [11 empty] | 18-XN-36102A |  | 24V | DCS | [11 empty] | 18-EJB-30-004 | 18-30-004-CC | [31 empty] | 3 | 1830
441 | 24 | 1830 | 18-XN-66101 | OFFGAS TO ET-6602 |  |  |  | 24 | [11 empty] | 18-XN-66101 |  | 24V | DCS | [11 empty] | 18-EJB-30-004 | 18-30-004-CC | [31 empty] | - | 1830
442 | 25 | 1830 | 18-XN-66105 | - |  |  |  | 25 | [11 empty] | 18-XN-66105 |  | 24V | DCS | [11 empty] | 18-6601-DJB-0002 | DCS | [31 empty] | - | 1830
443 | 26 | 1830 | 18-XN-66106 | - |  |  |  | 26 | [11 empty] | 18-XN-66106 |  | 24V | DCS | [11 empty] | 18-6601-DJB-0002 | DCS | [31 empty] | - | 1830
444 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | 24V | DCS
445 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | 24V | DCS
446 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | 24V | DCS
447 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | 24V | DCS
448 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | 24V | DCS
449 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | 24V | DCS
450 | 1 | 1830 | 18-YL-21103R | 18-PP-2101 RUN |  | 10 | 3 | 1 | ADV151-P |  |  |  | N | [6 empty] | 18-YL-21103R |  | RE | DCS | [44 empty] | 2 | 1830
451 | 2 | 1830 | 18-YL-21103F | 18-PP-2101 FAULT |  |  |  | 2 | [11 empty] | 18-YL-21103F |  | RE | DCS | [44 empty] | 2 | 1830
452 | 3 | 1830 | 18-YL-21104R | 18-PP-2102 RUN |  |  |  | 3 | [11 empty] | 18-YL-21104R |  | RE | DCS | [44 empty] | 2 | 1830
453 | 4 | 1830 | 18-YL-21104F | 18-PP-2102 FAULT |  |  |  | 4 | [11 empty] | 18-YL-21104F |  | RE | DCS | [44 empty] | 2 | 1830
454 | 5 | 1830 | 18-YL-21102L | 18-PB-2101 REMOTE |  |  |  | 5 | [11 empty] | 18-YL-21102L |  | RE | DCS | [44 empty] | 2 | 1830
455 | 6 | 1830 | 18-YL-21102R | 18-PB-2101 RUN |  |  |  | 6 | [11 empty] | 18-YL-21102R |  | RE | DCS | [44 empty] | 2 | 1830
456 | 7 | 1830 | 18-YL-21102F | 18-PB-2101 FAULT |  |  |  | 7 | [11 empty] | 18-YL-21102F |  | RE | DCS | [44 empty] | 2 | 1830
457 | 8 | 1830 | 18-YL-23101L | 18-PP-2301A REMOTE |  |  |  | 8 | [11 empty] | 18-YL-23101L |  | RE | DCS | [44 empty] | 2 | 1830
458 | 9 | 1830 | 18-YL-23101R | 18-PP-2301A RUNNING |  |  |  | 9 | [11 empty] | 18-YL-23101R |  | RE | DCS | [44 empty] | 2 | 1830
459 | 10 | 1830 | 18-YL-23101F | 18-PP-2301A FAULT |  |  |  | 10 | [11 empty] | 18-YL-23101F |  | RE | DCS | [44 empty] | 2 | 1830
460 | 11 | 1830 | 18-YL-23102F | 18-PP-2301B FAULT |  |  |  | 11 | [11 empty] | 18-YL-23102F |  | RE | DCS | [44 empty] | 2 | 1830
461 | 12 | 1830 | 18-YL-23102L | 18-PP-2301B REMOTE |  |  |  | 12 | [11 empty] | 18-YL-23102L |  | RE | DCS | [44 empty] | 2 | 1830
462 | 13 | 1830 | 18-YL-23102R | 18-PP-2301B RUNNING |  |  |  | 13 | [11 empty] | 18-YL-23102R |  | RE | DCS | [44 empty] | 2 | 1830
463 | 14 | 1830 | 18-YL-23105L | 18-PA-2301 REMOTE |  |  |  | 14 | [11 empty] | 18-YL-23105L |  | RE | DCS | [44 empty] | 2 | 1830
464 | 15 | 1830 | 18-YL-23105R | 18-PA-2301 RUN |  |  |  | 15 | [11 empty] | 18-YL-23105R |  | RE | DCS | [44 empty] | 2 | 1830
465 | 16 | 1830 | 18-YL-23105F | 18-PA-2301 FAULT |  |  |  | 16 | [11 empty] | 18-YL-23105F |  | RE | DCS | [44 empty] | 2 | 1830
466 | 17 | 1830 | 18-YL-24101L | 18-PP-2401 REMOTE |  |  |  | 17 | [11 empty] | 18-YL-24101L |  | RE | DCS | [44 empty] | 2 | 1830
467 | 18 | 1830 | 18-YL-24101R | 18-PP-2401 RUN |  |  |  | 18 | [11 empty] | 18-YL-24101R |  | RE | DCS | [44 empty] | 2 | 1830
468 | 19 | 1830 | 18-YL-24101F | 18-PP-2401 FAULT |  |  |  | 19 | [11 empty] | 18-YL-24101F |  | RE | DCS | [44 empty] | 2 | 1830
469 | 20 | 1830 | 18-YL-36106L | 18-PF-3606 REMOTE |  |  |  | 20 | [11 empty] | 18-YL-36106L |  | RE | DCS | [44 empty] | 3 | 1830
470 | 21 | 1830 | 18-YL-36106R | 18-PF-3606 RUN |  |  |  | 21 | [11 empty] | 18-YL-36106R |  | RE | DCS | [44 empty] | 3 | 1830
471 | 22 | 1830 | 18-YL-36106F | 18-PF-3606 FAULT |  |  |  | 22 | [11 empty] | 18-YL-36106F |  | RE | DCS | [44 empty] | 3 | 1830
472 | 23 | 1830 | 18-YL-66101L | 18-PV-6601X REMOTE |  |  |  | 23 | [11 empty] | 18-YL-66101L |  | RE | DCS | [44 empty] | 6 | 1830
473 | 24 | 1830 | 18-YL-66101R | 18-PV-6601X RUN |  |  |  | 24 | [11 empty] | 18-YL-66101R |  | RE | DCS | [44 empty] | 6 | 1830
474 | 25 | 1830 | 18-YL-66101F | 18-PV-6601X FAULT |  |  |  | 25 | [11 empty] | 18-YL-66101F |  | RE | DCS | [44 empty] | 6 | 1830
475 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | RE | DCS
476 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | RE | DCS
477 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | RE | DCS
478 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | RE | DCS
479 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | RE | DCS
480 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | RE | DCS
481 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | RE | DCS
482 | 1 | 1830 | 18-YL-92101L | 18-PP-9201A REMOTE |  | 10 | 4 | 1 | ADV151-P |  |  |  | N | [6 empty] | 18-YL-92101L |  | RE | DCS | [44 empty] | 9 | 1830
483 | 2 | 1830 | 18-YL-92101R | 18-PP-9201A RUN |  |  |  | 2 | [11 empty] | 18-YL-92101R |  | RE | DCS | [44 empty] | 9 | 1830
484 | 3 | 1830 | 18-YL-92101F | 18-PP-9201A FAULT |  |  |  | 3 | [11 empty] | 18-YL-92101F |  | RE | DCS | [44 empty] | 9 | 1830
485 | 4 | 1830 | 18-YL-92102L | 18-PP-9201B REMOTE |  |  |  | 4 | [11 empty] | 18-YL-92102L |  | RE | DCS | [44 empty] | 9 | 1830
486 | 5 | 1830 | 18-YL-92102R | 18-PP-9201B RUN |  |  |  | 5 | [11 empty] | 18-YL-92102R |  | RE | DCS | [44 empty] | 9 | 1830
487 | 6 | 1830 | 18-YL-92102F | 18-PP-9201B FAULT |  |  |  | 6 | [11 empty] | 18-YL-92102F |  | RE | DCS | [44 empty] | 9 | 1830
488 | 7 | 1830 | 18-YL-35103RN | 排气过滤器18-FL3501X反吹 |  |  |  | 7 | [11 empty] | 18-YL-35103RN |  | RE | DCS | [12 empty] | 无电缆信息 | [31 empty] | 5 | 1830
489 | 8 | 1830 | 18-LHS-35103REM | 排气过滤器18-FL3501X远程 |  |  |  | 8 | [11 empty] | 18-LHS-35103REM |  | RE | DCS | [12 empty] | 无电缆信息 | [31 empty] | 1 | 1830
490 | 9 | 1830 | 18-PASL-35203 | 输送氮气风机3501AX入压低 |  |  |  | 9 | [11 empty] | 18-PSAL-35203 |  | RE | DCS | [44 empty] | - | 1830
491 | 10 | 1830 | 18-TASH-35202 | 输送氮气风机3501AX出温高 |  |  |  | 10 | [11 empty] | 18-TSAH-35202 |  | RE | DCS | [11 empty] | 18-3501-DJB-0013 | DCS | [31 empty] | - | 1830
492 | 11 | 1830 | 18-PASH-35202 | 输送氮气风机3501AX出压高 |  |  |  | 11 | [11 empty] | 18-PSAH-35202 |  | RE | DCS | [11 empty] | 18-3501-DJB-0013 | DCS | [31 empty] | - | 1830
493 | 12 | 1830 | 18-PASL-35213 | 输送氮气风机3501BX入压低 |  |  |  | 12 | [11 empty] | 18-PSAL-35213 |  | RE | DCS | [11 empty] | 18-3501-DJB-0013 | DCS | [31 empty] | - | 1830
494 | 13 | 1830 | 18-TASH-35212 | 输送氮气风机3501BX出温高 |  |  |  | 13 | [11 empty] | 18-TSAH-35212 |  | RE | DCS | [11 empty] | 18-3501-DJB-0013 | DCS | [31 empty] | - | 1830
495 | 14 | 1830 | 18-PASH-35212 | 输送氮气风机3501BX出压高 |  |  |  | 14 | [11 empty] | 18-PSAL-35212 |  | RE | DCS | [11 empty] | 18-3501-DJB-0013 | DCS | [31 empty] | - | 1830
496 | 15 | 1830 | 18-YL-35201L | 输送氮气风机3501AX远程 |  |  |  | 15 | [11 empty] | 18-YL-35201L |  | RE | DCS | [44 empty] | 3 | 1830
497 | 16 | 1830 | 18-YL-35201R | 输送氮气风机3501AX运行 |  |  |  | 16 | [11 empty] | 18-YL-35201R |  | RE | DCS | [44 empty] | 3 | 1830
498 | 17 | 1830 | 18-YL-35201F | 输送氮气风机3501AX故障 |  |  |  | 17 | [11 empty] | 18-YL-35201F |  | RE | DCS | [44 empty] | 3 | 1830
499 | 18 | 1830 | 18-YL-35202L | 输送氮气风机3501BX远程 |  |  |  | 18 | [11 empty] | 18-YL-35202L |  | RE | DCS | [44 empty] | 3 | 1830
500 | 19 | 1830 | 18-YL-35202R | 输送氮气风机3501BX运行 |  |  |  | 19 | [11 empty] | 18-YL-35202R |  | RE | DCS | [44 empty] | 3 | 1830
501 | 20 | 1830 | 18-YL-35202F | 输送氮气风机3501BX故障 |  |  |  | 20 | [11 empty] | 18-YL-35202F |  | RE | DCS | [44 empty] | 3 | 1830
502 | 21 | 1830 | 18-YL-35102R | 粉料循环旋转阀3502X运行 |  |  |  | 21 | [11 empty] | 18-YL-35102R |  | RE | DCS | [44 empty] | 3 | 1830
503 | 22 | 1830 | 18-YL-35102F | 粉料循环旋转阀3502X故障 |  |  |  | 22 | [11 empty] | 18-YL-35102F |  | RE | DCS | [44 empty] | 3 | 1830
504 | 23 | 1830 | 18-YL-35102L | 粉料循环旋转阀3502X远程 |  |  |  | 23 | [11 empty] | 18-YL-35102L |  | RE | DCS | [44 empty] | 3 | 1830
505 | 24 | 1830 | 18-YLF-35101R | 粉料仓旋转阀3501X正转 |  |  |  | 24 | [11 empty] | 18-YLF-35101R |  | RE | DCS | [44 empty] | 3 | 1830
506 | 25 | 1830 | 18-YLR-35101R | 粉料仓旋转阀3501X反转 |  |  |  | 25 | [11 empty] | 18-YLR-35101R |  | RE | DCS | [44 empty] | 3 | 1830
507 | 26 | 1830 | 18-YL-35101F | 粉料仓旋转阀3501X故障 |  |  |  | 26 | [11 empty] | 18-YL-35101F |  | RE | DCS | [44 empty] | 3 | 1830
508 | 27 | 1830 | 18-YL-35101L | 粉料仓旋转阀3501X远程 |  |  |  | 27 | [11 empty] | 18-YL-35101L |  | RE | DCS | [44 empty] | 3 | 1830
509 | 28 | 1830 | 18-YL-35111R | 粉料仓旋转阀3501X风扇运 |  |  |  | 28 | [11 empty] | 18-YL-35111R |  | RE | DCS | [44 empty] | 3 | 1830
510 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | RE | DCS
511 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | RE | DCS
512 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | RE | DCS
513 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | RE | DCS
514 | 1 | 1812 | 18-UL-17110B | TEA CONTAINER SEQUENCE |  | 10 | 7 | 1 | ADV551-P |  |  |  | N | [6 empty] | 18-UL-17110B |  | 24V | DCS | [11 empty] | LCP-1 | 18-LCP-1-CC1 | [31 empty] | 1 | 1812
515 | 2 | 1812 | 18-XL-17121 | TEA CONTAINER TO CHANGE |  |  |  | 2 | [11 empty] | 18-UL-17121 |  | 24V | DCS | [11 empty] | LCP-1 | 18-LCP-1-CC1 | [31 empty] | - | 1812
516 | 3 | 1830 | 18-XS-35104 | 控制角座阀XV35104的开/关 |  |  |  | 3 | [11 empty] | 18-XS-35104 |  | 24V | DCS | [11 empty] | 18-3501-DJB-0016 | DCS | [31 empty] | - | 1830
517 | 4 | 1830 | 18-XS-35101 | 控制气动滑板阀XV35101开 |  |  |  | 4 | [11 empty] | 18-XS-35101 |  | 24V | DCS | [12 empty] | 无电缆信息 | [31 empty] | - | 1830
518 | 5 | 1830 | 18-XS-35102 | 控制气动滑板阀XV35102开 |  |  |  | 5 | [11 empty] | 18-XS-35102 |  | 24V | DCS | [12 empty] | 无电缆信息 | [31 empty] | - | 1830
519 | 6 | 1830 | 18-XS-35107 | 控制气动蝶阀XV35107开/关 |  |  |  | 6 | [11 empty] | 18-XS-35107 |  | 24V | DCS | [11 empty] | 18-3501-DJB-0016 | DCS | [31 empty] | - | 1830
520 | 7 | 1830 | 18-XS-35201 | 控制气动蝶阀XV35201开/关 |  |  |  | 7 | [11 empty] | 18-XS-35201 |  | 24V | DCS | [11 empty] | 18-3501-DJB-0012 | DCS | [31 empty] | - | 1830
521 | 8 | 1830 | 18-XS-35202 | 控制气动蝶阀XV35202开/关 |  |  |  | 8 | [11 empty] | 18-XS-35202 |  | 24V | DCS | [11 empty] | 18-3501-DJB-0012 | DCS | [31 empty] | - | 1830
522 | 9 | 1830 | 18-XS-35203 | 控制气动蝶阀XV35203开/关 |  |  |  | 9 | [11 empty] | 18-XS-35203 |  | 24V | DCS | [11 empty] | 18-3501-DJB-0012 | DCS | [31 empty] | - | 1830
523 | 10 | 1830 | 18-XS-35204 | 控制气动蝶阀XV35204开/关 |  |  |  | 10 | [11 empty] | 18-XS-35204 |  | 24V | DCS | [11 empty] | 18-3501-DJB-0012 | DCS | [31 empty] | - | 1830
524 | 11 | 1830 | 18-XS-35206 | 控制气动蝶阀XV35206开/关 |  |  |  | 11 | [11 empty] | 18-XS-35206 |  | 24V | DCS | [11 empty] | 18-3501-DJB-0012 | DCS | [31 empty] | - | 1830
525 | 12 |  |  | Spare |  |  |  | 12 | [13 empty] | 24V | DCS
526 | 13 |  |  | Spare |  |  |  | 13 | [13 empty] | 24V | DCS
527 | 14 |  |  | Spare |  |  |  | 14 | [13 empty] | 24V | DCS
528 | 15 |  |  | Spare |  |  |  | 15 | [13 empty] | 24V | DCS
529 | 16 |  |  | Spare |  |  |  | 16 | [13 empty] | 24V | DCS
530 | 17 | 1830 | 18-HS-35103 | 排气过滤器3501X反吹启/停 |  |  |  | 17 | [11 empty] | 18-HS-35103 |  | 24V | DCS | [12 empty] | 无电缆信息 | [31 empty] | - | 1830
531 | 18 |  |  | Spare |  |  |  | 18 | [13 empty] | 24V | DCS
532 | 19 |  |  | Spare |  |  |  | 19 | [13 empty] | 24V | DCS
533 | 20 |  |  | Spare |  |  |  | 20 | [13 empty] | 24V | DCS
534 | 21 |  |  | Spare |  |  |  | 21 | [13 empty] | 24V | DCS
535 | 22 |  |  | Spare |  |  |  | 22 | [13 empty] | 24V | DCS
536 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | 24V | DCS
537 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | 24V | DCS
538 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | 24V | DCS
539 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | 24V | DCS
540 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | 24V | DCS
541 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | 24V | DCS
542 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | 24V | DCS
543 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | 24V | DCS
544 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | 24V | DCS
545 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | 24V | DCS
546 | 1 | 1840 | 18-HS-62101S | 18-PP-6202A START |  | 10 | 8 | 1 | ADV551-P |  |  |  | N | [6 empty] | 18-HS-62101S |  | dry | DCS | [12 empty] | MCC | [31 empty] | - | 1840
547 | 2 | 1840 | 18-HS-62102S | 18-PP-6202B START |  |  |  | 2 | [11 empty] | 18-HS-62102S |  | dry | DCS | [12 empty] | MCC | [31 empty] | - | 1840
548 | 3 | 1830 | 18-HS-21102S | 18-PB-2101 START |  |  |  | 3 | [11 empty] | 18-HS-21102S |  | dry | DCS | [44 empty] | 2 | 1830
549 | 4 | 1830 | 18-HS-23101S | 18-PP-2301A START |  |  |  | 4 | [11 empty] | 18-HS-23101S |  | dry | DCS | [44 empty] | 2 | 1830
550 | 5 | 1830 | 18-HS-23102S | 18-PP-2301B START |  |  |  | 5 | [11 empty] | 18-HS-23102S |  | dry | DCS | [44 empty] | 2 | 1830
551 | 6 | 1830 | 18-HS-23105S | 18-PA-2301 START |  |  |  | 6 | [11 empty] | 18-HS-23105S |  | dry | DCS | [44 empty] | 2 | 1830
552 | 7 | 1830 | 18-HS-24101S | 18-PP-2401 START |  |  |  | 7 | [11 empty] | 18-HS-24101S |  | dry | DCS | [44 empty] | 2 | 1830
553 | 8 | 1830 | 18-HS-36106S | 18-PF-3606 START |  |  |  | 8 | [11 empty] | 18-HS-36106S |  | dry | DCS | [44 empty] | 3 | 1830
554 | 9 | 1830 | 18-HS-66101S | 18-PV-6601X START |  |  |  | 9 | [11 empty] | 18-HS-66101S |  | dry | DCS | [44 empty] | 6 | 1830
555 | 10 | 1830 | 18-HS-92101S | 18-PP-9201A START |  |  |  | 10 | [11 empty] | 18-HS-92101S |  | dry | DCS | [44 empty] | 9 | 1830
556 | 11 | 1830 | 18-HS-92102S | 18-PP-9201B START |  |  |  | 11 | [11 empty] | 18-HS-92102S |  | dry | DCS | [44 empty] | 9 | 1830
557 | 12 | 1830 | 18-HS-35201S | 输送氮气风机3501AX启动 |  |  |  | 12 | [11 empty] | 18-HS-35201S |  | dry | DCS | [44 empty] | 3 | 1830
558 | 13 | 1830 | 18-HS-35201L | 输送氮气风机3501AX允许 |  |  |  | 13 | [11 empty] | 18-HS-35201L |  | dry | DCS | [44 empty] | 3 | 1830
559 | 14 | 1830 | 18-HS-35202S | 输送氮气风机3501BX启动 |  |  |  | 14 | [11 empty] | 18-HS-35202S |  | dry | DCS | [44 empty] | 3 | 1830
560 | 15 | 1830 | 18-HS-35202L | 输送氮气风机3501BX允许 |  |  |  | 15 | [11 empty] | 18-HS-35202L |  | dry | DCS | [44 empty] | 3 | 1830
561 | 16 | 1830 | 18-HS-35102S | 粉料循环旋转阀3502X启动 |  |  |  | 16 | [11 empty] | 18-HS-35102S |  | dry | DCS | [44 empty] | 3 | 1830
562 | 17 | 1830 | 18-HSF-35101S | 粉料仓旋转阀3501X的正转 |  |  |  | 17 | [11 empty] | 18-HSF-35101S |  | dry | DCS | [44 empty] | 3 | 1830
563 | 18 | 1830 | 18-HSR-35101S | 粉料仓旋转阀3501X的反转 |  |  |  | 18 | [11 empty] | 18-HSR-35101S |  | dry | DCS | [44 empty] | 3 | 1830
564 | 19 |  |  | Spare |  |  |  | 19 | [13 empty] | dry | DCS
565 | 20 |  |  | Spare |  |  |  | 20 | [13 empty] | dry | DCS
566 | 21 |  |  | Spare |  |  |  | 21 | [13 empty] | dry | DCS
567 | 22 |  |  | Spare |  |  |  | 22 | [13 empty] | dry | DCS
568 | 23 |  |  | Spare |  |  |  | 23 | [13 empty] | dry | DCS
569 | 24 |  |  | Spare |  |  |  | 24 | [13 empty] | dry | DCS
570 | 25 |  |  | Spare |  |  |  | 25 | [13 empty] | dry | DCS
571 | 26 |  |  | Spare |  |  |  | 26 | [13 empty] | dry | DCS
572 | 27 |  |  | Spare |  |  |  | 27 | [13 empty] | dry | DCS
573 | 28 |  |  | Spare |  |  |  | 28 | [13 empty] | dry | DCS
574 | 29 |  |  | Spare |  |  |  | 29 | [13 empty] | dry | DCS
575 | 30 |  |  | Spare |  |  |  | 30 | [13 empty] | dry | DCS
576 | 31 |  |  | Spare |  |  |  | 31 | [13 empty] | dry | DCS
577 | 32 |  |  | Spare |  |  |  | 32 | [13 empty] | dry | DCS

## Sheet1
PID_TAG | COMMENT | TGCOMM
18-PT-62302 | 李强测试1 | 李强测试1

## I_O List
LOOP NO1 | PID_TAG | INSTRUMENT TYPE | COMMENT | P&IDNO | DCSTAG1 | 信号类型1 | REDUN1 | SIGNAL1 | SIGNAL |  | QTY | Signal_Detail | IS-BARRIER | IS_Non_IS | CARD#/RACK# | REMARKS |  | JB_CABLE_NM1 | J.B.NAME1 |  | LOOP NO | DCSTAG1
1840 | 18-TT-61102 | Integral Temperature Transmitter | GC TO TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61103 | Integral Temperature Transmitter | GC FROM TA-6101 TOP TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-016-iSC | 18-IJB-40-016 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61104 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61105 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC., CONTR. | 1840-PS07-611 | TIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AIR-IS | 1840 |  |  | -
1840 | 18-TT-61106 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61107 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61108 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61109 | Integral Temperature Transmitter | GC FROM ET-6101 TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61110 | Integral Temperature Transmitter | HCS FROM TA-6101 BOTTOM TEMP. INDIC. | 1840-PS07-611 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-002-iSC | 18-IJB-40-002 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61201 | Integral Temperature Transmitter | ETH TO ET-6103 TEMP. INDIC. | 1840-PS07-612 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-016-iSC | 18-IJB-40-016 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61203 | Integral Temperature Transmitter | ETH TO VE-6103 TEMP. INDIC. | 1840-PS07-612 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-006-iSC | 18-IJB-40-006 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61205 | Integral Temperature Transmitter | TA-6102 TEMP. INDIC. | 1840-PS07-612 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-007-iSC | 18-IJB-40-007 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61206 | Integral Temperature Transmitter | TA-6102 TEMP. INDIC. | 1840-PS07-612 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-007-iSC | 18-IJB-40-007 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61207 | Integral Temperature Transmitter | TA-6102 TEMP. INDIC., CONTR., ALARM | 1840-PS07-612 | TICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-007-iSC | 18-IJB-40-007 | AIR-IS | 1840 |  |  | -
1840 | 18-TT-61208 | Integral Temperature Transmitter | GC TO OSBL TEMP. INDIC., ALARM | 1840-PS07-612 | TIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AI-IS | 1840 |  |  | -
1840 | 18-TT-61209 | Integral Temperature Transmitter | ETH FROM ET-6103 TEMP. NDIC., ALARM | 1840-PS07-612 | TIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-016-iSC | 18-IJB-40-016 | AI-IS | 1840 |  |  | -
1840 | 18-TT-62101 | Integral Temperature Transmitter | TA-6201 TEMP. INDIC. | 1840-PS07-621 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AI-IS | 1840 |  |  | -
1840 | 18-TT-62102 | Integral Temperature Transmitter | TA-6201 TEMP. INDIC. | 1840-PS07-621 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AI-IS | 1840 |  |  | -
1840 | 18-TT-62103 | Integral Temperature Transmitter | TA-6201 TEMP. INDIC. | 1840-PS07-621 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AI-IS | 1840 |  |  | -
1840 | 18-TT-62104 | Integral Temperature Transmitter | TA-6201 TEMP. INDIC. | 1840-PS07-621 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AI-IS | 1840 |  |  | -
1840 | 18-TT-62107 | Integral Temperature Transmitter | PR TO VE-6202 TEMP. INDIC. | 1840-PS07-621 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-006-iSC | 18-IJB-40-006 | AI-IS | 1840 |  |  | -
1840 | 18-TT-62108 | Integral Temperature Transmitter | P TO VE-6203 TEMP. INDIC. | 1840-PS07-621 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-006-iSC | 18-IJB-40-006 | AI-IS | 1840 |  |  | -
1840 | 18-TT-62202 | Integral Temperature Transmitter | PR TO ET-6201 TEMP. INDIC., CONTR. | 1840-PS07-622 | TIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-010-iSC | 18-IJB-40-010 | AIR-IS | 1840 |  |  | -
1840 | 18-TT-62203 | Integral Temperature Transmitter | PR TO VE-6201 TEMP. INDIC. | 1840-PS07-622 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-006-iSC | 18-IJB-40-006 | AI-IS | 1840 |  |  | -
1840 | 18-TT-62205 | Integral Temperature Transmitter | PR TO PC-6201 TEMP. INDIC., ALA., INTERL. | 1840-PS07-622 | TISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AIR-IS | 1840 |  |  | -
1840 | 18-TT-62301 | Integral Temperature Transmitter | VE-6203 TEMP. INDIC. | 1840-PS07-623 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-002-iSC | 18-IJB-40-002 | AI-IS | 1840 |  |  | -
1840 | 18-TT-62302 | Integral Temperature Transmitter | P FROM VE-6203 TEMP. INDIC. | 1840-PS07-623 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-001-iSC | 18-IJB-40-001 | AI-IS | 1840 |  |  | -
1840 | 18-TT-63101 | Integral Temperature Transmitter | COOL. TO ET-6301 TEMP. INDIC., ALARM | 1840-PS07-631 | TIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-010-iSC | 18-IJB-40-010 | AI-IS | 1840 |  |  | -
1840 | 18-PT-61103 | Pressure Transmitter | GC TO TA-6101 PRES. INDIC., CONTR., ALA. | 1840-PS07-611 | PICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-015-iSC | 18-IJB-40-015 | AIR-IS | 1840 |  |  | -
1840 | 18-PT-61108 | Pressure Transmitter | LLS TO ET-6101 PRES. INDI., ALA., INTER. | 1840-PS07-611 | PISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AIR-IS | 1840 |  |  | -
1840 | 18-PT-61109 | Pressure Transmitter | GC TO TA-6106 PRES. INDIC., CONTR., ALA. | 1840-PS07-611 | PICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AIR-IS | 1840 |  |  | -
1840 | 18-PT-61202 | Pressure Transmitter | COOL. FROM ET-6102 PRES. INDIC., CONTR. | 1840-PS07-612 | PIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AIR-IS | 1840 |  |  | -
1840 | 18-PT-61204 | Pressure Transmitter | GC ENDS TO ET-6105 PRES. INDIC., CONTR. | 1840-PS07-612 | PIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AIR-IS | 1840 |  |  | -
1840 | 18-PT-61210 | Pressure Transmitter | COOL. FROM ET-6104 PRES. INDIC., CONTR. | 1840-PS07-612 | PIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-010-iSC | 18-IJB-40-010 | AIR-IS | 1840 |  |  | -
1840 | 18-PT-62103 | Pressure Transmitter | TA-6201 BOTTOM PRES. INDIC. | 1840-PS07-621 | PI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-010-iSC | 18-IJB-40-010 | AI-IS | 1840 |  |  | -
1840 | 18-PT-62104 | Pressure Transmitter | VE-6202 TOP PRES. INDIC., CONTR., ALA. | 1840-PS07-621 | PICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AIR-IS | 1840 |  |  | -
1840 | 18-PT-62202 | Pressure Transmitter | PR TO VE-6201 PRES. INDIC., CONTR. ALA., INTERL. | 1840-PS07-622 | PICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-006-iSC | 18-IJB-40-006 | AIR-IS | 1840 |  |  | -
1840 | 18-PT-62301 | Pressure Transmitter With Diaphragm Seal | VE-6203 TO P PRES. INDIC.,CONTR. ALA. | 1840-PS07-623 | PICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 无电缆信息 |  | AIR-IS | 1840 |  |  | -
1840 | 18-PT-62302 | Pressure Transmitter | LLS TO ET-6203 PRES. INDIC., ALA., INTERL. | 1840-PS07-623 | PISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-001-iSC | 18-IJB-40-001 | AIR-IS | 1840 |  |  | -
1840 | 18-PT-62303 | Pressure Transmitter | P TO POSM PRES. INDIC. | 1840-PS07-623 | PI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-001-iSC | 18-IJB-40-001 | AI-IS | 1840 |  |  | -
1840 | 18-PT-63104 | Pressure Transmitter With Diaphragm Seal | VE-6303 PRES. INDIC., CONTR. ALA. | 1840-PS07-631 | PICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-016-iSC | 18-IJB-40-016 | AIR-IS | 1840 |  |  | -
1840 | 18-PDT-61104 | D/P Transmitter | TA-6101 PRES.DIFFER. INDIC., ALARNM | 1840-PS07-611 | PDIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 防雷仪表 |  | AI-IS | 1840 |  |  | -
1840 | 18-PDT-61211 | D/P Transmitter | TA-6102 PRES.DIFFER. INDIC., ALARM | 1840-PS07-612 | PDIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-016-iSC | 18-IJB-40-016 | AI-IS | 1840 |  |  | -
1840 | 18-PDT-62101 | D/P Transmitter | TA-6201 PRES.DIFFER. INDIC., ALARM | 1840-PS07-621 | PDIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 防雷仪表 |  | AI-IS | 1840 |  |  | -
1840 | 18-PDT-62108 | D/P Transmitter With Diaphragm Seal | PR TO ET-3101 PRES.DIFFER. INDIC., ALA., INTERL. | 1840-PS07-621 | PDISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-006-iSC | 18-IJB-40-006 | AIR-IS | 1840 |  |  | -
1840 | 18-FT-61101 | VORTEX FLOWMETER | GC TO TA-6101 FLOW | 1840-PS07-611 | FIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AI-IS | 1840 |  |  | -
1840 | 18-FT-61103 | VORTEX FLOWMETER | GC TO TA-6101 FLOW | 1840-PS07-611 | FICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AIR-IS | 1840 |  |  | -
1840 | 18-FT-61104 | VORTEX FLOWMETER | LLS TO ET-6101 FLOW | 1840-PS07-611 | FICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AIR-IS | 1840 |  |  | -
1840 | 18-FT-61201 | VORTEX FLOWMETER | RECO. ETHY. TO TA-6102 FLOW | 1840-PS07-612 | FIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-007-iSC | 18-IJB-40-007 | AIR-IS | 1840 |  |  | -
1840 | 18-FT-61202 | VORTEX FLOWMETER | HCS TO TA-6101 FLOW | 1840-PS07-612 | FIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-011-iSC | 18-IJB-40-011 | AIR-IS | 1840 |  |  | -
1840 | 18-FT-61205 | Coriolis Mass Flowmeter | GC TO ET-6105 FLOW INDICA., ALARM | 1840-PS07-612 | FIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 18-40-003-SC | 18-EJB-40-003 | AI-NIS | 1840 |  |  | -
1840 | 18-FT-61206 | Coriolis Mass Flowmeter | C2 OFFSPEC TO OSBL FLOW | 1840-PS07-612 | FI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 18-40-003-SC | 18-EJB-40-003 | AI-NIS | 1840 |  |  | -
1840 | 18-FT-62101 | VORTEX FLOWMETER | C3 HCS TO TA-6201 FLOW | 1840-PS07-621 | FIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-002-iSC | 18-IJB-40-002 | AIR-IS | 1840 |  |  | -
1840 | 18-FT-62103 | VORTEX FLOWMETER | C3 HCS TO TA-6201 REFL. FLOW | 1840-PS07-621 | FIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-002-iSC | 18-IJB-40-002 | AIR-IS | 1840 |  |  | -
1840 | 18-FT-62104 | Coriolis Mass Flowmeter | P TO VE-6203 FLOW | 1840-PS07-621 | FICQA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 18-40-003-SC | 18-EJB-40-003 | AIR-NIS | 1840 |  |  | -
1840 | 18-FT-62105 | Coriolis Mass Flowmeter | PR TO ET-3101 FLOW | 1840-PS07-621 | FICQ | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 18-40-003-SC | 18-EJB-40-003 | AIR-NIS | 1840 |  |  | -
1840 | 18-FT-62201 | VORTEX FLOWMETER | PR TO PC-6201 FLOW INDICA. | 1840-PS07-622 | FI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-006-iSC | 18-IJB-40-006 | AI-IS | 1840 |  |  | -
1840 | 18-FT-62202 | VORTEX FLOWMETER | PR TO PC-6201 BYPASS FLOW | 1840-PS07-622 | FI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-016-iSC | 18-IJB-40-016 | AI-IS | 1840 |  |  | -
1840 | 18-FT-62301 | VORTEX FLOWMETER | LLS TO ET-6203 FLOW | 1840-PS07-623 | FICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-001-iSC | 18-IJB-40-001 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-61101 | Displacer Transmitter | 18-VE-6101 | 1840-PS07-611 | LICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-007-iSC | 18-IJB-40-007 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-61103 | Displacer Transmitter | TA-6101 LEVEL INDIC., CONTR., ALA., INTERL. | 1840-PS07-611 | LICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-005-iSC | 18-IJB-40-005 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-61201 | D/P Level Transmitter With Diaphgram Seal | ET-6104 LEVEL INDIC., CONTR., ALA. | 1840-PS07-612 | LICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-010-iSC | 18-IJB-40-010 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-61202 | D/P Level Transmitter With Diaphgram Seal | ET-6102 LEVEL INDIC., CONTR., ALA. | 1840-PS07-612 | LICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-016-iSC | 18-IJB-40-016 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-61203 | Displacer Transmitter | VE-6103 LEVEL INDIC., CONTR., ALA., INTERL. | 1840-PS07-612 | LICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-006-iSC | 18-IJB-40-006 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-61205 | Displacer Transmitter | VE-6102 LEVEL INDIC., CONT., ALA., INTERL. | 1840-PS07-612 | LICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-007-iSC | 18-IJB-40-007 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-62101 | Displacer Transmitter | TA-6201 LEVEL INDIC., CON., ALA., INTERL. | 1840-PS07-621 | LICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-010-iSC | 18-IJB-40-010 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-62105 | Displacer Transmitter | VE-6202 LEVEL INDIC., CON., ALA., INTERL. | 1840-PS07-621 | LICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-006-iSC | 18-IJB-40-006 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-62201 | Displacer Transmitter | VE-6201 LEVEL INDIC., ALA., INTERL. | 1840-PS07-622 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-002-iSC | 18-IJB-40-002 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-62301 | D/P Level Transmitter With Diaphgram Seal | VE-6203 LEVEL INDIC., CON. ALA.INTERL. | 1840-PS07-623 | LICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-002-iSC | 18-IJB-40-002 | AIR-IS | 1840 |  |  | -
1840 | 18-LT-63103 | Displacer Transmitter | VE-6303 LEVEL INDIC., ALAR. | 1840-PS07-631 | LIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-006-iSC | 18-IJB-40-006 | AI-IS | 1840 |  |  | -
1840 | 18-LS-61207 | Tuning Folk | PP-6103 INLET LEVEL SWITCH | 1840-PS07-612 | LSL | DCS-DI | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | 单拉 |  | DIR-RE | 1840 |  |  | -
1840 | 18-TV-62202 | Globe | CWR FROM ET-61202 FOR PR TEMP. CONTR. | 1840-PS07-622 | TV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-017-iSC | 18-IJB-40-017 | AOR-IS | 1840 |  |  | -
1840 | 18-PXV-61103A | Globe | GC TO TA-6101 PRESSURE CONTROL | 1830-PS07-661 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-017-iSC | 18-IJB-40-017 | AOR-IS | 1840 |  |  | 6
1840 | 18-PV-61103B | Globe | CWS FOR TA-6101 PRES. CONTROL | 1830-PS07-661 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-012-iSC | 18-IJB-40-012 | AOR-IS | 1840 |  |  | 6
1840 | 18-PV-61109 | Globe | GC TO FLARE FOR GC TO ET-6106 PRES. CONTR. | 1840-PS07-611 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-012-iSC | 18-IJB-40-012 | AOR-IS | 1840 |  |  | -
1840 | 18-PV-61202 | Globe | COOL. FROM ET-6102 FOR PRES. CONTR. | 1840-PS07-612 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-012-iSC | 18-IJB-40-012 | AOR-IS | 1840 |  |  | -
1840 | 18-PV-61204 | Globe | HCS TO ET-6105 FOR ET-6102 PRES. CONTR. | 1840-PS07-612 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-012-iSC | 18-IJB-40-012 | AOR-IS | 1840 |  |  | -
1840 | 18-PV-61210 | Globe | COOL. FROM ET-6104 FOR ET-6104 PRES. CONTR. | 1840-PS07-612 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-012-iSC | 18-IJB-40-012 | AOR-IS | 1840 |  |  | -
1840 | 18-PV-62104 | Globe | PRE TO FLARE FOR VE-6202 PRES. CONTR. | 1840-PS07-621 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-012-iSC | 18-IJB-40-012 | AOR-IS | 1840 |  |  | -
1840 | 18-PV-62301 | Globe | P TO OSBL PRES. CONTR. | 1840-PS07-623 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-008-iSC | 18-IJB-40-008 | AOR-IS | 1840 |  |  | -
1840 | 18-PV-63104A | Globe | COOL. TO VE-6303 FOR PESS. CONTR. | 1840-PS07-631 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-012-iSC | 18-IJB-40-012 | AOR-IS | 1840 |  |  | 6
1840 | 18-PV-63104B | Globe | COOL. TO FLARE FOR VE-6303 PESS. CONTR. | 1840-PS07-631 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-017-iSC | 18-IJB-40-017 | AOR-IS | 1840 |  |  | 6
1840 | 18-FXV-61103 | Globe | GC TO TA-6101 FLOW CONTROL | 1840-PS07-611 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-008-iSC | 18-IJB-40-008 | AOR-IS | 1840 |  |  | -
1840 | 18-FXV-61104 | Globe | LLS TO ET-6101 FLOW CONTROL | 1840-PS07-611 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-008-iSC | 18-IJB-40-008 | AOR-IS | 1840 |  |  | -
1840 | 18-FV-61201 | Globe | RECOV. ETHY. TO TA-6102 FLOW CONTROL | 1840-PS07-612 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-012-iSC | 18-IJB-40-012 | AOR-IS | 1840 |  |  | -
1840 | 18-FV-61202 | Globe | HCS TO TA-6101 REFLUX FLOW CONTROL | 1840-PS07-612 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-012-iSC | 18-IJB-40-012 | AOR-IS | 1840 |  |  | -
1840 | 18-FXV-62101 | Globe | C3 TO TA-6201 FLOW CONTROL | 1840-PS07-621 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-008-iSC | 18-IJB-40-008 | AOR-IS | 1840 |  |  | -
1840 | 18-FV-62103 | Globe | C3 TO TA-6201 REFLUX FLOW CONTROL | 1840-PS07-621 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-008-iSC | 18-IJB-40-008 | AOR-IS | 1840 |  |  | -
1840 | 18-FV-62104 | Globe | PROPANE FROM TA-6201 FLOW CONTROL | 1840-PS07-621 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-008-iSC | 18-IJB-40-008 | AOR-IS | 1840 |  |  | -
1840 | 18-FV-62105 | Globe | PR TO OSBL TANK FLOW CONTR. | 1840-PS07-621 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-008-iSC | 18-IJB-40-008 | AOR-IS | 1840 |  |  | -
1840 | 18-FV-62301 | Globe | LLS TO ET-6203 FLOW CONTROL | 1840-PS07-623 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-008-iSC | 18-IJB-40-008 | AOR-IS | 1840 |  |  | -
1840 | 18-LV-61201 | Globe | COOL. TO ET-6104 LEVEL CONTROL | 1840-PS07-612 | LV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-012-iSC | 18-IJB-40-012 | AOR-IS | 1840 |  |  | -
1840 | 18-LV-61202 | Globe | COOL. TO ET-6102 LEVEL CONTR. | 1840-PS07-612 | LV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-017-iSC | 18-IJB-40-017 | AOR-IS | 1840 |  |  | -
1840 | 18-LV-61203 | Globe | C2 OFFSPEC TO OSBL FOR VE-6103 LEVEL CONTR. | 1840-PS07-612 | LV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-017-iSC | 18-IJB-40-017 | AOR-IS | 1840 |  |  | -
1840 | 18-PZSL-61103A | Limit Switch | CARRIER GAS TO TA-6101 | 1830-PS07-661 | PZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-013-iCC | 18-IJB-40-013 | DI-MI | 1840 |  |  | 6
1840 | 18-PZSL-61202 | Limit Switch | COOL. FROM ET-6102 FOR PRES. CONTR. | 1840-PS07-612 | PZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-013-iCC | 18-IJB-40-013 | DI-MI | 1840 |  |  | -
1840 | 18-PZSL-61204 | Limit Switch | HCS TO ET-6105 FOR ET-6102 PRES. CONTR. | 1840-PS07-612 | PZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-013-iCC | 18-IJB-40-013 | DI-MI | 1840 |  |  | -
1840 | 18-PZSL-61210 | Limit Switch | COOL. FROM ET-6104 FOR ET-6104 PRES. CONTR. | 1840-PS07-612 | PZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-013-iCC | 18-IJB-40-013 | DI-MI | 1840 |  |  | -
1840 | 18-PZSL-62104 | Limit Switch | HCS TO ET-6105 FOR ET-6102 PRES. CONTR. | 1840-PS07-621 | PZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-013-iCC | 18-IJB-40-013 | DI-MI | 1840 |  |  | -
1840 | 18-FZSL-61103 | Limit Switch | LIQUID FEED TO TA-6101 | 1840-PS07-611 | FZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-004-iCC | 18-IJB-40-004 | DI-MI | 1840 |  |  | -
1840 | 18-FZSL-61104 | Limit Switch | LLP STEAM TO ET-6101 | 1840-PS07-611 | FZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-009-iCC | 18-IJB-40-009 | DI-MI | 1840 |  |  | -
1840 | 18-FZSL-61201 | Limit Switch | RECOV. ETHY. TO TA-6102 FLOW CONTROL | 1840-PS07-612 | FZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-013-iCC | 18-IJB-40-013 | DI-MI | 1840 |  |  | -
1840 | 18-FZSL-61202 | Limit Switch | HCS TO TA-6101 REFLUX FLOW CONTROL | 1840-PS07-612 | FZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-013-iCC | 18-IJB-40-013 | DI-MI | 1840 |  |  | -
1840 | 18-FZSL-62101 | Limit Switch | C3 TO TA-6201 | 1840-PS07-621 | FZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-004-iCC | 18-IJB-40-004 | DI-MI | 1840 |  |  | -
1840 | 18-FZSL-62104 | Limit Switch | PROPANE FROM TA-6201 FLOW CONTROL | 1840-PS07-621 | FZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-009-iCC | 18-IJB-40-009 | DI-MI | 1840 |  |  | -
1840 | 18-FZSL-62105 | Limit Switch | PR TO OSBL TANK FLOW CONTR. | 1840-PS07-621 | FZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-009-iCC | 18-IJB-40-009 | DI-MI | 1840 |  |  | -
1840 | 18-LZSL-61201 | Limit Switch | COOL. TO ET-6104 LEVEL CONTROL | 1840-PS07-612 | LZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-013-iCC | 18-IJB-40-013 | DI-MI | 1840 |  |  | -
1840 | 18-LZSL-61202 | Limit Switch | COOL. TO ET-6102 LEVEL CONTR. | 1840-PS07-612 | LZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-013-iCC | 18-IJB-40-013 | DI-MI | 1840 |  |  | -
1840 | 18-LZSL-61203 | Limit Switch | C2 OFFSPEC TO OSBL FOR VE-6103 LEVEL CONTR. | 1840-PS07-612 | LZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-013-iCC | 18-IJB-40-013 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-61102 | Limit Switch | RECOV. MONOMERS FROM UP-6501 | 1840-PS07-611 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-014-iCC | 18-IJB-40-014 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-61102 | Limit Switch | RECOV. MONOMERS FROM UP-6501 | 1840-PS07-611 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-014-iCC | 18-IJB-40-014 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-61103 | Limit Switch | LIQUID BLEED FROM PP-3201 | 1840-PS07-611 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-014-iCC | 18-IJB-40-014 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-61103 | Limit Switch | LIQUID BLEED FROM PP-3201 | 1840-PS07-611 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-014-iCC | 18-IJB-40-014 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-61104 | Limit Switch | LLP STEAM TO ET-6101 | 1840-PS07-611 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-009-iCC | 18-IJB-40-009 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-61104 | Limit Switch | LLP STEAM TO ET-6101 | 1840-PS07-611 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-009-iCC | 18-IJB-40-009 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-61105 | Limit Switch | LLSC FROM ET-6101 | 1840-PS07-611 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-004-iCC | 18-IJB-40-004 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-61105 | Limit Switch | LLSC FROM ET-6101 | 1840-PS07-611 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-004-iCC | 18-IJB-40-004 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-61106 | Limit Switch | CARRIER GAS TO ET-6106 | 1840-PS07-611 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-014-iCC | 18-IJB-40-014 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-61106 | Limit Switch | CARRIER GAS TO ET-6106 | 1840-PS07-611 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-014-iCC | 18-IJB-40-014 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-61201 | Limit Switch | RECOV. ETHY. TO VE-6103 ON-OFF VALVE | 1840-PS07-612 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-014-iCC | 18-IJB-40-014 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-61201 | Limit Switch | RECOV. ETHY. TO VE-6103 ON-OFF VALVE | 1840-PS07-612 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-014-iCC | 18-IJB-40-014 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-61206 | Limit Switch | C2 OFFSPEC TO OSBL ON-OFF VALVE | 1840-PS07-612 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-014-iCC | 18-IJB-40-014 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-61206 | Limit Switch | C2 OFFSPEC TO OSBL ON-OFF VALVE | 1840-PS07-612 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-014-iCC | 18-IJB-40-014 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-62101 | Limit Switch | C3 TO TA-6201 | 1840-PS07-621 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-004-iCC | 18-IJB-40-004 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-62101 | Limit Switch | C3 TO TA-6201 | 1840-PS07-621 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-004-iCC | 18-IJB-40-004 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-62105 | Limit Switch | PRTO ET-3101 ON-OFF VALVE | 1840-PS07-621 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-009-iCC | 18-IJB-40-009 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-62105 | Limit Switch | PRTO ET-3101 ON-OFF VALVE | 1840-PS07-621 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-009-iCC | 18-IJB-40-009 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-62106 | Limit Switch | RECO. PR FROM VE-6202 ON-OFF VALVE | 1840-PS07-621 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-009-iCC | 18-IJB-40-009 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-62106 | Limit Switch | RECO. PR FROM VE-6202 ON-OFF VALVE | 1840-PS07-621 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-009-iCC | 18-IJB-40-009 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-62301 | Limit Switch | LLS TO ET-6203 ON-OFF VALVE | 1840-PS07-623 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-003-iCC | 18-IJB-40-003 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-62301 | Limit Switch | LLS TO ET-6203 ON-OFF VALVE | 1840-PS07-623 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-003-iCC | 18-IJB-40-003 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-62302 | Limit Switch | LLSC FROM ET-6203 ON-OFF VALVE | 1840-PS07-623 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-003-iCC | 18-IJB-40-003 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-62302 | Limit Switch | LLSC FROM ET-6203 ON-OFF VALVE | 1840-PS07-623 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-003-iCC | 18-IJB-40-003 | DI-MI | 1840 |  |  | -
1840 | 18-XZSH-62303 | Limit Switch | P TO POSM ON-OFF VALVE | 1840-PS07-623 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-003-iCC | 18-IJB-40-003 | DI-MI | 1840 |  |  | -
1840 | 18-XZSL-62303 | Limit Switch | P TO POSM ON-OFF VALVE | 1840-PS07-623 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-40-003-iCC | 18-IJB-40-003 | DI-MI | 1840 |  |  | -
1840 | 18-PN-62104 | Solenoid Valve | - | 1840-PS07-621 | PN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-40-001-CC | 18-EJB-40-001 | DOR-24V | 1840 |  |  | -
1840 | 18-XN-61105 | Solenoid Valve | - | 1840-PS07-611 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-40-001-CC | 18-EJB-40-001 | DOR-24V | 1840 |  |  | -
1840 | 18-XN-61201 | Solenoid Valve | - | 1840-PS07-612 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-40-001-CC | 18-EJB-40-001 | DOR-24V | 1840 |  |  | -
1840 | 18-XN-61206 | Solenoid Valve | - | 1840-PS07-612 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-40-001-CC | 18-EJB-40-001 | DOR-24V | 1840 |  |  | -
1840 | 18-XN-62106 | Solenoid Valve | - | 1840-PS07-621 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-40-001-CC | 18-EJB-40-001 | DOR-24V | 1840 |  |  | -
1840 | 18-XN-62301 | Solenoid Valve | - | 1840-PS07-623 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-40-001-CC | 18-EJB-40-001 | DOR-24V | 1840 |  |  | -
1840 | 18-XN-62302 | Solenoid Valve | - | 1840-PS07-623 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-40-001-CC | 18-EJB-40-001 | DOR-24V | 1840 |  |  | -
1840 | 18-HS-61101A | Pushbutton | RUD | 1840-PS07-611 | HS | DCS-DI | - | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | Console | C01 |  |  | DI-RE | 1840 |  | 7 | -
1840 | 18-HS-61101B | Pushbutton | RUD | 1840-PS07-611 | HS | DCS-DI | - | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | - | C01 | 单拉 |  | DI-RE | 1840 |  | 7 | -
1840 | 18-HS-61102 | Pushbutton | RUD RESET | 1840-PS07-611 | HS | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | Console | C01 |  |  | DI-RE | 1840 |  | 6 | -
7
1840 | 18-PT-61281A | Pressure Transmitter | 18-PP-6102A | 1840-PS07-612 | PIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-001-iSC | 18-IJB-40-001 | AI-IS | 1840 |  | 7 | -
1840 | 18-PT-61281B | Pressure Transmitter | 18-PP-6102B | 1840-PS07-612 | PIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-001-iSC | 18-IJB-40-001 | AI-IS | 1840 |  | 7 | -
1840 | 18-PT-61283 | Pressure Transmitter | 18-PP-6103 | 1840-PS07-612 | PIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-001-iSC | 18-IJB-40-001 | AI-IS | 1840 |  | 6 | -
1840 | 18-PT-62181A | Pressure Transmitter | 18-PP-6202A | 1840-PS07-621 | PIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-001-iSC | 18-IJB-40-001 | AI-IS | 1840 |  | 7 | -
1840 | 18-PT-62181B | Pressure Transmitter | 18-PP-6202B | 1840-PS07-621 | PIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-40-001-iSC | 18-IJB-40-001 | AI-IS | 1840 |  | 7 | -
1840 | 18-HS-61201P | DCS | 18-PP-6102A STOP | 1840-PS07-612 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1840 |  | 7 | -
1840 | 18-YL-61201R | DCS | 18-PP-6102A RUN | 1840-PS07-612 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-YL-61201F | DCS | 18-PP-6102A FAULT | 1840-PS07-612 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-HS-61202P | DCS | 18-PP-6102B STOP | 1840-PS07-612 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1840 |  | 7 | -
1840 | 18-YL-61202R | DCS | 18-PP-6102B RUN | 1840-PS07-612 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-YL-61202F | DCS | 18-PP-6102B FAULT | 1840-PS07-612 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-HS-61203P | DCS | 18-PP-6103 STOP | 1840-PS07-612 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1840 |  | 7 | -
1840 | 18-YL-61203R | DCS | 18-PP-6103 RUN | 1840-PS07-612 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-YL-61203F | DCS | 18-PP-6103 FAULT | 1840-PS07-612 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-HS-62101S | DCS | 18-PP-6202A START | 1840-PS07-621 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DO-Dry | 1840 |  | 7 | -
1840 | 18-HS-62101P | DCS | 18-PP-6202A STOP | 1840-PS07-621 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1840 |  | 7 | -
1840 | 18-YL-62101L | DCS | 18-PP-6202A REMOTE | 1840-PS07-621 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-YL-62101R | DCS | 18-PP-6202A RUN | 1840-PS07-621 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-YL-62101F | DCS | 18-PP-6202A FAULT | 1840-PS07-621 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-II-62101 | DCS | 18-PP-6202A CURRENT | 1840-PS07-621 | II | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AI-NIS | 1840 |  | 6 | -
1840 | 18-HS-62102S | DCS | 18-PP-6202B START | 1840-PS07-621 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DO-Dry | 1840 |  | 7 | -
1840 | 18-HS-62102P | DCS | 18-PP-6202B STOP | 1840-PS07-621 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1840 |  | 7 | -
1840 | 18-YL-62102L | DCS | 18-PP-6202B REMOTE | 1840-PS07-621 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-YL-62102R | DCS | 18-PP-6202B RUN | 1840-PS07-621 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-YL-62102F | DCS | 18-PP-6202B FAULT | 1840-PS07-621 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1840 |  | 7 | -
1840 | 18-II-62102 | DCS | 18-PP-6202B CURRENT | 1840-PS07-621 | II | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AI-NIS | 1840 |  |  | -
1812 | 18-TT-17104 | Temperature Transmitter | VE-1705 | 1812-PS07-171 | TISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-002-iSC | 18-IJB-12-002 | AIR-IS | 1812 |  |  | -
1812 | 18-PT-17106 | Pressure Transmitter With In-Line Diaphragm Seal | LP NITROGEN TO VE-1701 / VE-1702 | 1812-PS07-171 | PICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-003-iSC | 18-IJB-12-003 | AIR-IS | 1812 |  |  | -
1812 | 18-PV-17106A | Globe | LP NITROGEN TO VE-1701 | 1812-PS07-171 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-001-iSC | 18-IJB-12-001 | AOR-IS | 1812 |  |  | 1
1812 | 18-PV-17106B | Ball | LP NITROGEN TO VE-1702 | 1812-PS07-171 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-001-iSC | 18-IJB-12-001 | AOR-IS | 1812 |  |  | 1
1812 | 18-PT-17202 | Pressure Transmitter With In-Line Diaphragm Seal | TEA FROM PP-1701A | 1812-PS07-172 | PIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-002-iSC | 18-IJB-12-002 | AI-IS | 1812 |  |  | -
1812 | 18-PT-17204 | Pressure Transmitter With In-Line Diaphragm Seal | TEA FROM PP-1702A | 1812-PS07-172 | PIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-002-iSC | 18-IJB-12-002 | AI-IS | 1812 |  |  | -
1812 | 18-PT-17206 | Pressure Transmitter With In-Line Diaphragm Seal | TEA FROM PP-1701B | 1812-PS07-172 | PIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-002-iSC | 18-IJB-12-002 | AI-IS | 1812 |  |  | -
1812 | 18-PT-17208 | Pressure Transmitter With In-Line Diaphragm Seal | TEA FROM PP-1702B | 1812-PS07-172 | PIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-002-iSC | 18-IJB-12-002 | AI-IS | 1812 |  |  | -
1812 | 18-PT-17301 | Pressure Transmitter With Diaphragm Seal | PP-1704 DISCHARGE | 1812-PS07-173 | PIC | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-003-iSC | 18-IJB-12-003 | AIR-IS | 1812 |  |  | -
1812 | 18-PV-17301 | Globe | White Oil return to VE-1701 | 1812-PS07-173 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-001-iSC | 18-IJB-12-001 | AOR-IS | 1812 |  |  | -
1812 | 18-PT-17302 | Pressure Transmitter With Diaphragm Seal | LP NITROGEN/WHITE OIL TO FLARE | 1812-PS07-173 | PICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-003-iSC | 18-IJB-12-003 | AIR-IS | 1812 |  |  | -
1812 | 18-PV-17302A | Globe | LP NITROGEN TO VE-1703 | 1812-PS07-173 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-001-iSC | 18-IJB-12-001 | AOR-IS | 1812 |  |  | 1
1812 | 18-PV-17302B | Globe | NITROGEN/White Oil TO FLARE | 1812-PS07-173 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-001-iSC | 18-IJB-12-001 | AOR-IS | 1812 |  |  | 1
1812 | 18-PS-17211 | Pressure Switch | 18-PP-1701A DIAPHRAGM | 1812-PS07-172 | PSH | DCS-DI | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-12-004-CC | 18-EJB-12-004 | DIR-RE | 1812 |  |  | -
1812 | 18-PS-17212 | Pressure Switch | 18-PP-1701B DIAPHRAGM | 1812-PS07-172 | PSH | DCS-DI | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-12-004-CC | 18-EJB-12-004 | DIR-RE | 1812 |  |  | -
1812 | 18-PS-17213 | Pressure Switch | 18-PP-1702A DIAPHRAGM | 1812-PS07-172 | PSH | DCS-DI | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-12-004-CC | 18-EJB-12-004 | DIR-RE | 1812 |  |  | -
1812 | 18-PS-17214 | Pressure Switch | 18-PP-1702B DIAPHRAGM | 1812-PS07-172 | PSH | DCS-DI | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-12-004-CC | 18-EJB-12-004 | DIR-RE | 1812 |  |  | -
1812 | 18-PS-17303 | Pressure Switch | 18-PP-1704 DIAPHRAGM | 1812-PS07-173 | PSH | DCS-DI | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-12-004-CC | 18-EJB-12-004 | DIR-RE | 1812 |  |  | -
1812 | 18-FT-17101 | CORIOLIS MASS FLOWMETER | TEA TO VE-1701 | 1812-PS07-171 | FQIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 18-12-001-EC | 18-EJB-12-003 | AI-NIS | 1812 |  |  | -
1812 | 18-FT-17105 | CORIOLIS MASS FLOWMETER | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | FI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 18-12-001-EC | 18-EJB-12-003 | AI-NIS | 1812 |  |  | -
1812 | 18-FI-17105B | Local Indicator | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | FI | DCS-AO | Yes | 4~20mA | 4~20mA | 20mA | 1 | - | Yes |  | - | - | C01 | 18-12-007-iSC | 18-IJB-12-007 | AOR-IS | 1812 |  |  | 1
1812 | 18-FT-17108 | VORTEX FLOWMETER | NITROGEN TO TEA CONTAINER | 1812-PS07-171 | FQISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-003-iSC | 18-IJB-12-003 | AIR-IS | 1812 |  |  | -
1812 | 18-FT-17114 | CORIOLIS MASS FLOWMETER | WHITE OIL FLUSH FROM PP-1703 | 1812-PS07-171 | FQI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 18-12-001-EC | 18-EJB-12-003 | AI-NIS | 1812 |  |  | -
1812 | 18-LT-17101 | RADAR LEVEL TRANS. | VE-1701 | 1812-PS07-171 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-003-iSC | 18-IJB-12-003 | AIR-IS | 1812 |  |  | -
1812 | 18-LT-17102 | RADAR LEVEL TRANS. | VE-1701 | 1812-PS07-171 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-003-iSC | 18-IJB-12-003 | AIR-IS | 1812 |  |  | -
1812 | 18-LI-17102 | Local Indicator | VE-1701 | 1812-PS07-171 | LI | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | Yes |  | - | - | C01 | 18-12-007-iSC | 18-IJB-12-007 | AOR-IS | 1812 |  |  | -
1812 | 18-LT-17103 | D/P Level Transmitter with Extended Diaphgram Seal | VE-1702 | 1812-PS07-171 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-003-iSC | 18-IJB-12-003 | AIR-IS | 1812 |  |  | -
1812 | 18-LI-17103 | Local Indicator | VE-1702 | 1812-PS07-171 | LI | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | Yes |  | - | - | C01 | 18-12-007-iSC | 18-IJB-12-007 | AOR-IS | 1812 |  |  | -
1812 | 18-LT-17104 | D/P Level Transmitter with Extended Diaphgram Seal | VE-1705 | 1812-PS07-171 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-002-iSC | 18-IJB-12-002 | AIR-IS | 1812 |  |  | -
1812 | 18-LI-17104B | Local Indicator | VE-1702 | 1812-PS07-171 | LI | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | Yes |  | - | - | C01 | 18-12-007-iSC | 18-IJB-12-007 | AOR-IS | 1812 |  |  | 1
1812 | 18-LT-17107 | D/P Level Transmitter with Diaphgram Seal | VE-1706 | 1812-PS07-171 | LIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-002-iSC | 18-IJB-12-002 | AI-IS | 1812 |  |  | -
1812 | 18-LS-17108 | LEVEL SWITCH | VE-1705 | 1812-PS07-171 | LAH | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | 18-12-006-iCC | 18-IJB-12-006 | DI-MI | 1812 |  |  | -
1812 | 18-LT-17109 | Level Transmitter | PA-1705 | 1812-PS07-171 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | EKATO | C01 | 18-12-002-iSC | 18-IJB-12-002 | AIR-IS | 1812 |  |  | -
1812 | 18-LT-17301 | D/P Level Transmitter with Diaphgram Seal | VE-1703 | 1812-PS07-173 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-12-002-iSC | 18-IJB-12-002 | AIR-IS | 1812 |  |  | -
1812 | 18-XN-17101 | Solenoid Valve | LP N2 FROM HEADER | 1812-PS07-171 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-12-002-CC | 18-EJB-12-002 | DOR-24V | 1812 |  |  | -
1812 | 18-XZSH-17101 | Limit Switch | LP N2 FROM HEADER | 1812-PS07-171 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-004-iCC | 18-IJB-12-004 | DI-MI | 1812 |  |  | -
1812 | 18-XZSL-17101 | Limit Switch | LP N2 FROM HEADER | 1812-PS07-171 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-004-iCC | 18-IJB-12-004 | DI-MI | 1812 |  |  | -
1812 | 18-XN-17102 | Solenoid Valve | LP NITROGEN TO VE-1701 | 1812-PS07-171 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-12-002-CC | 18-EJB-12-002 | DOR-24V | 1812 |  |  | -
1812 | 18-XZSH-17102 | Limit Switch | LP NITROGEN TO VE-1701 | 1812-PS07-171 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-004-iCC | 18-IJB-12-004 | DI-MI | 1812 |  |  | -
1812 | 18-XZSL-17102 | Limit Switch | LP NITROGEN TO VE-1701 | 1812-PS07-171 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-004-iCC | 18-IJB-12-004 | DI-MI | 1812 |  |  | -
1812 | 18-XN-17103 | Solenoid Valve | LP NITROGEN TO VE-1702 | 1812-PS07-171 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-12-002-CC | 18-EJB-12-002 | DOR-24V | 1812 |  |  | -
1812 | 18-XZSH-17103 | Limit Switch | LP NITROGEN TO VE-1702 | 1812-PS07-171 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-004-iCC | 18-IJB-12-004 | DI-MI | 1812 |  |  | -
1812 | 18-XZSL-17103 | Limit Switch | LP NITROGEN TO VE-1702 | 1812-PS07-171 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-004-iCC | 18-IJB-12-004 | DI-MI | 1812 |  |  | -
1812 | 18-XN-17104 | Solenoid Valve | TEA TO VE-1701 | 1812-PS07-171 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-12-002-CC | 18-EJB-12-002 | DOR-24V | 1812 |  |  | -
1812 | 18-XZSH-17104 | Limit Switch | TEA TO VE-1701 | 1812-PS07-171 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-005-iCC | 18-IJB-12-005 | DI-MI | 1812 |  |  | -
1812 | 18-XZSL-17104 | Limit Switch | TEA TO VE-1701 | 1812-PS07-171 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-005-iCC | 18-IJB-12-005 | DI-MI | 1812 |  |  | -
1812 | 18-XN-17105 | Solenoid Valve | TEA CONTAINER ISOLATION VALVE | 1812-PS07-171 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-12-002-CC | 18-EJB-12-002 | DOR-24V | 1812 |  |  | -
1812 | 18-XZSH-17105 | Limit Switch | TEA CONTAINER ISOLATION VALVE | 1812-PS07-171 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-004-iCC | 18-IJB-12-004 | DI-MI | 1812 |  |  | -
1812 | 18-XZSL-17105 | Limit Switch | TEA CONTAINER ISOLATION VALVE | 1812-PS07-171 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-004-iCC | 18-IJB-12-004 | DI-MI | 1812 |  |  | -
1812 | 18-HS-17108 | Pushbutton | XV-17105 RESET | 1812-PS07-171 | HS | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-2-CC1 | LCP-2 | DI-RE | 1812 |  |  | -
1812 | 18-XN-17106 | Solenoid Valve | FLUSHING TO VE-1705 | 1812-PS07-171 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-12-002-CC | 18-EJB-12-002 | DOR-24V | 1812 |  |  | -
1812 | 18-XZSH-17106 | Limit Switch | FLUSHING TO VE-1705 | 1812-PS07-171 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-005-iCC | 18-IJB-12-005 | DI-MI | 1812 |  |  | -
1812 | 18-XZSL-17106 | Limit Switch | FLUSHING TO VE-1705 | 1812-PS07-171 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-005-iCC | 18-IJB-12-005 | DI-MI | 1812 |  |  | -
1812 | 18-XHSO-17106 | Pushbutton | FLUSHING TO VE-1705 | 1812-PS07-171 | XHSO | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-2-CC1 | LCP-2 | DI-RE | 1812 |  |  | -
1812 | 18-XHSC-17106 | Pushbutton | FLUSHING TO VE-1705 | 1812-PS07-171 | XHSC | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-2-CC1 | LCP-2 | DI-RE | 1812 |  |  | -
1812 | 18-XN-17107 | Solenoid Valve | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-12-002-CC | 18-EJB-12-002 | DOR-24V | 1812 |  |  | -
1812 | 18-XZSH-17107 | Limit Switch | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-005-iCC | 18-IJB-12-005 | DI-MI | 1812 |  |  | -
1812 | 18-XZSL-17107 | Limit Switch | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-005-iCC | 18-IJB-12-005 | DI-MI | 1812 |  |  | -
1812 | 18-XHSO-17107 | Pushbutton | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | XHSO | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-2-CC1 | LCP-2 | DI-RE | 1812 |  |  | -
1812 | 18-XHSC-17107 | Pushbutton | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | XHSC | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-2-CC1 | LCP-2 | DI-RE | 1812 |  |  | -
1812 | 18-XZSH-17108 | Limit Switch | WASTE WHITE OIL FROM VE-1705 TO DRUM | 1812-PS07-171 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-006-iCC | 18-IJB-12-006 | DI-MI | 1812 |  |  | -
1812 | 18-XZSL-17108 | Limit Switch | WASTE WHITE OIL FROM VE-1705 TO DRUM | 1812-PS07-171 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-006-iCC | 18-IJB-12-006 | DI-MI | 1812 |  |  | -
1812 | 18-XN-17111 | Solenoid Valve | White Oil to VE-1701 | 1812-PS07-171 | XN | DCS-DO | Yes | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-12-002-CC | 18-EJB-12-002 | DOR-24V | 1812 |  |  | -
1812 | 18-XZSH-17111 | Limit Switch | White Oil to VE-1701 | 1812-PS07-171 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-006-iCC | 18-IJB-12-006 | DI-MI | 1812 |  |  | -
1812 | 18-XZSL-17111 | Limit Switch | White Oil to VE-1701 | 1812-PS07-171 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-12-006-iCC | 18-IJB-12-006 | DI-MI | 1812 |  |  | -
1812 | 18-XHSO-17111 | Pushbutton | White Oil to VE-1701 | 1812-PS07-171 | XHSO | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-12-004-CC | 18-EJB-12-004 | DI-RE | 1812 |  |  | -
1812 | 18-XHSC-17111 | Pushbutton | White Oil to VE-1701 | 1812-PS07-171 | XHSC | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-12-004-CC | 18-EJB-12-004 | DI-RE | 1812 |  |  | -
1812 | 18-YS-17101 | STATIC GROUDING SYSTEM | WHITE OIL DRUM | 1812-PS07-171 | YSA | DCS-DI | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | Yes |  | - | - | C01 | 18-12-001-EC | 18-EJB-12-003 | DIR-IS | 1812 |  |  | -
1812 | 18-YS-17102 | STATIC GROUDING SYSTEM | TEA CONTAINER | 1812-PS07-171 | YSA | DCS-DI | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | Yes |  | - | - | C01 | 18-12-001-EC | 18-EJB-12-003 | DIR-IS | 1812 |  |  | -
1812 | 18-HS-17102B | Pushbutton | TEA CONTAINER OFFLINE | 1812-PS07-171 | HS | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-1-CC1 | LCP-1 | DI-RE | 1812 |  |  | 1
1812 | 18-HS-17103 | Pushbutton | SYSTEM FLUSH | 1812-PS07-171 | HS | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-1-CC1 | LCP-1 | DI-RE | 1812 |  |  | -
1812 | 18-HS-17104 | Pushbutton | SYSTEM PRESSURE | 1812-PS07-171 | HS | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-1-CC1 | LCP-1 | DI-RE | 1812 |  |  | -
1812 | 18-HS-17105 | Pushbutton | SYSTEM DEPRESSURE | 1812-PS07-171 | HS | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-1-CC1 | LCP-1 | DI-RE | 1812 |  |  | -
1812 | 18-HS-17106 | Pushbutton | TEA CONTAINER ONLINE | 1812-PS07-171 | HS | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-1-CC1 | LCP-1 | DI-RE | 1812 |  |  | -
1812 | 18-UL-17110B | Status Lamp | TEA CONTAINER SEQUENCE | 1812-PS07-171 | UL | DCS-DO | - | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-LCP-1-CC1 | LCP-1 | DO-24V | 1812 |  |  | 1
1812 | 18-XL-17121 | Status Lamp | TEA CONTAINER READY TO CHANGE | 1812-PS07-171 | UL | DCS-DO | - | WET (NC) | WET | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-LCP-1-CC1 | LCP-1 | DO-24V | 1812 |  |  | -
1812 | 18-HS-17109A | Pushbutton | PA-1705 START | 1812-PS07-171 | HS | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-2-CC1 | LCP-2 | DI-RE | 1812 |  |  | 1
1812 | 18-HS-17109B | Pushbutton | PA-1705 STOP | 1812-PS07-171 | HS | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-LCP-2-CC1 | LCP-2 | DI-RE | 1812 |  |  | 1
1812 | 18-HS-17201P | DCS | PP-1701A STOP | 1812-PS07-172 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1812 |  |  | 1
1812 | 18-YL-17201R | DCS | PP-1701A RUN | 1812-PS07-172 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-YL-17201F | DCS | PP-1701A FAULT | 1812-PS07-172 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-SI-17201 | DCS | PP-1701A SPEED | 1812-PS07-172 | SI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AI-NIS | 1812 |  |  | -
1812 | 18-SC-17201 | DCS | PP-1701A SPEED CONTROL | 1812-PS07-172 | SC | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AOR-NIS | 1812 |  |  | -
1812 | 18-HS-17202P | DCS | PP-1701B STOP | 1812-PS07-172 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1812 |  |  | 1
1812 | 18-YL-17202R | DCS | PP-1701B RUN | 1812-PS07-172 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-YL-17202F | DCS | PP-1701B FAULT | 1812-PS07-172 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-SI-17202 | DCS | PP-1701B SPEED | 1812-PS07-172 | SI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AI-NIS | 1812 |  |  | -
1812 | 18-SC-17202 | DCS | PP-1701B SPEED CONTROL | 1812-PS07-172 | SC | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AOR-NIS | 1812 |  |  | -
1812 | 18-HS-17203P | DCS | PP-1702A STOP | 1812-PS07-172 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1812 |  |  | 1
1812 | 18-YL-17203R | DCS | PP-1702A RUN | 1812-PS07-172 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-YL-17203F | DCS | PP-1702A FAULT | 1812-PS07-172 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-SI-17203 | DCS | PP-1702A SPEED | 1812-PS07-172 | SI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AI-NIS | 1812 |  |  | -
1812 | 18-SC-17203 | DCS | PP-1702A SPEED CONTROL | 1812-PS07-172 | SC | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AOR-NIS | 1812 |  |  | -
1812 | 18-HS-17204P | DCS | PP-1702B STOP | 1812-PS07-172 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1812 |  |  | 1
1812 | 18-YL-17204R | DCS | PP-1702B RUN | 1812-PS07-172 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-YL-17204F | DCS | PP-1702B FAULT | 1812-PS07-172 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-SI-17204 | DCS | PP-1702B SPEED | 1812-PS07-172 | SI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AI-NIS | 1812 |  |  | -
1812 | 18-SC-17204 | DCS | PP-1702B SPEED CONTROL | 1812-PS07-172 | SC | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AOR-NIS | 1812 |  |  | -
1812 | 18-HS-17301P | DCS | PP-1704 STOP | 1812-PS07-173 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1812 |  |  | 1
1812 | 18-YL-17301R | DCS | PP-1704 RUN | 1812-PS07-173 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-YL-17301F | DCS | PP-1704 FAULT | 1812-PS07-173 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-SI-17301 | DCS | PP-1704 SPEED | 1812-PS07-173 | SI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AI-NIS | 1812 |  |  | -
1812 | 18-SC-17301 | DCS | PP-1704 SPEED CONTROL | 1812-PS07-173 | SC | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AOR-NIS | 1812 |  |  | -
1812 | 18-HS-17109P | DCS | PP-1705 STOP | 1812-PS07-173 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | MCC |  | DOR-Dry | 1812 |  |  | 1
1812 | 18-YL-17109R | DCS | PP-1705 RUN | 1812-PS07-173 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1812 | 18-YL-17109F | DCS | PP-1705 FAULT | 1812-PS07-173 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 | MCC |  | DI-RE | 1812 |  |  | 1
1830 | 18-TT-21101 | Integral Temperature Transmitter | PEROXIDE DOSING ROOM | 1830-PS07-211 | TIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-005-iSC | 18-IJB-30-005 | AI-IS | 1830 |  |  | -
1830 | 18-TT-21102 | Integral Temperature Transmitter | PEROXIDE FROM PP-2101 | 1830-PS07-211 | TISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-005-iSC | 18-IJB-30-005 | AIR-IS | 1830 |  |  | -
1830 | 18-TT-21104 | Integral Temperature Transmitter | VE-2101 | 1830-PS07-211 | TISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-005-iSC | 18-IJB-30-005 | AIR-IS | 1830 |  |  | -
1830 | 18-TT-23101 | Integral Temperature Transmitter | VE-2301 | 1830-PS07-231 | TIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-017-iSC | 单拉 | AI-IS | 1830 |  |  | -
1830 | 18-TT-23102 | Integral Temperature Transmitter | VE-2302 | 1830-PS07-231 | TIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-010-iSC | 18-IJB-30-010 | AI-IS | 1830 |  |  | -
1830 | 18-TT-36102 | Integral Temperature Transmitter | COOLING WATER TO PX PIPE | 1830-PS07-211 | TIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-005-iSC | 18-IJB-30-005 | AI-IS | 1830 |  |  | -
1830 | 18-TT-66101 | Integral Temperature Transmitter | OFFGAS FROM ET-6602 | 1830-PS07-661 | TIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-015-iSC | 18-IJB-30-015 | AI-IS | 1830 |  |  | -
1830 | 18-TT-66104 | Temperature Transmitter | ET-6601X outlet | 1830-PS07-661 | TIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | UP-6601VENDOR | C01 | DCS | 18-6601-DJB-0003 | AI-IS | 1830 |  |  | -
1830 | 18-TT-92101 | Integral Temperature Transmitter | WASTE WATER TO OSBL | 1830-PS07-921 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-005-iSC | 18-IJB-30-005 | AI-IS | 1830 |  |  | -
1830 | 18-TT-92102 | Integral Temperature Transmitter | VP-9201 SURFACE WATER COLLECTION | 1830-PS07-921 | TIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-005-iSC | 18-IJB-30-005 | AI-IS | 1830 |  |  | -
1830 | 18-PT-21103 | Pressure Transmitter With In-Line Diaphragm Seal | PEROXIDE FROM PP-2102 | 1830-PS07-211 | PISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-005-iSC | 18-IJB-30-005 | AIR-IS | 1830 |  |  | -
1830 | 18-PT-21105 | Pressure Transmitter With In-Line Diaphragm Seal | PEROXIDE FROM PP-2101 | 1830-PS07-211 | PISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-005-iSC | 18-IJB-30-005 | AIR-IS | 1830 |  |  | -
1830 | 18-PT-21108 | Pressure Transmitter With In-Line Diaphragm Seal | PEROXIDE FROM PP-2101 | 1830-PS07-211 | PISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-005-iSC | 18-IJB-30-005 | AIR-IS | 1830 |  |  | -
1830 | 18-PT-21110 | Pressure Transmitter With In-Line Diaphragm Seal | PEROXIDE FROM PP-2101 | 1830-PS07-211 | PICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-005-iSC | 18-IJB-30-005 | AIR-IS | 1830 |  |  | -
1830 | 18-PT-23101 | Pressure Transmitter With Diaphragm Seal | LP NITROGEN TO VE-2301 | 1830-PS07-231 | PICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-015-iSC | 18-IJB-30-015 | AIR-IS | 1830 |  |  | -
1830 | 18-PT-24101 | Pressure Transmitter | NITROGEN TO VE-2401 | 1830-PS07-241 | PICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-010-iSC | 18-IJB-30-010 | AIR-IS | 1830 |  |  | -
1830 | 18-PT-66101 | Pressure Transmitter | OFFGAS TO ET-6602 | 1830-PS07-661 | PICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-015-iSC | 18-IJB-30-015 | AIR-IS | 1830 |  |  | -
1830 | 18-PT-66102 | Pressure Transmitter | OFFGAS TO ATM AT SAFE LOCATION | 1830-PS07-661 | PICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-015-iSC | 18-IJB-30-015 | AIR-IS | 1830 |  |  | -
1830 | 18-PT-92101 | Pressure Transmitter With Diaphragm Seal | WASTE WATER TO OSBL | 1830-PS07-921 | PI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-007-iSC | 18-IJB-30-007 | AI-IS | 1830 |  |  | -
1830 | 18-PDT-23105 | D/P Transmitter With In-Line Diaphragm Seal | FL-2301A/B | 1830-PS07-231 | PDIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-006-iSC | 18-IJB-30-006 | AI-IS | 1830 |  |  | -
1830 | 18-PDT-24103 | D/P Transmitter With In-Line Diaphragm Seal | FL-2401 | 1830-PS07-241 | PDIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-006-iSC | 18-IJB-30-006 | AI-IS | 1830 |  |  | -
1830 | 18-PS-21104 | Pressure Switch | 18-PP-2101 DIAPHRAGM | 1830-PS07-211 | PSH | DCS-DI | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | - | C01 | 单拉 | 单拉 | DIR-RE | 1830 |  |  | -
1830 | 18-PS-21102 | Pressure Switch | 18-PP-2102 DIAPHRAGM | 1830-PS07-211 | PSH | DCS-DI | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | - | C01 | 单拉 | 单拉 | DIR-RE | 1830 |  |  | -
1830 | 18-FT-21102 | Variable Area Flowmeter | LP NITROGEN TO VE-2101 | 1830-PS07-211 | FISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-007-iSC | 18-IJB-30-007 | AIR-IS | 1830 |  |  | -
1830 | 18-FT-21107 | Variable Area Flowmeter | COOLING WATER | 1830-PS07-211 | FIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-007-iSC | 18-IJB-30-007 | AI-IS | 1830 |  |  | -
1830 | 18-FT-21109 | Variable Area Flowmeter | LP NITROGEN TO PEROXIDE DRUM | 1830-PS07-211 | FISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-007-iSC | 18-IJB-30-007 | AIR-IS | 1830 |  |  | -
1830 | 18-FT-21103 | Coriolis Mass Flowmeter | PEROXIDE TO PJ-3601X | 1830-PS07-211 | FICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 单拉 | 单拉 | AIR-NIS | 1830 |  |  | -
1830 | 18-FT-23101 | Coriolis Mass Flowmeter | MELTABLE ADDITIVES TO PJ-3601X | 1830-PS07-231 | FICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 18-30-009-EC | 18-EJB-30-009 | AIR-NIS | 1830 |  |  | -
1830 | 18-FT-24101 | Coriolis Mass Flowmeter | LIQUID ADDITIVES TO PJ-3601X | 1830-PS07-241 | FICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 18-30-009-EC | 18-EJB-30-009 | AIR-NIS | 1830 |  |  | -
1830 | 18-FT-36103 | Coriolis Mass Flowmeter | DEMIN. WATER TO PJ-3601X | 1830-PS07-361 | FICSA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 18-30-009-EC | 18-EJB-30-009 | AIR-NIS | 1830 |  |  | -
1830 | 18-FT-92102 | Magnetic Flowmeter | WASTE W ATER TO OSBL | 1830-PS07-921 | FQI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | 24VDC | - |  | - | - | C01 | 单拉 | 单拉 | AI-NIS | 1830 |  |  | -
1830 | 18-LT-21101 | D/P Level Transmitter With Diaphgram Seal | 18-VE-2101 | 1830-PS07-211 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-007-iSC | 18-IJB-30-007 | AIR-IS | 1830 |  |  | -
1830 | 18-LT-23101 | D/P Level Transmitter With Extended Diaphgram Seal | 18-VE-2301 | 1830-PS07-231 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-010-iSC | 18-IJB-30-010 | AIR-IS | 1830 |  |  | -
1830 | 18-LT-23102 | D/P Level Transmitter With Extended Diaphgram Seal | 18-VE-2302 | 1830-PS07-231 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-010-iSC | 18-IJB-30-010 | AIR-IS | 1830 |  |  | -
1830 | 18-LT-24101 | D/P Level Transmitter With Extended Diaphgram Seal | 18-VE-2401 | 1830-PS07-241 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-010-iSC | 18-IJB-30-010 | AIR-IS | 1830 |  |  | -
1830 | 18-LT-92101 | Radar Level Transmitter | VP-9201 SURFACE WATER COLLECTION | 1830-PS07-921 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-007-iSC | 18-IJB-30-007 | AIR-IS | 1830 |  |  | -
1830 | 18-LT-66101 | Level Transmitter | 18-VE-6601X | 1830-PS07-661 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | UP-6601VENDOR | C01 | DCS | 18-6601-DJB-0003 | AIR-IS | 1830 |  |  | -
1830 | 18-LT-66202 | Displacer Transmitter | 18-VE-6602 | 1830-PS07-662 | LICA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-006-iSC | 18-IJB-30-006 | AIR-IS | 1830 |  |  | -
1830 | 18-LT-66203 | Displacer Transmitter | 18-VE-6602 | 1830-PS07-662 | LIA | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-006-iSC | 18-IJB-30-006 | AI-IS | 1830 |  |  | -
1830 | 18-LS-36202 | Tuning Folk | 18-VE-36202 | 1830-PS07-362 | LSL | DCS-DI | Yes | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | 18-30-003-iCC | 18-IJB-30-003 | DIR-MI | 1830 |  |  | -
1830 | 18-TI-21101 | Local Indicator | PEROXIDE DOSING ROOM | 1830-PS07-211 | TI | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-021-iSC | 18-IJB-30-021 | AOR-IS | 1830 |  |  | -
1830 | 18-LI-21101 | Local Indicator | 18-VE-2101 | 1830-PS07-211 | LI | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-021-iSC | 18-IJB-30-021 | AOR-IS | 1830 |  |  | -
1830 | 18-LI-23101 | Local Indicator | 18-VE-2301 | 1830-PS07-231 | LI | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-024-SC | 单拉 | AOR-IS | 1830 |  |  | -
1830 | 18-LI-24101 | Local Indicator | 18-VE-2401 | 1830-PS07-241 | LI | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-024-SC | 单拉 | AOR-IS | 1830 |  |  | -
1830 | 18-PV-21110 | Ball | PEROXIDE TO VE-2101 | 1830-PS07-211 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-012-iSC | 18-IJB-30-012 | AOR-IS | 1830 |  |  | -
1830 | 18-PV-23101A | Globe | LP NITROGEN TO VE-2301 | 1830-PS07-231 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-014-iSC | 18-IJB-30-014 | AOR-IS | 1830 |  |  | 2
1830 | 18-PV-23101B | Globe | NITROGEN TO ATM. | 1830-PS07-231 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-014-iSC | 18-IJB-30-014 | AOR-IS | 1830 |  |  | 2
1830 | 18-PV-24101A | Globe | LP NITROGEN TO VE-2401 | 1830-PS07-241 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-001-iSC | 18-IJB-30-001 | AOR-IS | 1830 |  |  | 2
1830 | 18-PV-24101B | Globe | LP NITROGEN LIQUID ADDITIVE DRUM | 1830-PS07-241 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-001-iSC | 18-IJB-30-001 | AOR-IS | 1830 |  |  | 2
1830 | 18-PV-66101 | Control Valve | By-pass pressure control valve | 1830-PS07-661 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | UP-6601VENDOR | C01 | DCS | 18-6601-DJB-0003 | AOR-IS | 1830 |  |  | -
1830 | 18-PV-66102 | Globe | VACUMM OFFGAS TO OSBL | 1830-PS07-661 | PV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-014-iSC | 18-IJB-30-014 | AOR-IS | 1830 |  |  | -
1830 | 18-FV-21103A | Ball | PEROXIDE TO UP-3601 | 1830-PS07-211 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-012-iSC | 18-IJB-30-012 | AOR-IS | 1830 |  |  | 2
1830 | 18-FV-21103B | Ball | PEROXIDE TO UP-3601 | 1830-PS07-211 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-012-iSC | 18-IJB-30-012 | AOR-IS | 1830 |  |  | 2
1830 | 18-FV-36103 | Globe | DEMINERALIZED WATER FROM HEADER TO UP-3601 | 1830-PS07-361 | FV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-001-iSC | 18-IJB-30-001 | AOR-IS | 1830 |  |  | -
1830 | 18-LV-66202 | Globe | WASTE WATER TO VP-9201 | 1830-PS07-662 | LV | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-001-iSC | 18-IJB-30-001 | AOR-IS | 1830 |  |  | -
1830 | 18-HV-36105 | Ball | PEROXIDE FROM PP-2101 TO UP-3601 | 1830-PS07-361 | HIC | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-001-iSC | 18-IJB-30-001 | AOR-IS | 1830 |  |  | -
1830 | 18-HV-66102 | Globe | OFFGAS TO ATM AT SAFE LOCATION | 1830-PS07-661 | HIC | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 18-30-014-iSC | 18-IJB-30-014 | AOR-IS | 1830 |  |  | -
1830 | 18-PZSL-66102 | Limit Switch | - | 1830-PS07-661 | PZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-016-iCC | 18-IJB-30-016 | DI-MI | 1830 |  |  | -
1830 | 18-HZSH-66102 | Limit Switch | - | 1830-PS07-661 | HZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-016-iCC | 18-IJB-30-016 | DI-MI | 1830 |  |  | -
1830 | 18-HZSL-66102 | Limit Switch | - | 1830-PS07-661 | HZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-016-iCC | 18-IJB-30-016 | DI-MI | 1830 |  |  | -
1830 | 18-XZSH-21101 | Limit Switch | - | 1830-PS07-211 | HZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-002-iCC | 18-IJB-30-002 | DI-MI | 1830 |  |  | -
1830 | 18-XZSL-21101 | Limit Switch | - | 1830-PS07-211 | HZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-002-iCC | 18-IJB-30-002 | DI-MI | 1830 |  |  | -
1830 | 18-XZSH-21103 | Limit Switch | - | 1830-PS07-211 | HZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-002-iCC | 18-IJB-30-002 | DI-MI | 1830 |  |  | -
1830 | 18-XZSL-21103 | Limit Switch | - | 1830-PS07-211 | HZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-002-iCC | 18-IJB-30-002 | DI-MI | 1830 |  |  | -
1830 | 18-XZSH-21104 | Limit Switch | - | 1830-PS07-211 | HZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-002-iCC | 18-IJB-30-002 | DI-MI | 1830 |  |  | -
1830 | 18-XZSL-21104 | Limit Switch | - | 1830-PS07-211 | HZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-002-iCC | 18-IJB-30-002 | DI-MI | 1830 |  |  | -
1830 | 18-XZSH-23101 | Limit Switch | - | 1830-PS07-231 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-013-iCC | 18-IJB-30-013 | DI-MI | 1830 |  |  | -
1830 | 18-XZSL-23101 | Limit Switch | - | 1830-PS07-231 | HZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-013-iCC | 18-IJB-30-013 | DI-MI | 1830 |  |  | -
1830 | 18-XZSH-24102 | Limit Switch | - | 1830-PS07-241 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-013-iCC | 18-IJB-30-013 | DI-MI | 1830 |  |  | -
1830 | 18-XZSL-24102 | Limit Switch | - | 1830-PS07-241 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-013-iCC | 18-IJB-30-013 | DI-MI | 1830 |  |  | -
1830 | 18-XZSH-36101 | Limit Switch | - | 1830-PS07-361 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-003-iCC | 18-IJB-30-003 | DI-MI | 1830 |  |  | -
1830 | 18-XZSL-36101 | Limit Switch | - | 1830-PS07-361 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-003-iCC | 18-IJB-30-003 | DI-MI | 1830 |  |  | -
1830 | 18-XZSH-36102 | Limit Switch | - | 1830-PS07-361 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-003-iCC | 18-IJB-30-003 | DI-MI | 1830 |  |  | -
1830 | 18-XZSL-36102 | Limit Switch | - | 1830-PS07-361 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-003-iCC | 18-IJB-30-003 | DI-MI | 1830 |  |  | -
1830 | 18-XZSH-66101 | Limit Switch | - | 1830-PS07-661 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-016-iCC | 18-IJB-30-016 | DI-MI | 1830 |  |  | -
1830 | 18-XZSL-66101 | Limit Switch | - | 1830-PS07-661 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | - | C01 | 18-30-016-iCC | 18-IJB-30-016 | DI-MI | 1830 |  |  | -
1830 | 18-XZSH-66105 | Limit Switch | - | 1830-PS07-661 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | UP-6601VENDOR | C01 | DCS | 18-6601-DJB-0001 | DI-MI | 1830 |  |  | -
1830 | 18-XZSL-66105 | Limit Switch | - | 1830-PS07-661 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | UP-6601VENDOR | C01 | DCS | 18-6601-DJB-0001 | DI-MI | 1830 |  |  | -
1830 | 18-XZSH-66106 | Limit Switch | - | 1830-PS07-661 | XZSH | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | UP-6601VENDOR | C01 | DCS | 18-6601-DJB-0001 | DI-MI | 1830 |  |  | -
1830 | 18-XZSL-66106 | Limit Switch | - | 1830-PS07-661 | XZSL | DCS-DI | - | NAMUR(NO) | NAMUR | (NO) | 1 | - | Yes |  | - | UP-6601VENDOR | C01 | DCS | 18-6601-DJB-0001 | DI-MI | 1830 |  |  | -
1830 | 18-XHSO-21101 | Pushbutton | PEROXIDE FROM PP-2102 | 1830-PS07-211 | XHSO | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-30-023-CC | 18-EJB-30-023 | DI-RE | 1830 |  |  | -
1830 | 18-XHSC-21101 | Pushbutton | PEROXIDE FROM PP-2102 | 1830-PS07-211 | XHSC | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-30-023-CC | 18-EJB-30-023 | DI-RE | 1830 |  |  | -
1830 | 18-XHSO-24102 | Pushbutton | LIQUID ADDITIVES TO VE-2401 | 1830-PS07-241 | XHSO | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-30-025-CC | 18-EJB-30-025 | DI-RE | 1830 |  |  | -
1830 | 18-XHSC-24102 | Pushbutton | LIQUID ADDITIVES TO VE-2401 | 1830-PS07-241 | XHSC | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-30-025-CC | 18-EJB-30-025 | DI-RE | 1830 |  |  | -
1830 | 18-XHSO-66101 | Pushbutton | - | 1830-PS07-661 | XHSO | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-30-023-CC | 18-EJB-30-023 | DI-RE | 1830 |  |  | -
1830 | 18-XHSC-66101 | Pushbutton | - | 1830-PS07-661 | XHSC | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 18-30-023-CC | 18-EJB-30-023 | DI-RE | 1830 |  |  | -
1830 | [19 empty] | AI-IS | 1830
1830 | 18-PN-66102 | Solenoid Valve | VACUUM OFFGAS | 1830-PS07-661 | PN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-30-004-CC | 18-EJB-30-004 | DOR-24V | 1830 |  |  | -
1830 | 18-XN-21101 | Solenoid Valve | PX FROM PP-2102 TO VE-2101 | 1830-PS07-211 | XN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-30-018-CC | 18-EJB-30-018 | DOR-24V | 1830 |  |  | -
1830 | 18-XN-21103 | Solenoid Valve | PX FROM VE-2101 TO PP-2101 | 1830-PS07-211 | XN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-30-018-CC | 18-EJB-30-018 | DOR-24V | 1830 |  |  | -
1830 | 18-XN-21104 | Solenoid Valve | FIRE WATER TO PX DOSING ROOM | 1830-PS07-211 | XN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-30-018-CC | 18-EJB-30-018 | DOR-24V | 1830 |  |  | -
1830 | 18-XN-23101 | Solenoid Valve | ADD. VE-2301 TO VE-2302 | 1830-PS07-231 | XN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-30-004-CC | 18-EJB-30-004 | DOR-24V | 1830 |  |  | -
1830 | 18-XN-24102 | Solenoid Valve | PP-2402 DISCHARGE | 1830-PS07-241 | XN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-30-004-CC | 18-EJB-30-004 | DOR-24V | 1830 |  |  | -
1830 | 18-XN-36101A | Solenoid Valve | PEROXIDE TO PJ-3601X | 1830-PS07-361 | XN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-30-004-CC | 18-EJB-30-004 | DOR-24V | 1830 |  |  | 3
1830 | 18-XN-36102A | Solenoid Valve | PEROXIDE TO PJ-3601X | 1830-PS07-361 | XN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-30-004-CC | 18-EJB-30-004 | DOR-24V | 1830 |  |  | 3
1830 | 18-XN-66101 | Solenoid Valve | OFFGAS FROM VE-3601X TO ET-6602 | 1830-PS07-661 | XN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | 18-30-004-CC | 18-EJB-30-004 | DOR-24V | 1830 |  |  | -
1830 | 18-XN-66105 | Solenoid Valve | - | 1830-PS07-661 | XN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | DCS | 18-6601-DJB-0002 | DOR-24V | 1830 |  |  | -
1830 | 18-XN-66106 | Solenoid Valve | - | 1830-PS07-661 | XN | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | - |  | - | - | C01 | DCS | 18-6601-DJB-0002 | DOR-24V | 1830 |  |  | -
1830 | [19 empty] | AI-IS | 1830
1830 | 18-AT-66101 | O2 Analyzer | O2 IN OFFGAS FROM UP-6601 | 1830-PS07-661 | AISA | DCS-AI | Yes | 4~20mA | 4~20mA | 20mA | 1 | 220VAC | - |  | - | - | C01 | 18-30-024-SC | 单拉 | AIR-NIS | 1830 |  |  | -
1830 | [19 empty] | AI-IS | 1830
1830 | 18-YS-24103 | Static Grounding Transmitter | LIQUID ADDITIVE DRUM | 1830-PS07-241 | YSA | DCS-DI | Yes | DRY (NC) | DRY | (NC) | 1 | 24VDC | Yes |  | - | - | C01 | 18-30-013-iCC | 18-IJB-30-013 | DIR-IS | 1830 |  |  | -
1830 | [19 empty] | AI-IS | 1830
1830 | 18-LT-23103 | Level Transmitter | 18-PA-2301 | 1830-PS07-231 | LISA | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | EKATO | C01 | DCS | 18-PA2301-DJB-0001 | AIR-IS | 1830 |  |  | -
1830 | [19 empty] | AI-IS | 1830
1830 | 18-YL-21103R | DCS | 18-PP-2101 RUN | 1830-PS07-211 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-21103F | DCS | 18-PP-2101 FAULT | 1830-PS07-211 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-HS-21103P | DCS | 18-PP-2101 STOP | 1830-PS07-211 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 2
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-21104P | DCS | 18-PP-2102 STOP | 1830-PS07-211 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 2
1830 | 18-YL-21104R | DCS | 18-PP-2102 RUN | 1830-PS07-211 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-21104F | DCS | 18-PP-2102 FAULT | 1830-PS07-211 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-21102S | DCS | 18-PB-2101 START | 1830-PS07-211 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 2
1830 | 18-HS-21102P | DCS | 18-PB-2101 STOP | 1830-PS07-211 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 2
1830 | 18-YL-21102L | DCS | 18-PB-2101 REMOTE | 1830-PS07-211 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-21102R | DCS | 18-PB-2101 RUN | 1830-PS07-211 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-21102F | DCS | 18-PB-2101 FAULT | 1830-PS07-211 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-23101S | DCS | 18-PP-2301A START | 1830-PS07-231 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 2
1830 | 18-HS-23101P | DCS | 18-PP-2301A DCS STOP | 1830-PS07-231 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 2
1830 | 18-YL-23101L | DCS | 18-PP-2301A REMOTE | 1830-PS07-231 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-23101R | DCS | 18-PP-2301A RUNNING | 1830-PS07-231 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-23101F | DCS | 18-PP-2301A FAULT | 1830-PS07-231 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-SI-23101 | DCS | 18-PP-2301A SPEED | 1830-PS07-231 | SI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 |  |  | AI-NIS | 1830 |  |  | -
1830 | 18-SC-23101 | DCS | 18-PP-2301A CONTROL | 1830-PS07-231 | SC | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AOR-NIS | 1830 |  |  | -
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-23102S | DCS | 18-PP-2301B START | 1830-PS07-231 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 2
1830 | 18-HS-23102P | DCS | 18-PP-2301B STOP | 1830-PS07-231 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 2
1830 | 18-YL-23102F | DCS | 18-PP-2301B FAULT | 1830-PS07-231 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-23102L | DCS | 18-PP-2301B REMOTE | 1830-PS07-231 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-23102R | DCS | 18-PP-2301B RUNNING | 1830-PS07-231 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-SI-23102 | DCS | 18-PP-2301B SPEED | 1830-PS07-231 | SI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 |  |  | AI-NIS | 1830 |  |  | -
1830 | 18-SC-23102 | DCS | 18-PP-2301B SPEED CONTROL | 1830-PS07-231 | SC | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AOR-NIS | 1830 |  |  | -
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-23105S | DCS | 18-PA-2301 START | 1830-PS07-231 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 2
1830 | 18-HS-23105P | DCS | 18-PA-2301 STOP | 1830-PS07-231 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 2
1830 | 18-YL-23105L | DCS | 18-PA-2301 REMOTE | 1830-PS07-231 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-23105R | DCS | 18-PA-2301 RUN | 1830-PS07-231 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-23105F | DCS | 18-PA-2301 FAULT | 1830-PS07-231 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-II-23105 | DCS | 18-PA-2301 CURRENT | 1830-PS07-231 | II | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 |  |  | AI-NIS | 1830 |  |  | -
1830 | 18-SI-23105 | DCS | 18-PA-2301 SPEED | 1830-PS07-231 | SI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 |  |  | AI-NIS | 1830 |  |  | -
1830 | 18-SC-23105 | DCS | 18-PA-2301 SPEED CONTROL | 1830-PS07-231 | SC | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AOR-NIS | 1830 |  |  | -
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-24101S | DCS | 18-PP-2401 START | 1830-PS07-241 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 2
1830 | 18-HS-24101P | DCS | 18-PP-2401 STOP | 1830-PS07-241 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 2
1830 | 18-YL-24101L | DCS | 18-PP-2401 REMOTE | 1830-PS07-241 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-24101R | DCS | 18-PP-2401 RUN | 1830-PS07-241 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-YL-24101F | DCS | 18-PP-2401 FAULT | 1830-PS07-241 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 2
1830 | 18-SI-24101 | DCS | 18-PP-2401 SPEED | 1830-PS07-241 | SI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 |  |  | AI-NIS | 1830 |  |  | -
1830 | 18-SC-24101 | DCS | 18-PP-2401 SPEED CONTROL | 1830-PS07-241 | SC | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AOR-NIS | 1830 |  |  | -
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-36106S | DCS | 18-PF-3606 START | 1830-PS07-361 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 3
1830 | 18-HS-36106P | DCS | 18-PF-3606 STOP | 1830-PS07-361 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 3
1830 | 18-YL-36106L | DCS | 18-PF-3606 REMOTE | 1830-PS07-361 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-YL-36106R | DCS | 18-PF-3606 RUN | 1830-PS07-361 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-YL-36106F | DCS | 18-PF-3606 FAULT | 1830-PS07-361 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-66101S | DCS | 18-PV-6601X START | 1830-PS07-661 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 6
1830 | 18-HS-66101P | DCS | 18-PV-6601X STOP | 1830-PS07-661 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 6
1830 | 18-YL-66101L | DCS | 18-PV-6601X REMOTE | 1830-PS07-661 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 6
1830 | 18-YL-66101R | DCS | 18-PV-6601X RUN | 1830-PS07-661 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 6
1830 | 18-YL-66101F | DCS | 18-PV-6601X FAULT | 1830-PS07-661 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 6
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-92101S | DCS | 18-PP-9201A START | 1830-PS07-921 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 9
1830 | 18-HS-92101P | DCS | 18-PP-9201A STOP | 1830-PS07-921 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 9
1830 | 18-YL-92101L | DCS | 18-PP-9201A REMOTE | 1830-PS07-921 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 9
1830 | 18-YL-92101R | DCS | 18-PP-9201A RUN | 1830-PS07-921 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 9
1830 | 18-YL-92101F | DCS | 18-PP-9201A FAULT | 1830-PS07-921 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 9
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-92102S | DCS | 18-PP-9201B START | 1830-PS07-921 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 9
1830 | 18-HS-92102P | DCS | 18-PP-9201B STOP | 1830-PS07-921 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 9
1830 | 18-YL-92102L | DCS | 18-PP-9201B REMOTE | 1830-PS07-921 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 9
1830 | 18-YL-92102R | DCS | 18-PP-9201B RUN | 1830-PS07-921 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 9
1830 | 18-YL-92102F | DCS | 18-PP-9201B FAULT | 1830-PS07-921 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 9
1830 | [19 empty] | AI-IS | 1830
1830 | 18-HS-HEF102AS | DCS | 边墙风机1830-HEF-102A/103A启动 | - | HS | DCS-DO | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  | 9 | F
1830 | 18-HS-HEF102BS | DCS | 边墙风机1830-HEF-102B/103B启动 | - | HS | DCS-DO | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  | 9 | F
1830 | 18-HS-HEF104AS | DCS | 边墙风机1830-HEF-104A启动 | - | HS | DCS-DO | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  | 9 | F
1830 | 18-HS-HEF104BS | DCS | 边墙风机1830-HEF-104B/105B启动 | - | HS | DCS-DO | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  | 9 | F
1830 | [19 empty] | AI-IS | 1830
1830 | 上海博隆风送系统 | [18 empty] | AI-IS | 1830
1830 | 18-HS-35103 | DCS | 排气过滤器18-FL-3501X反吹启/停控制 | 1830-PS07-351 | HS | DCS-DO | - | WET（NO） | WET | （NO） | 1 | 220VAC | - |  | - | - | C01 | 无电缆信息 |  | DO-24V | 1830 |  |  | -
1830 | 18-YL-35103RN | DCS | 排气过滤器18-FL-3501X反吹运行状态 | 1830-PS07-351 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 无电缆信息 |  | DI-RE | 1830 |  | 8 | 5
1830 | 18-LHS-35103REM | DCS | 排气过滤器18-FL-3501X反吹远程状态 | 1830-PS07-351 | LHS | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | - | C01 | 无电缆信息 |  | DI-RE | 1830 |  | 9 | 1
1830 | 18-PDI-35102 | DCS | 排气过滤器18-FL-3501X差压显示 | 1830-PS07-351 | PDI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0019 | AI-IS | 1830 |  |  | -
1830 | 18-XZH-35103 | DCS | 手动蝶阀18-BV-35103开状态 | 1830-PS07-351 | XZH | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0018 | DI-MI | 1830 |  |  | -
1830 | 18-XZL-35103 | DCS | 手动蝶阀18-BV-35103关状态 | 1830-PS07-351 | XZL | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0018 | DI-MI | 1830 |  |  | -
1830 | 18-PI-35101 | DCS | 粉料料仓18-VS-3501X顶部压力显示 | 1830-PS07-351 | PI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0019 | AI-IS | 1830 |  |  | -
1830 | 18-LAHH-35102 | DCS | 粉料料仓18-VS-3501X高高料位报警 | 1830-PS07-351 | LAHH | DCS-DI | - | DRY (NC) | DRY | (NC) | 1 | 24VDC | Yes |  | - | 四线制 | C01 | DCS | 18-3501-DJB-0018 | DI-IS | 1830 |  |  | -
1830 | 18-WI-35101 | DCS | 粉料料仓18-VS-3501X物料重量显示 | 1830-PS07-351 | WI | DCS-AI | - | 4~20mA | 4~20mA | 20mA | 1 | 220VAC | - |  | - | 四线制 | C01 | DCS | 18-LP-3501X | AI-NIS | 1830 |  |  | -
1830 | 18-LAHH-35103 | DCS | 粉料料仓18-VS-3501X低低料位报警 | 1830-PS07-351 | LAHH | DCS-DI | - | DRY (NC) | DRY | (NC) | 1 | 24VDC | Yes |  | - | 四线制 | C01 | DCS | 18-3501-DJB-0015 | DI-IS | 1830 |  |  | -
1830 | 18-XS-35104 | DCS | 控制角座阀18-XV-35104的开/关信号 | 1830-PS07-351 | XS | DCS-DO | - | WET（NO） | WET | （NO） | 1 | 24VDC | - |  | - | - | C01 | DCS | 18-3501-DJB-0016 | DO-24V | 1830 |  |  | -
1830 | 18-XS-35101 | DCS | 控制气动滑板阀18-XV-35101开/关信号 | 1830-PS07-351 | XS | DCS-DO | - | WET（NO） | WET | （NO） | 1 | 24VDC | - |  | - | - | C01 | 无电缆信息 |  | DO-24V | 1830 |  |  | -
1830 | 18-XZH-35101 | DCS | 气动滑板阀18-XV-35101开状态 | 1830-PS07-351 | XZH | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | 无电缆信息 |  | DI-MI | 1830 |  |  | -
1830 | 18-XZL-35101 | DCS | 气动滑板阀18-XV-35101关状态 | 1830-PS07-351 | XZL | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | 无电缆信息 |  | DI-MI | 1830 |  |  | -
1830 | 18-XS-35102 | DCS | 控制气动滑板阀18-XV-35102开/关信号 | 1830-PS07-351 | XS | DCS-DO | - | WET（NO） | WET | （NO） | 1 | 24VDC | - |  | - | - | C01 | 无电缆信息 |  | DO-24V | 1830 |  |  | -
1830 | 18-XZH-35102 | DCS | 气动滑板阀18-XV-35102开状态 | 1830-PS07-351 | XZH | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0015 | DI-MI | 1830 |  |  | -
1830 | 18-XZL-35102 | DCS | 气动滑板阀18-XV-35102关状态 | 1830-PS07-351 | XZL | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0015 | DI-MI | 1830 |  |  | -
1830 | 18-PIA-35108 | DCS | UP-3501系统循环线输送压力显示 | 1830-PS07-351 | PI | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0017 | AIR-IS | 1830 |  |  | -
1830 | 18-XS-35107 | DCS | 控制气动蝶阀18-XV-35107开/关信号 | 1830-PS07-351 | XS | DCS-DO | - | WET（NO） | WET | （NO） | 1 | 24VDC | - |  | - | - | C01 | DCS | 18-3501-DJB-0016 | DO-24V | 1830 |  |  | -
1830 | 18-XZH-35107 | DCS | 气动蝶阀18-XV-35107开状态 | 1830-PS07-351 | XZH | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0015 | DI-MI | 1830 |  |  | -
1830 | 18-XZL-35107 | DCS | 气动蝶阀18-XV-35107关状态 | 1830-PS07-351 | XZL | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0015 | DI-MI | 1830 |  |  | -
1830 | 18-PI-35205 | DCS | 输送氮气风机入口压力显示 | 1830-PS07-352 | PI | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 无电缆信息 |  | AIR-IS | 1830 |  |  | -
1830 | 18-PY-35201 | DCS | 输送氮气风机入口排气调节阀定位器 | 1830-PS07-352 | PY | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0010 | AOR-IS | 1830 |  |  | -
1830 | 18-PY-35205 | DCS | 输送氮气风机入口补气调节阀定位器 | 1830-PS07-352 | PY | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0010 | AOR-IS | 1830 |  |  | -
1830 | 18-FI-35201 | DCS | 输送氮气风机入口补气流量显示 | 1830-PS07-352 | FI | DCS-AO | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0009 | AOR-IS | 1830 |  |  | -
1830 | 18-AI-35201 | DCS | 输送氮气风机入口烃含量显示 | 1830-PS07-352 | AI | DCS-AI | Yes | 4~20mA | 4~20mA |  | 1 | 220VAC | - |  | - | 四线制 | C01 | SIS | 单拉 | AIR-NIS | 1830 |  |  | -
1830 | 18-AI-35202 | DCS | 输送氮气风机入口氧含量显示 | 1830-PS07-352 | AI | DCS-AI | Yes | 4~20mA | 4~20mA |  | 1 | 220VAC | - |  | - | 四线制 | C01 | 无电缆信息 |  | AIR-NIS | 1830 |  |  | -
1830 | 18-XS-35201 | DCS | 控制气动蝶阀18-XV-35201开/关信号 | 1830-PS07-352 | XS | DCS-DO | - | WET（NO） | WET | （NO） | 1 | 24VDC | - |  | - | - | C01 | DCS | 18-3501-DJB-0012 | DO-24V | 1830 |  |  | -
1830 | 18-XZH-35201 | DCS | 气动蝶阀18-XV-35201开状态 | 1830-PS07-352 | XZH | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0011 | DI-MI | 1830 |  |  | -
1830 | 18-XZL-35201 | DCS | 气动蝶阀18-XV-35201关状态 | 1830-PS07-352 | XZL | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0011 | DI-MI | 1830 |  |  | -
1830 | 18-PI-35201A | DCS | 风机18-PB-3501AX入口压力显示 | 1830-PS07-352 | PI | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0009 | AIR-IS | 1830 |  |  | 3
1830 | 18-PI-35201B | DCS | 风机18-PB-3501AX入口压力显示 | 1830-PS07-352 | PI | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0009 | AIR-IS | 1830 |  |  | 3
1830 | 18-TI-35204A | DCS | 输送氮气风机18-PB-3501AX主电机定子温度显示 | 1830-PS07-352 | TI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | Yes |  | - | - | C01 | DCS | 18-LP-KM-3501AX | AI-IS | 1830 |  |  | 3
1830 | 18-TI-35204B | DCS | 输送氮气风机18-PB-3501AX主电机定子温度显示 | 1830-PS07-352 | TI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | Yes |  | - | - | C01 | DCS | 18-LP-KM-3501AX | AI-IS | 1830 |  |  | 3
1830 | 18-TI-35204C | DCS | 输送氮气风机18-PB-3501AX主电机定子温度显示 | 1830-PS07-352 | TI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | Yes |  | - | - | C01 | DCS | 18-LP-KM-3501AX | AI-IS | 1830 |  |  | 3
1830 | 18-TI-35204D | DCS | 输送氮气风机18-PC-3501AX主电机轴承温度显示 | 1830-PS07-352 | TI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | Yes |  | - | - | C01 | DCS | 18-LP-KM-3501AX | AI-IS | 1830 |  |  | 3
1830 | 18-TI-35204E | DCS | 输送氮气风机18-PC-3501AX主电机轴承温度显示 | 1830-PS07-352 | TI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | Yes |  | - | - | C01 | DCS | 18-LP-KM-3501AX | AI-IS | 1830 |  |  | 3
1830 | 18-PASL-35203 | DCS | 输送氮气风机18-PB-3501AX入口压力低报警 | 1830-PS07-352 | PSAL | DCS-DI | - | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | -
1830 | 18-TASH-35202 | DCS | 输送氮气风机18-PB-3501AX出口温度高报警 | 1830-PS07-352 | TSAH | DCS-DI | - | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | DCS | 18-3501-DJB-0013 | DI-RE | 1830 |  |  | -
1830 | 18-PASH-35202 | DCS | 输送氮气风机18-PB-3501AX出口压力高报警 | 1830-PS07-352 | PSAH | DCS-DI | - | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 | DCS | 18-3501-DJB-0013 | DI-RE | 1830 |  |  | -
1830 | 18-XS-35202 | DCS | 控制气动蝶阀18-XV-35202开/关信号 | 1830-PS07-352 | XS | DCS-DO | - | WET（NO） | WET | （NO） | 1 | 24VDC | - |  | - | - | C01 | DCS | 18-3501-DJB-0012 | DO-24V | 1830 |  |  | -
1830 | 18-XZH-35202 | DCS | 气动蝶阀18-XV-35202开状态 | 1830-PS07-352 | XZH | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0011 | DI-MI | 1830 |  |  | -
1830 | 18-XZL-35202 | DCS | 气动蝶阀18-XV-35202关状态 | 1830-PS07-352 | XZL | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0011 | DI-MI | 1830 |  |  | -
1830 | 18-XS-35203 | DCS | 控制气动蝶阀18-XV-35203开/关信号 | 1830-PS07-352 | XS | DCS-DO | - | WET（NO） | WET | （NO） | 1 | 24VDC | - |  | - | - | C01 | DCS | 18-3501-DJB-0012 | DO-24V | 1830 |  |  | -
1830 | 18-XZH-35203 | DCS | 气动蝶阀18-XV-35203开状态 | 1830-PS07-352 | XZH | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0011 | DI-MI | 1830 |  |  | -
1830 | 18-XZL-35203 | DCS | 气动蝶阀18-XV-35203关状态 | 1830-PS07-352 | XZL | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0011 | DI-MI | 1830 |  |  | -
1830 | 18-PI-35211A | DCS | 风机18-PB-3501BX入口压力显示 | 1830-PS07-352 | PI | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0009 | AIR-IS | 1830 |  |  | 3
1830 | 18-PI-35211B | DCS | 风机18-PB-3501BX入口压力显示 | 1830-PS07-352 | PI | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0009 | AIR-IS | 1830 |  |  | 3
1830 | 18-TI-35214A | DCS | 输送氮气风机18-PB-3501BX主电机定子温度显示 | 1830-PS07-352 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-LP-KM-3501BX | AI-IS | 1830 |  |  | 3
1830 | 18-TI-35214B | DCS | 输送氮气风机18-PB-3501BX主电机定子温度显示 | 1830-PS07-352 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-LP-KM-3501BX | AI-IS | 1830 |  |  | 3
1830 | 18-TI-35214C | DCS | 输送氮气风机18-PB-3501BX主电机定子温度显示 | 1830-PS07-352 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-LP-KM-3501BX | AI-IS | 1830 |  |  | 3
1830 | 18-TI-35214D | DCS | 输送氮气风机18-PC-3501BX主电机轴承温度显示 | 1830-PS07-352 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-LP-KM-3501BX | AI-IS | 1830 |  |  | 3
1830 | 18-TI-35214E | DCS | 输送氮气风机18-PC-3501BX主电机轴承温度显示 | 1830-PS07-352 | TI | DCS-AI | - | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-LP-KM-3501BX | AI-IS | 1830 |  |  | 3
1830 | 18-PASL-35213 | DCS | 输送氮气风机18-PC-3501BX入口压力低报警 | 1830-PS07-352 | PSAL | DCS-DI | - | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | - | C01 | DCS | 18-3501-DJB-0013 | DI-RE | 1830 |  |  | -
1830 | 18-TASH-35212 | DCS | 输送氮气风机18-PC-3501BX出口温度高报警 | 1830-PS07-352 | TSAH | DCS-DI | - | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | - | C01 | DCS | 18-3501-DJB-0013 | DI-RE | 1830 |  |  | -
1830 | 18-PASH-35212 | DCS | 输送氮气风机18-PC-3501BX出口压力高报警 | 1830-PS07-352 | PSAL | DCS-DI | - | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | - | C01 | DCS | 18-3501-DJB-0013 | DI-RE | 1830 |  |  | -
1830 | 18-XS-35204 | DCS | 控制气动蝶阀18-XV-35204开/关信号 | 1830-PS07-352 | XS | DCS-DO | - | WET（NO） | WET | （NO） | 1 | 24VDC | - |  | - | - | C01 | DCS | 18-3501-DJB-0012 | DO-24V | 1830 |  |  | -
1830 | 18-XZH-35204 | DCS | 气动蝶阀18-XV-35204开状态 | 1830-PS07-352 | XZH | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0011 | DI-MI | 1830 |  |  | -
1830 | 18-XZL-35204 | DCS | 气动蝶阀18-XV-35204关状态 | 1830-PS07-352 | XZL | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0011 | DI-MI | 1830 |  |  | -
1830 | 18-TI-35201 | DCS | 输送氮气风机出口温度显示 | 1830-PS07-352 | TI | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0009 | AIR-IS | 1830 |  |  | -
1830 | 18-XS-35206 | DCS | 控制气动蝶阀18-XV-35206开/关信号 | 1830-PS07-352 | XS | DCS-DO | - | WET（NO） | WET | （NO） | 1 | 24VDC | - |  | - | - | C01 | DCS | 18-3501-DJB-0012 | DO-24V | 1830 |  |  | -
1830 | 18-XZH-35206 | DCS | 气动蝶阀18-XV-35206开状态 | 1830-PS07-352 | XZH | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0011 | DI-MI | 1830 |  |  | -
1830 | 18-XZL-35206 | DCS | 气动蝶阀18-XV-35206关状态 | 1830-PS07-352 | XZL | DCS-DI | - | NAMUR(NC) | NAMUR | (NC) | 1 | - | Yes |  | - | - | C01 | DCS | 18-3501-DJB-0011 | DI-MI | 1830 |  |  | -
1830 | 18-PI-35204 | DCS | 输送氮气出口冷却器EM-3502X出口压力显示 | 1830-PS07-352 | PI | DCS-AI | Yes | 4~20mA HART | 4~20mA | HART | 1 | - | Yes |  | - | - | C01 | 无电缆信息 |  | AIR-IS | 1830 |  |  | -
1830 | [20 empty] | 1830
1830 | 18-YL-35201L | DCS | 输送氮气风机18-PB-3501AX主电机远程状态 | 1830-PS07-352 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-HS-35201P | DCS | 输送氮气风机18-PB-3501AX主电机停止控制 | 1830-PS07-352 | HS | DCS-DO | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 3
1830 | 18-HS-35201S | DCS | 输送氮气风机18-PB-3501AX主电机启动控制 | 1830-PS07-352 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 3
1830 | 18-HS-35201L | DCS | 输送氮气风机18-PB-3501AX主电机允许启动 | 1830-PS07-352 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 3
1830 | 18-YL-35201R | DCS | 输送氮气风机18-PB-3501AX主电机运行状态 | 1830-PS07-352 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-YL-35201F | DCS | 输送氮气风机18-PB-3501AX主电机故障状态 | 1830-PS07-352 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-II-35201 | DCS | 输送氮气风机18-PB-3501AX主电机电流显示 | 1830-PS07-352 | II | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 |  |  | AI-NIS | 1830 |  |  | -
1830 | [20 empty] | 1830
1830 | 18-YL-35202L | DCS | 输送氮气风机18-PB-3501BX主电机远程状态 | 1830-PS07-352 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-HS-35202P | DCS | 输送氮气风机18-PB-3501BX主电机停止控制 | 1830-PS07-352 | HS | DCS-DO | Yes | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 3
1830 | 18-HS-35202S | DCS | 输送氮气风机18-PB-3501BX主电机启动控制 | 1830-PS07-352 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 3
1830 | 18-HS-35202L | DCS | 输送氮气风机18-PB-3501BX主电机允许启动 | 1830-PS07-352 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 3
1830 | 18-YL-35202R | DCS | 输送氮气风机18-PB-3501BX主电机运行状态 | 1830-PS07-352 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-YL-35202F | DCS | 输送氮气风机18-PB-3501BX主电机故障状态 | 1830-PS07-352 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-II-35202 | DCS | 输送氮气风机18-PB-3501BX主电机电流显示 | 1830-PS07-352 | II | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 |  |  | AI-NIS | 1830 |  |  | -
1830 | [20 empty] | 1830
1830 | 18-HS-35102P | DCS | 粉料循环旋转阀18-PF-3502X的停止控制 | 1830-PS07-351 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 3
1830 | 18-HS-35102S | DCS | 粉料循环旋转阀18-PF-3502X的启动控制 | 1830-PS07-351 | HS | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 3
1830 | 18-YL-35102R | DCS | 粉料循环旋转阀18-PF-3502X的运行状态 | 1830-PS07-351 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-YL-35102F | DCS | 粉料循环旋转阀18-PF-3502X的故障状态 | 1830-PS07-351 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-YL-35102L | DCS | 粉料循环旋转阀18-PF-3502X的远程状态 | 1830-PS07-351 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | [20 empty] | 1830
1830 | 18-HS-35101P | DCS | 粉料仓旋转阀18-PF-3501X的停止控制 | 1830-PS07-351 | HS | DCS-DO | Yes | DRY (NC) | DRY | (NC) | 1 | - | - |  | - | MCC | C01 |  |  | DOR-Dry | 1830 |  |  | 3
1830 | 18-HSF-35101S | DCS | 粉料仓旋转阀18-PF-3501X的正转启动控制 | 1830-PS07-351 | HSF | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 3
1830 | 18-HSR-35101S | DCS | 粉料仓旋转阀18-PF-3501X的反转启动控制 | 1830-PS07-351 | HSR | DCS-DO | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DO-Dry | 1830 |  |  | 3
1830 | 18-YLF-35101R | DCS | 粉料仓旋转阀18-PF-3501X的正转运行状态 | 1830-PS07-351 | YLF | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-YLR-35101R | DCS | 粉料仓旋转阀18-PF-3501X的反转运行状态 | 1830-PS07-351 | YLR | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-YL-35101F | DCS | 粉料仓旋转阀18-PF-3501X的故障状态 | 1830-PS07-351 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-YL-35101L | DCS | 粉料仓旋转阀18-PF-3501X的远程状态 | 1830-PS07-351 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3
1830 | 18-SC-35101 | DCS | 粉料仓旋转阀18-PF-3501X的速度控制 | 1830-PS07-351 | SC | DCS-AO | Yes | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 | MCC |  | AOR-NIS | 1830 |  |  | -
1830 | 18-SI-35101 | DCS | 粉料仓旋转阀18-PF-3501X的速度显示 | 1830-PS07-351 | SI | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 |  |  | AI-NIS | 1830 |  |  | -
1830 | 18-II-35101 | DCS | 粉料仓旋转阀18-PF-3501X的电流显示 | 1830-PS07-351 | II | DCS-AI | - | 4~20mA | 4~20mA |  | 1 | - | - |  | - | MCC | C01 |  |  | AI-NIS | 1830 |  |  | -
1830 | [20 empty] | 1830
1830 | 18-YL-35111R | DCS | 粉料仓旋转阀18-PF-3501X的风扇运行状态 | 1830-PS07-351 | YL | DCS-DI | - | DRY (NO) | DRY | (NO) | 1 | - | - |  | - | MCC | C01 |  |  | DI-RE | 1830 |  |  | 3

## 卡件布置
|  | FCS0304 Node 1 | [10 empty] | FCS0304 Node 6
| Channel | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 |  |  |  |  | Channel | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8 |  | AIR(Hart)4-20mA | 4~20ma | NIS
|  | AAI143-H | AAI143-H | AAI543-H | AAI543-H | ADV151-P | ADV151-P | [5 empty] | AAI143-H | AAI143-H | AAI543-H | AAI543-H | ADCV01 | ADCV01 | ADV551-P | ADV551-P |  |  | 安全栅 | IS
|  | 16 |  | 16 |  | 32 | [6 empty] | 16 |  | 16 |  |  |  | 32 |  |  |  | 输入隔离器 | ISO
|  | IS | R | IS | R | MI | R | [5 empty] | IS | R | NIS | R |  |  | Dry | R |  |  | Pt100+温变 | Pt
[23 empty] | 浪涌 | SU
Node 1 | 1 | 18-PT-62302 |  | 18-PV-62301 |  | 18-LS-36202 |  |  |  |  | Node 6 | 1 | 18-PT-24101 |  | 18-SC-17201 |  |  |  | 18-HS-61201P |  |  | AOR(Hart)4-20mA | 4~20ma | NIS
| 2 | 18-FT-62301 |  | 18-FXV-61103 |  | Spare | [5 empty] | 2 | 18-LT-23101 |  | 18-SC-17202 |  |  |  | 18-HS-61202P |  |  |  | 安全栅 | IS
| 3 | 18-FT-62101 |  | 18-FXV-61104 |  | Spare | [5 empty] | 3 | 18-LT-23102 |  | 18-SC-17203 |  |  |  | 18-HS-61203P |  |  |  | 输出隔离器 | ISO
| 4 | 18-FT-62103 |  | 18-FXV-62101 |  | Spare | [5 empty] | 4 | 18-LT-24101 |  | 18-SC-17204 |  |  |  | 18-HS-62101P |  |  | DIRNAMUR | 继电器 | MR
| 5 | 18-LT-62201 |  | 18-FV-62103 |  | Spare | [5 empty] | 5 | 18-PT-23101 |  | 18-SC-17301 |  |  |  | 18-HS-62102P |  |  |  | 安全栅 | MI
| 6 | 18-LT-62301 |  | 18-FV-62104 |  | Spare | [5 empty] | 6 | 18-PT-66101 |  | Spare |  |  |  | Spare |  |  | DIR（干接点） | 安全栅 | IS
| 7 | 18-TT-62205 |  | 18-FV-62105 |  | Spare | [5 empty] | 7 | 18-PT-66102 |  | Spare |  |  |  | Spare |  |  |  | 继电器 | RE
| 8 | 18-PT-61108 |  | 18-FV-62301 |  | Spare | [5 empty] | 8 | 18-PI-35201A |  | Spare |  |  |  | Spare |  |  | DOR（中间继电器） | 干接点 | dry
| 9 | 18-FT-61103 |  | 18-TV-62202 |  | Spare | [5 empty] | 9 | 18-PI-35201B |  | Spare |  |  |  | Spare |  |  |  | 湿接点 | 24v
| 10 | 18-FT-61104 |  | 18-PXV-61103A |  | Spare | [5 empty] | 10 | 18-PI-35211A |  | Spare |  |  |  | Spare |  |  | AI(Hart)4-20mA | 4-20mA | NIS
| 11 | 18-LT-61103 |  | 18-PV-63104B |  | Spare | [5 empty] | 11 | 18-PI-35211B |  | Spare |  |  |  | Spare |  |  |  | 安全栅 | IS
| 12 | Spare |  | 18-LV-61202 |  | Spare | [5 empty] | 12 | 18-TI-35201 |  | Spare |  |  |  | Spare |  |  |  | 输入隔离器 | ISO
| 13 | Spare |  | 18-LV-61203 |  | Spare | [5 empty] | 13 | Spare |  | Spare |  |  |  | Spare |  |  |  | Pt100+温变 | Pt
| 14 | Spare |  | Spare |  | Spare | [5 empty] | 14 | Spare |  | Spare |  |  |  | Spare |  |  |  | 浪涌 | SU
| 15 | Spare |  | Spare |  | Spare | [5 empty] | 15 | Spare |  | Spare |  |  |  | Spare |  |  | AO(Hart)4-20mA | 4~20ma | NIS
| 16 | Spare |  | Spare |  | Spare | [5 empty] | 16 | Spare |  | Spare |  |  |  | Spare |  |  |  | 安全栅 | IS
| 17 |  |  |  |  | Spare | [5 empty] | 17 | [6 empty] | Spare |  |  |  | 隔离器 | ISO
| 18 |  |  |  |  | Spare | [5 empty] | 18 | [6 empty] | Spare |  |  | DINAMUR | 继电器 | MR
| 19 |  |  |  |  | Spare | [5 empty] | 19 | [6 empty] | Spare |  |  |  | 安全栅 | MI
| 20 |  |  |  |  | Spare | [5 empty] | 20 | [6 empty] | Spare |  |  | DI（干接点） | 继电器 | RE
| 21 |  |  |  |  | Spare | [5 empty] | 21 | [6 empty] | Spare |  |  |  | 安全栅 | IS
| 22 |  |  |  |  | Spare | [5 empty] | 22 | [6 empty] | Spare |  |  | DO（中间继电器） | 干接点 | dry
| 23 |  |  |  |  | Spare | [5 empty] | 23 | [6 empty] | Spare |  |  |  | 湿接点 | 24v
| 24 |  |  |  |  | Spare | [5 empty] | 24 | [6 empty] | Spare |  |  | PI | 脉冲 | PI
| 25 |  |  |  |  | Spare | [5 empty] | 25 | [6 empty] | Spare
| 26 |  |  |  |  | Spare | [5 empty] | 26 | [6 empty] | Spare
| 27 |  |  |  |  | Spare | [5 empty] | 27 | [6 empty] | Spare
| 28 |  |  |  |  | Spare | [5 empty] | 28 | [6 empty] | Spare
| 29 |  |  |  |  | Spare | [5 empty] | 29 | [6 empty] | Spare
| 30 |  |  |  |  | Spare | [5 empty] | 30 | [6 empty] | Spare
| 31 |  |  |  |  | Spare | [5 empty] | 31 | [6 empty] | Spare
| 32 |  |  |  |  | Spare | [5 empty] | 32 | [6 empty] | Spare
I/O numbeE | [10 empty] | I/O numbeE
|  | FCS0304 Node 2 | [10 empty] | FCS0304 Node 7
| Channel | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8 |  |  | Channel | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8
|  | AAI143-H | AAI143-H | AAI543-H | AAI543-H | ADV151-P | ADCV01 | ADV151-P | ADV151-P |  |  |  | AAI143-H | AAI143-H | AAI543-H | AAI543-H | ADCV01 | ADCV01 | ADV551-P | ADV551-P
|  | 16 |  | 16 |  | 32 |  | 32 | 32 |  |  |  | 16 |  | 16 |  |  |  | 32
|  | IS | R | IS | R | IS |  | MI | MI |  |  |  | NIS | R | NIS | R |  |  | Dry | R
Node 2 | 1 | 18-PT-62202 |  | 18-PV-61103B |  | 18-LAHH-35102 |  | 18-XZSH-62301 | 18-PZSL-61103A |  | Node 7 | 1 | 18-FT-62104 |  | 18-SC-23101 |  |  |  | 18-HS-17201P
| 2 | 18-PDT-62108 |  | 18-PV-61109 |  | 18-LAHH-35103 |  | 18-XZSL-62301 | 18-PZSL-61202 |  |  | 2 | 18-FT-62105 |  | 18-SC-23102 |  |  |  | 18-HS-17202P
| 3 | 18-LT-61203 |  | 18-PV-61202 |  | Spare |  | 18-XZSH-62302 | 18-PZSL-61204 |  |  | 3 | 18-FT-21103 |  | 18-SC-23105 |  |  |  | 18-HS-17203P
| 4 | 18-LT-62105 |  | 18-PV-61204 |  | Spare |  | 18-XZSL-62302 | 18-PZSL-61210 |  |  | 4 | 18-FT-23101 |  | 18-SC-24101 |  |  |  | 18-HS-17204P
| 5 | 18-TT-61207 |  | 18-PV-61210 |  | Spare |  | 18-XZSH-62303 | 18-PZSL-62104 |  |  | 5 | 18-FT-24101 |  | 18-SC-35101 |  |  |  | 18-HS-17301P
| 6 | 18-FT-61201 |  | 18-PV-62104 |  | Spare |  | 18-XZSL-62303 | 18-FZSL-61201 |  |  | 6 | 18-FT-36103 |  | Spare |  |  |  | 18-HS-17109P
| 7 | 18-LT-61101 |  | 18-PV-63104A |  | Spare |  | 18-FZSL-61103 | 18-FZSL-61202 |  |  | 7 | 18-AT-66101 |  | Spare |  |  |  | Spare
| 8 | 18-LT-61205 |  | 18-FV-61201 |  | Spare |  | 18-FZSL-62101 | 18-LZSL-61201 |  |  | 8 | 18-AI-35201 |  | Spare |  |  |  | Spare
| 9 | 18-TT-62202 |  | 18-FV-61202 |  | Spare |  | 18-XZSH-61105 | 18-LZSL-61202 |  |  | 9 | 18-AI-35202 |  | Spare |  |  |  | Spare
| 10 | 18-PT-61210 |  | 18-LV-61201 |  | Spare |  | 18-XZSL-61105 | 18-LZSL-61203 |  |  | 10 | Spare |  | Spare |  |  |  | Spare
| 11 | 18-LT-61201 |  | Spare |  | Spare |  | 18-XZSH-62101 | 18-XZSH-61102 |  |  | 11 | Spare |  | Spare |  |  |  | Spare
| 12 | 18-LT-62101 |  | Spare |  | Spare |  | 18-XZSL-62101 | 18-XZSL-61102 |  |  | 12 | Spare |  | Spare |  |  |  | Spare
| 13 | Spare |  | Spare |  | Spare |  | 18-FZSL-61104 | 18-XZSH-61103 |  |  | 13 | Spare |  | Spare |  |  |  | Spare
| 14 | Spare |  | Spare |  | Spare |  | 18-FZSL-62104 | 18-XZSL-61103 |  |  | 14 | Spare |  | Spare |  |  |  | Spare
| 15 | Spare |  | Spare |  | Spare |  | 18-FZSL-62105 | 18-XZSH-61106 |  |  | 15 | Spare |  | Spare |  |  |  | Spare
| 16 | Spare |  | Spare |  | Spare |  | 18-XZSH-61104 | 18-XZSL-61106 |  |  | 16 | Spare |  | Spare |  |  |  | Spare
| 17 |  |  |  |  | Spare |  | 18-XZSL-61104 | 18-XZSH-61201 |  |  | 17 | [6 empty] | Spare
| 18 |  |  |  |  | Spare |  | 18-XZSH-62105 | 18-XZSL-61201 |  |  | 18 | [6 empty] | Spare
| 19 |  |  |  |  | Spare |  | 18-XZSL-62105 | 18-XZSH-61206 |  |  | 19 | [6 empty] | Spare
| 20 |  |  |  |  | Spare |  | 18-XZSH-62106 | 18-XZSL-61206 |  |  | 20 | [6 empty] | Spare
| 21 |  |  |  |  | Spare |  | 18-XZSL-62106 | 18-XZSH-17101 |  |  | 21 | [6 empty] | Spare
| 22 |  |  |  |  | Spare |  | 18-LS-17108 | 18-XZSL-17101 |  |  | 22 | [6 empty] | Spare
| 23 |  |  |  |  | Spare |  | 18-XZSH-17108 | 18-XZSH-17102 |  |  | 23 | [6 empty] | Spare
| 24 |  |  |  |  | Spare |  | 18-XZSL-17108 | 18-XZSL-17102 |  |  | 24 | [6 empty] | Spare
| 25 |  |  |  |  | Spare |  | 18-XZSH-17111 | 18-XZSH-17103 |  |  | 25 | [6 empty] | Spare
| 26 |  |  |  |  | Spare |  | 18-XZSL-17111 | 18-XZSL-17103 |  |  | 26 | [6 empty] | Spare
| 27 |  |  |  |  | Spare |  | Spare | 18-XZSH-17105 |  |  | 27 | [6 empty] | Spare
| 28 |  |  |  |  | Spare |  | Spare | 18-XZSL-17105 |  |  | 28 | [6 empty] | Spare
| 29 |  |  |  |  | Spare |  | Spare | Spare |  |  | 29 | [6 empty] | Spare
| 30 |  |  |  |  | Spare |  | Spare | Spare |  |  | 30 | [6 empty] | Spare
| 31 |  |  |  |  | Spare |  | Spare | Spare |  |  | 31 | [6 empty] | Spare
| 32 |  |  |  |  | Spare |  | Spare | Spare |  |  | 32 | [6 empty] | Spare
I/O numbeE | [10 empty] | I/O numbeE
|  | FCS0304 Node 3 | [10 empty] | FCS0304 Node 8
| Channel | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8 |  |  | Channel | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8
|  | AAI143-H | AAI143-H | AAI543-H | AAI543-H | ALE111 | ADCV01 | ADV151-P | ADV151-P |  |  |  | AAI143-H | AAI143-H | AAI143-H | AAI143-H | ADCV01 | ADCV01 | ADV551-P | ADV551-P
|  | 16 |  | 16 |  | modbus |  | 32 | 32 |  |  |  | 16 | 16 | 16 | 16 |  |  | 32
|  | IS | R | IS | R |  |  | MI | MI |  |  |  | IS | IS | IS | IS |  |  | Dry | R
Node 3 | 1 | 18-PT-61109 |  | 18-PV-17106A |  |  |  | 18-XZSH-17104 | 18-XZSH-66105 |  | Node 8 | 1 | 18-TT-62302 | 18-TT-61203 | 18-TT-61107 | 18-TT-61103 |  |  | 18-HS-21103P
| 2 | 18-PT-61202 |  | 18-PV-17106B |  |  |  | 18-XZSL-17104 | 18-XZSL-66105 |  |  | 2 | 18-PT-62303 | 18-TT-62107 | 18-TT-61108 | 18-TT-61201 |  |  | 18-HS-21104P
| 3 | 18-PT-61204 |  | 18-PV-17301 |  |  |  | 18-XZSH-17106 | 18-XZSH-66106 |  |  | 3 | 18-PT-61281A | 18-TT-62108 | 18-TT-61208 | 18-TT-61209 |  |  | 18-HS-21102P
| 4 | 18-PT-62104 |  | 18-PV-17302A |  |  |  | 18-XZSL-17106 | 18-XZSL-66106 |  |  | 4 | 18-PT-61281B | 18-TT-62203 | 18-FT-61101 | 18-PDT-61211 |  |  | 18-HS-23101P
| 5 | 18-FT-61202 |  | 18-PV-17302B |  |  |  | 18-XZSH-17107 | 18-XZH-35201 |  |  | 5 | 18-PT-61283 | 18-FT-62201 | 18-TT-61104 | 18-FT-62202 |  |  | 18-HS-23102P
| 6 | 18-TT-61105 |  | 18-FI-17105B |  |  |  | 18-XZSL-17107 | 18-XZL-35201 |  |  | 6 | 18-PT-62181A | 18-LT-63103 | 18-TT-61106 | 18-PT-17202 |  |  | 18-HS-23105P
| 7 | 18-PT-61103 |  | 18-LI-17102 |  |  |  | 18-XZSH-21101 | 18-XZH-35202 |  |  | 7 | 18-PT-62181B | 18-TT-61205 | 18-TT-62101 | 18-PT-17204 |  |  | 18-HS-24101P
| 8 | 18-PT-63104 |  | 18-LI-17103 |  |  |  | 18-XZSL-21101 | 18-XZL-35202 |  |  | 8 | 18-TT-61110 | 18-TT-61206 | 18-TT-62102 | 18-PT-17206 |  |  | 18-HS-36106P
| 9 | 18-LT-61202 |  | 18-LI-17104B |  |  |  | 18-XZSH-21103 | 18-XZH-35203 |  |  | 9 | 18-TT-62301 | 18-TT-63101 | 18-TT-62103 | 18-PT-17208 |  |  | 18-HS-66101P
| 10 | 18-PT-62301 |  | 18-TI-21101 |  |  |  | 18-XZSL-21103 | 18-XZL-35203 |  |  | 10 | 18-TT-61102 | 18-PT-62103 | 18-TT-62104 | 18-LT-17107 |  |  | 18-HS-92101P
| 11 | 18-LT-66101 |  | 18-LI-21101 |  |  |  | 18-XZSH-21104 | 18-XZH-35204 |  |  | 11 | 18-TT-61109 | 18-PDT-61104 | 18-PDT-62101 | Spare |  |  | 18-HS-92102P
| 12 | 18-LT-23103 |  | Spare |  |  |  | 18-XZSL-21104 | 18-XZL-35204 |  |  | 12 | Spare | Spare | Spare | Spare |  |  | 18-HS-HEF102AS
| 13 | Spare |  | Spare |  |  |  | 18-XZSH-36101 | 18-XZH-35206 |  |  | 13 | Spare | Spare | Spare | Spare |  |  | 18-HS-HEF102BS
| 14 | Spare |  | Spare |  |  |  | 18-XZSL-36101 | 18-XZL-35206 |  |  | 14 | Spare | Spare | Spare | Spare |  |  | 18-HS-HEF104AS
| 15 | Spare |  | Spare |  |  |  | 18-XZSH-36102 | 18-XZH-35102 |  |  | 15 | Spare | Spare | Spare | Spare |  |  | 18-HS-HEF104BS
| 16 | Spare |  | Spare |  |  |  | 18-XZSL-36102 | 18-XZL-35102 |  |  | 16 | Spare | Spare | Spare | Spare |  |  | 18-HS-35201P
| 17 | [6 empty] | 18-XZSH-23101 | 18-XZH-35107 |  |  | 17 | [6 empty] | 18-HS-35202P
| 18 | [6 empty] | 18-XZSL-23101 | 18-XZL-35107 |  |  | 18 | [6 empty] | 18-HS-35102P
| 19 | [6 empty] | 18-XZSH-24102 | 18-XZH-35103 |  |  | 19 | [6 empty] | 18-HS-35101P
| 20 | [6 empty] | 18-XZSL-24102 | 18-XZL-35103 |  |  | 20 | [6 empty] | Spare
| 21 | [6 empty] | 18-PZSL-66102 | 18-XZH-35101 |  |  | 21 | [6 empty] | Spare
| 22 | [6 empty] | 18-HZSH-66102 | 18-XZL-35101 |  |  | 22 | [6 empty] | Spare
| 23 | [6 empty] | 18-HZSL-66102 | Spare |  |  | 23 | [6 empty] | Spare
| 24 | [6 empty] | 18-XZSH-66101 | Spare |  |  | 24 | [6 empty] | Spare
| 25 | [6 empty] | 18-XZSL-66101 | Spare |  |  | 25 | [6 empty] | Spare
| 26 | [6 empty] | Spare | Spare |  |  | 26 | [6 empty] | Spare
| 27 | [6 empty] | Spare | Spare |  |  | 27 | [6 empty] | Spare
| 28 | [6 empty] | Spare | Spare |  |  | 28 | [6 empty] | Spare
| 29 | [6 empty] | Spare | Spare |  |  | 29 | [6 empty] | Spare
| 30 | [6 empty] | Spare | Spare |  |  | 30 | [6 empty] | Spare
| 31 | [6 empty] | Spare | Spare |  |  | 31 | [6 empty] | Spare
| 32 | [6 empty] | Spare | Spare |  |  | 32 | [6 empty] | Spare
I/O numbeE | [10 empty] | I/O numbeE
|  | FCS0304 Node 4 | [10 empty] | FCS0304 Node 9
| Channel | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8 |  |  | Channel | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8
|  | AAI143-H | AAI143-H | AAI543-H | AAI543-H | ALE111 | ADCV01 | ADV151-P | ADV151-P |  |  |  | AAI143-H | AAI143-H | ADV151-P | ADV151-P | ADCV01 | ADCV01 | ADV551-P | ADV551-P
|  | 16 |  | 16 |  | modbus |  | 32 |  |  |  |  | 16 | 16 | 32 | 32 |  |  | 32
|  | IS | R | IS | R |  |  | IS | R |  |  |  | IS | IS | RE | RE |  |  | 24V | R
Node 4 | 1 | 18-TT-17104 |  | 18-PV-24101A |  |  |  | 18-YS-17101 |  |  | Node 9 | 1 | 18-TT-21101 | 18-PDI-35102 | 18-HS-61101A | 18-XHSO-17111 |  |  | 18-PN-62104
| 2 | 18-LT-17104 |  | 18-PV-24101B |  |  |  | 18-YS-17102 |  |  |  | 2 | 18-TT-36102 | 18-PI-35101 | 18-HS-61101B | 18-XHSC-17111 |  |  | 18-XN-61105
| 3 | 18-LT-17109 |  | 18-FV-36103 |  |  |  | 18-YS-24103 |  |  |  | 3 | 18-TT-92101 | 18-TI-35204A | 18-HS-61102 | 18-YL-17201R |  |  | 18-XN-61201
| 4 | 18-LT-17301 |  | 18-LV-66202 |  |  |  | Spare |  |  |  | 4 | 18-TT-92102 | 18-TI-35204B | 18-YL-61201R | 18-YL-17201F |  |  | 18-XN-61206
| 5 | 18-PT-17106 |  | 18-HV-36105 |  |  |  | Spare |  |  |  | 5 | 18-PDT-23105 | 18-TI-35204C | 18-YL-61201F | 18-YL-17202R |  |  | 18-XN-62106
| 6 | 18-PT-17301 |  | 18-PV-21110 |  |  |  | Spare |  |  |  | 6 | 18-PDT-24103 | 18-TI-35204D | 18-YL-61202R | 18-YL-17202F |  |  | 18-XN-62301
| 7 | 18-PT-17302 |  | 18-FV-21103A |  |  |  | Spare |  |  |  | 7 | 18-LT-66203 | 18-TI-35204E | 18-YL-61202F | 18-YL-17203R |  |  | 18-XN-62302
| 8 | 18-FT-17108 |  | 18-FV-21103B |  |  |  | Spare |  |  |  | 8 | 18-PT-92101 | 18-TI-35214A | 18-YL-61203R | 18-YL-17203F |  |  | 18-XN-17101
| 9 | 18-LT-17101 |  | 18-PV-23101A |  |  |  | Spare |  |  |  | 9 | 18-FT-21107 | 18-TI-35214B | 18-YL-61203F | 18-YL-17204R |  |  | 18-XN-17102
| 10 | 18-LT-17102 |  | 18-PV-23101B |  |  |  | Spare |  |  |  | 10 | 18-TT-23102 | 18-TI-35214C | 18-YL-62101L | 18-YL-17204F |  |  | 18-XN-17103
| 11 | 18-LT-17103 |  | 18-PV-66102 |  |  |  | Spare |  |  |  | 11 | 18-TT-66101 | 18-TI-35214D | 18-YL-62101R | 18-YL-17301R |  |  | 18-XN-17104
| 12 | 18-PI-35204 |  | 18-HV-66102 |  |  |  | Spare |  |  |  | 12 | 18-TT-23101 | 18-TI-35214E | 18-YL-62101F | 18-YL-17301F |  |  | 18-XN-17105
| 13 | 18-PI-35205 |  | Spare |  |  |  | Spare |  |  |  | 13 | 18-TT-66104 | Spare | 18-YL-62102L | 18-YL-17109R |  |  | 18-XN-17106
| 14 | Spare |  | Spare |  |  |  | Spare |  |  |  | 14 | Spare | Spare | 18-YL-62102R | 18-YL-17109F |  |  | 18-XN-17107
| 15 | Spare |  | Spare |  |  |  | Spare |  |  |  | 15 | Spare | Spare | 18-YL-62102F | 18-XHSO-21101 |  |  | 18-XN-17111
| 16 | Spare |  | Spare |  |  |  | Spare |  |  |  | 16 | Spare | Spare | Spare | 18-XHSC-21101 |  |  | 18-PN-66102
| 17 | [6 empty] | Spare |  |  |  | 17 |  |  | 18-HS-17102B | 18-XHSO-24102 |  |  | 18-XN-21101
| 18 | [6 empty] | Spare |  |  |  | 18 |  |  | 18-HS-17103 | 18-XHSC-24102 |  |  | 18-XN-21103
| 19 | [6 empty] | Spare |  |  |  | 19 |  |  | 18-HS-17104 | 18-XHSO-66101 |  |  | 18-XN-21104
| 20 | [6 empty] | Spare |  |  |  | 20 |  |  | 18-HS-17105 | 18-XHSC-66101 |  |  | 18-XN-23101
| 21 | [6 empty] | Spare |  |  |  | 21 |  |  | 18-HS-17106 | Spare |  |  | 18-XN-24102
| 22 | [6 empty] | Spare |  |  |  | 22 |  |  | 18-HS-17108 | Spare |  |  | 18-XN-36101A
| 23 | [6 empty] | Spare |  |  |  | 23 |  |  | 18-XHSO-17106 | Spare |  |  | 18-XN-36102A
| 24 | [6 empty] | Spare |  |  |  | 24 |  |  | 18-XHSC-17106 | Spare |  |  | 18-XN-66101
| 25 | [6 empty] | Spare |  |  |  | 25 |  |  | 18-XHSO-17107 | Spare |  |  | 18-XN-66105
| 26 | [6 empty] | Spare |  |  |  | 26 |  |  | 18-XHSC-17107 | Spare |  |  | 18-XN-66106
| 27 | [6 empty] | Spare |  |  |  | 27 |  |  | 18-HS-17109A | Spare |  |  | Spare
| 28 | [6 empty] | Spare |  |  |  | 28 |  |  | 18-HS-17109B | Spare |  |  | Spare
| 29 | [6 empty] | Spare |  |  |  | 29 |  |  | Spare | Spare |  |  | Spare
| 30 | [6 empty] | Spare |  |  |  | 30 |  |  | Spare | Spare |  |  | Spare
| 31 | [6 empty] | Spare |  |  |  | 31 |  |  | Spare | Spare |  |  | Spare
| 32 | [6 empty] | Spare |  |  |  | 32 |  |  | Spare | Spare |  |  | Spare
I/O numbeE | [10 empty] | I/O numbeE
|  | FCS0304 Node 5 | [10 empty] | FCS0304 Node 10
| Channel | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8 |  |  | Channel | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8
|  | AAI143-H | AAI143-H | AAI543-H | AAI543-H | ADCV01 | ADCV01 | ADV151-P | ADV151-P |  |  |  | AAI143-H | AAI143-H | ADV151-P | ADV151-P | ADCV01 | ADCV01 | ADV551-P | ADV551-P
|  | 16 |  | 16 |  |  |  | 32 |  |  |  |  | 16 | 16 | 32 | 32 |  |  | 32 | 32
|  | IS | R | IS | R |  |  | RE | R |  |  |  | NIS | NIS | RE | RE |  |  | 24V | Dry
Node 5 | 1 | 18-TT-21102 |  | 18-PY-35201 |  |  |  | 18-LS-61207 |  |  | Node 10 | 1 | 18-FT-61205 | 18-SI-17201 | 18-YL-21103R | 18-YL-92101L |  |  | 18-UL-17110B | 18-HS-62101S
| 2 | 18-TT-21104 |  | 18-PY-35205 |  |  |  | 18-PS-17211 |  |  |  | 2 | 18-FT-61206 | 18-SI-17202 | 18-YL-21103F | 18-YL-92101R |  |  | 18-XL-17121 | 18-HS-62102S
| 3 | 18-PT-21103 |  | 18-FI-35201 |  |  |  | 18-PS-17212 |  |  |  | 3 | 18-FT-17101 | 18-SI-17203 | 18-YL-21104R | 18-YL-92101F |  |  | 18-XS-35104 | 18-HS-21102S
| 4 | 18-PT-21105 |  | 18-PV-66101 |  |  |  | 18-PS-17213 |  |  |  | 4 | 18-FT-17105 | 18-SI-17204 | 18-YL-21104F | 18-YL-92102L |  |  | 18-XS-35101 | 18-HS-23101S
| 5 | 18-PT-21108 |  | 18-LI-23101 |  |  |  | 18-PS-17214 |  |  |  | 5 | 18-FT-17114 | 18-SI-17301 | 18-YL-21102L | 18-YL-92102R |  |  | 18-XS-35102 | 18-HS-23102S
| 6 | 18-PT-21110 |  | 18-LI-24101 |  |  |  | 18-PS-17303 |  |  |  | 6 | 18-FT-92102 | 18-SI-23101 | 18-YL-21102R | 18-YL-92102F |  |  | 18-XS-35107 | 18-HS-23105S
| 7 | 18-LT-66202 |  | Spare |  |  |  | 18-PS-21104 |  |  |  | 7 | 18-WI-35101 | 18-SI-23102 | 18-YL-21102F | 18-YL-35103RN |  |  | 18-XS-35201 | 18-HS-24101S
| 8 | 18-FT-21102 |  | Spare |  |  |  | 18-PS-21102 |  |  |  | 8 | 18-II-62101 | 18-SI-23105 | 18-YL-23101L | 18-LHS-35103REM |  |  | 18-XS-35202 | 18-HS-36106S
| 9 | 18-FT-21109 |  | Spare |  |  |  | Spare |  |  |  | 9 | 18-II-62102 | 18-SI-24101 | 18-YL-23101R | 18-PASL-35203 |  |  | 18-XS-35203 | 18-HS-66101S
| 10 | 18-LT-21101 |  | Spare |  |  |  | Spare |  |  |  | 10 | 18-II-23105 | 18-SI-35101 | 18-YL-23101F | 18-TASH-35202 |  |  | 18-XS-35204 | 18-HS-92101S
| 11 | 18-LT-92101 |  | Spare |  |  |  | Spare |  |  |  | 11 | 18-II-35201 | Spare | 18-YL-23102F | 18-PASH-35202 |  |  | 18-XS-35206 | 18-HS-92102S
| 12 | 18-PIA-35108 |  | Spare |  |  |  | Spare |  |  |  | 12 | 18-II-35202 | Spare | 18-YL-23102L | 18-PASL-35213 |  |  | Spare | 18-HS-35201S
| 13 | Spare |  | Spare |  |  |  | Spare |  |  |  | 13 | 18-II-35101 | Spare | 18-YL-23102R | 18-TASH-35212 |  |  | Spare | 18-HS-35201L
| 14 | Spare |  | Spare |  |  |  | Spare |  |  |  | 14 | Spare | Spare | 18-YL-23105L | 18-PASH-35212 |  |  | Spare | 18-HS-35202S
| 15 | Spare |  | Spare |  |  |  | Spare |  |  |  | 15 | Spare | Spare | 18-YL-23105R | 18-YL-35201L |  |  | Spare | 18-HS-35202L
| 16 | Spare |  | Spare |  |  |  | Spare |  |  |  | 16 | Spare | Spare | 18-YL-23105F | 18-YL-35201R |  |  | Spare | 18-HS-35102S
| 17 | [6 empty] | Spare |  |  |  | 17 |  |  | 18-YL-24101L | 18-YL-35201F |  |  | 18-HS-35103 | 18-HSF-35101S
| 18 | [6 empty] | Spare |  |  |  | 18 |  |  | 18-YL-24101R | 18-YL-35202L |  |  | Spare | 18-HSR-35101S
| 19 | [6 empty] | Spare |  |  |  | 19 |  |  | 18-YL-24101F | 18-YL-35202R |  |  | Spare | Spare
| 20 | [6 empty] | Spare |  |  |  | 20 |  |  | 18-YL-36106L | 18-YL-35202F |  |  | Spare | Spare
| 21 | [6 empty] | Spare |  |  |  | 21 |  |  | 18-YL-36106R | 18-YL-35102R |  |  | Spare | Spare
| 22 | [6 empty] | Spare |  |  |  | 22 |  |  | 18-YL-36106F | 18-YL-35102F |  |  | Spare | Spare
| 23 | [6 empty] | Spare |  |  |  | 23 |  |  | 18-YL-66101L | 18-YL-35102L |  |  | Spare | Spare
| 24 | [6 empty] | Spare |  |  |  | 24 |  |  | 18-YL-66101R | 18-YLF-35101R |  |  | Spare | Spare
| 25 | [6 empty] | Spare |  |  |  | 25 |  |  | 18-YL-66101F | 18-YLR-35101R |  |  | Spare | Spare
| 26 | [6 empty] | Spare |  |  |  | 26 |  |  | Spare | 18-YL-35101F |  |  | Spare | Spare
| 27 | [6 empty] | Spare |  |  |  | 27 |  |  | Spare | 18-YL-35101L |  |  | Spare | Spare
| 28 | [6 empty] | Spare |  |  |  | 28 |  |  | Spare | 18-YL-35111R |  |  | Spare | Spare
| 29 | [6 empty] | Spare |  |  |  | 29 |  |  | Spare | Spare |  |  | Spare | Spare
| 30 | [6 empty] | Spare |  |  |  | 30 |  |  | Spare | Spare |  |  | Spare | Spare
| 31 | [6 empty] | Spare |  |  |  | 31 |  |  | Spare | Spare |  |  | Spare | Spare
| 32 | [6 empty] | Spare |  |  |  | 32 |  |  | Spare | Spare |  |  | Spare | Spare
I/O numbeE | [10 empty] | I/O numbeE
[10 empty] | 227 | [10 empty] | 308

## 变更记录
2019-09-12 | 初版

## 电缆表
分支电缆 BRANCH CABLE |  |  |  |  | 桥架TRAY |  | 主电缆 MAIN CABLE | [5 empty] | 保护管 CONDU. |  | 备注
编号 | 起点 | 终点 | 类型 | 长度 | 规格 | 长度 | 编号 | 起点 | 终点 | 类型 | 长度 | 工作芯数 | 规格 | 长度
|  |  |  | LENG |  | LENG |  |  |  |  | LENG | CORES |  | LENG
NO | FROM | TO | TYPE | (m) | SPEC. | (m) | NO | FROM | TO | TYPE | (m) | USED | SPEC. | (m) | REMARKS | 电缆到界区外1m | 界区外1m到机柜室 | 问题
| 18-TT-62302 | 18-IJB-40-001 | iKA | - | - | - | 18-40-001-iSC |  | PP装置机柜间（DCS） | MiA12 | 136 | 9 | 400x200 | 9 | -
| 18-PT-61281A | 18-IJB-40-001 | iKA | - | - | - | 18-40-001-iSC
| 18-PT-61281B | 18-IJB-40-001 | iKA | - | - | - | 18-40-001-iSC
| 18-PT-61283 | 18-IJB-40-001 | iKA | - | - | - | 18-40-001-iSC
| 18-PT-62181A | 18-IJB-40-001 | iKA | - | - | - | 18-40-001-iSC
| 18-PT-62181B | 18-IJB-40-001 | iKA | - | - | - | 18-40-001-iSC
| 18-PT-62302 | 18-IJB-40-001 | iKA | - | - | - | 18-40-001-iSC
| 18-PT-62303 | 18-IJB-40-001 | iKA | - | - | - | 18-40-001-iSC
| 18-FT-62301 | 18-IJB-40-001 | iKA | - | - | - | 18-40-001-iSC
spare | - | - | -
spare | - | - | -
spare | - | - | -
| 18-TT-61110 | 18-IJB-40-002 | iKA | - | - | - | 18-40-002-iSC |  | PP装置机柜间（DCS） | MiA8 | 136 | 6 | - | - | -
| 18-TT-62301 | 18-IJB-40-002 | iKA | - | - | - | 18-40-002-iSC
| 18-FT-62101 | 18-IJB-40-002 | iKA | - | - | - | 18-40-002-iSC
| 18-FT-62103 | 18-IJB-40-002 | iKA | - | - | - | 18-40-002-iSC
| 18-LT-62201 | 18-IJB-40-002 | iKA | - | - | - | 18-40-002-iSC
| 18-LT-62301 | 18-IJB-40-002 | iKA | - | - | - | 18-40-002-iSC
spare | - | - | -
spare | - | - | -
| 18-XZSH-62301 | 18-IJB-40-003 | iKA | - | - | - | 18-40-003-iCC |  | DCS（中控室) | MiA8 | 136 | 6 | - | - | -
| 18-XZSL-62301 |  | iKA | - | - | - | 18-40-003-iCC
| 18-XZSH-62302 |  | iKA | - | - | - | 18-40-003-iCC
| 18-XZSL-62302 |  | iKA | - | - | - | 18-40-003-iCC
| 18-XZSH-62303 |  | iKA | - | - | - | 18-40-003-iCC
| 18-XZSL-62303 |  | iKA | - | - | - | 18-40-003-iCC
spare | - | - | -
spare | - | - | -
| 18-FZSL-61103 | 18-IJB-40-004 | iKA | - | - | - | 18-40-004-iCC |  | PP装置机柜间（DCS） | MiA8 | 136 | 7 | - | - | -
| 18-FZSL-62101 |  | iKA | - | - | - | 18-40-004-iCC
| 18-XZSH-62101 |  | iKA | - | - | - | 18-40-004-iCC
| 18-XZSL-62101 |  | iKA | - | - | - | 18-40-004-iCC
| 18-XZSH-61105 |  | iKA | - | - | - | 18-40-004-iCC
| 18-XZSL-61105 |  | iKA | - | - | - | 18-40-004-iCC
spare | - | - | -
spare | - | - | -
| 18-XN-61105 | 18-EJB-40-001 | KA | - | - | - | 18-40-001-CC |  | DCS（中控室) | MA8 | 133 | 7 | 200x100 | 6 | -
| 18-XN-61201 | 18-EJB-40-001 | KA | - | - | - | 18-40-001-CC
| 18-XN-61206 | 18-EJB-40-001 | KA | - | - | - | 18-40-001-CC
| 18-XN-62106 | 18-EJB-40-001 | KA | - | - | - | 18-40-001-CC
| 18-XN-62301 | 18-EJB-40-001 | KA | - | - | - | 18-40-001-CC
| 18-XN-62302 | 18-EJB-40-001 | KA | - | - | - | 18-40-001-CC
| 18-PN-62104 | 18-EJB-40-001 | KA | - | - | - | 18-40-001-CC
spare | - | - | -
| 18-TT-61102 | 18-IJB-40-005 | iKA | - | - | - | 18-40-005-iSC |  | PP装置机柜间（DCS） | MiA8 | 139 | 7 | 400x200 | 6 | -
| 18-TT-61109 |  | iKA | - | - | - | 18-40-005-iSC
| 18-PT-61108 |  | iKA | - | - | - | 18-40-005-iSC
| 18-FT-61103 |  | iKA | - | - | - | 18-40-005-iSC
| 18-FT-61104 |  | iKA | - | - | - | 18-40-005-iSC
| 18-LT-61103 |  | iKA | - | - | - | 18-40-005-iSC
18-TT-62205-iSC | 18-TT-62205 |  | iKA | - | - | - | 18-40-005-iSC
spare | - | - | -
| 18-TT-61203 | 18-IJB-40-006 | iKA | - | - | - | 18-40-006-iSC |  | PP装置机柜间（DCS） | MiA12 | 139 | 10 | - | - | -
| 18-TT-62107 |  | iKA | - | - | - | 18-40-006-iSC
| 18-TT-62108 |  | iKA | - | - | - | 18-40-006-iSC
| 18-TT-62203 |  | iKA | - | - | - | 18-40-006-iSC
| 18-PT-62202 |  | iKA | - | - | - | 18-40-006-iSC
| 18-PDT-62108 |  | iKA | - | - | - | 18-40-006-iSC
| 18-FT-62201 |  | iKA | - | - | - | 18-40-006-iSC
| 18-LT-61203 |  | iKA | - | - | - | 18-40-006-iSC
| 18-LT-62105 |  | iKA | - | - | - | 18-40-006-iSC
| 18-LT-63103 |  | iKA | - | - | - | 18-40-006-iSC
spare | - | - | -
spare | - | - | -
| 18-TT-61205 | 18-IJB-40-007 | iKA | - | - | - | 18-40-007-iSC |  | PP装置机柜间（DCS） | MiA8 | 139 | 6 | - | - | -
| 18-TT-61206 |  | iKA | - | - | - | 18-40-007-iSC
| 18-TT-61207 |  | iKA | - | - | - | 18-40-007-iSC
| 18-FT-61201 |  | iKA | - | - | - | 18-40-007-iSC
| 18-LT-61101 |  | iKA | - | - | - | 18-40-007-iSC
| 18-LT-61205 |  | iKA | - | - | - | 18-40-007-iSC
spare | - | - | -
spare | - | - | -
| 18-PV-62301 | 18-IJB-40-008 | iKA | - | - | - | 18-40-008-iSC |  | PP装置机柜间（DCS） | MiA12 | 139 | 8 | - | - | -
| 18-FXV-61103 |  | iKA | - | - | - | 18-40-008-iSC
| 18-FXV-61104 |  | iKA | - | - | - | 18-40-008-iSC
| 18-FXV-62101 |  | iKA | - | - | - | 18-40-008-iSC
| 18-FV-62103 |  | iKA | - | - | - | 18-40-008-iSC
| 18-FV-62104 |  | iKA | - | - | - | 18-40-008-iSC
| 18-FV-62105 |  | iKA | - | - | - | 18-40-008-iSC
| 18-FV-62301 |  | iKA | - | - | - | 18-40-008-iSC
spare | - | - | -
spare | - | - | -
spare | - | - | -
spare | - | - | -
| 18-FZSL-61104 | 18-IJB-40-009 | iKA | - | - | - | 18-40-009-iCC |  | PP装置机柜间（DCS） | MiA12 | 139 | 9 | - | - | -
| 18-FZSL-62104 |  | iKA | - | - | - | 18-40-009-iCC
| 18-FZSL-62105 |  | iKA | - | - | - | 18-40-009-iCC
| 18-XZSH-61104 |  | iKA | - | - | - | 18-40-009-iCC
| 18-XZSL-61104 |  | iKA | - | - | - | 18-40-009-iCC
| 18-XZSH-62105 |  | iKA | - | - | - | 18-40-009-iCC
| 18-XZSL-62105 |  | iKA | - | - | - | 18-40-009-iCC
| 18-XZSH-62106 |  | iKA | - | - | - | 18-40-009-iCC
| 18-XZSL-62106 |  | iKA | - | - | - | 18-40-009-iCC
spare | - | - | -
spare | - | - | -
spare | - | - | -
| 18-FT-61205 | 18-EJB-40-002 | KA | - | - | - | 18-40-002-EC |  | PP装置机柜间（PDP） | MA8 | 139 | 5 | 300x200 | 5 | -
| 18-FT-61206 | 18-EJB-40-002 | KA | - | - | - | 18-40-002-EC
| 18-FT-62104 | 18-EJB-40-002 | KA | - | - | - | 18-40-002-EC
| 18-FT-62105 | 18-EJB-40-002 | KA | - | - | - | 18-40-002-EC
| 18-LS-61207 | 18-EJB-40-002 | KA |  |  |  | 18-40-002-EC
spare | - | - | -
spare | - | - | -
spare | - | - | -
| 18-FT-61205 | 18-EJB-40-003 | KA | - | - | - | 18-40-003-SC |  | PP装置机柜间（DCS） | MA8 | 139 | 4 | - | - | -
| 18-FT-61206 | 18-EJB-40-003 | KA | - | - | - | 18-40-003-SC
| 18-FT-62104 | 18-EJB-40-003 | KA | - | - | - | 18-40-003-SC
| 18-FT-62105 | 18-EJB-40-003 | KA | - | - | - | 18-40-003-SC
spare | - | - | -
spare | - | - | -
spare | - | - | -
spare | - | - | -
| 18-TT-62202 | 18-IJB-40-010 | iKA | - | - | - | 18-40-010-iSC |  | PP装置机柜间（DCS） | MiA8 | 146 | 6 | 400x200 | 7 | -
| 18-TT-63101 |  | iKA | - | - | - | 18-40-010-iSC
| 18-PT-61210 |  | iKA | - | - | - | 18-40-010-iSC
| 18-PT-62103 |  | iKA | - | - | - | 18-40-010-iSC
| 18-LT-61201 |  | iKA | - | - | - | 18-40-010-iSC
| 18-LT-62101 |  | iKA | - | - | - | 18-40-010-iSC
spare | - | - | -
spare | - | - | -
| 18-TT-61107 | 18-IJB-40-011 | iKA | - | - | - | 18-40-011-iSC |  | PP装置机柜间（DCS） | MiA12 | 146 | 9 | - | - | -
| 18-TT-61108 |  | iKA | - | - | - | 18-40-011-iSC
| 18-TT-61208 |  | iKA | - | - | - | 18-40-011-iSC
| 18-PT-61109 |  | iKA | - | - | - | 18-40-011-iSC
| 18-PT-61202 |  | iKA | - | - | - | 18-40-011-iSC
| 18-PT-61204 |  | iKA | - | - | - | 18-40-011-iSC
| 18-PT-62104 |  | iKA | - | - | - | 18-40-011-iSC
| 18-FT-61101 |  | iKA | - | - | - | 18-40-011-iSC
| 18-FT-61202 |  | iKA | - | - | - | 18-40-011-iSC
spare | - | - | -
spare | - | - | -
spare | - | - | -
| 18-PV-61103B | 18-IJB-40-012 | iKA | - | - | - | 18-40-012-iSC |  | PP装置机柜间（DCS） | MiA12 | 146 | 10 | - | - | -
| 18-PV-61109 |  | iKA | - | - | - | 18-40-012-iSC
| 18-PV-61202 |  | iKA | - | - | - | 18-40-012-iSC
| 18-PV-61204 |  | iKA | - | - | - | 18-40-012-iSC
| 18-PV-61210 |  | iKA | - | - | - | 18-40-012-iSC
| 18-PV-62104 |  | iKA | - | - | - | 18-40-012-iSC
| 18-PV-63104A |  | iKA | - | - | - | 18-40-012-iSC
| 18-FV-61201 |  | iKA | - | - | - | 18-40-012-iSC
| 18-FV-61202 |  | iKA | - | - | - | 18-40-012-iSC
| 18-LV-61201 |  | iKA | - | - | - | 18-40-012-iSC
spare | - | - | -
spare | - | - | -
| 18-PZSL-61103A | 18-IJB-40-013 | iKA | - | - | - | 18-40-013-iCC |  | PP装置机柜间（DCS） | MiA12 | 146 | 10 | - | - | -
| 18-PZSL-61202 |  | iKA | - | - | - | 18-40-013-iCC
| 18-PZSL-61204 |  | iKA | - | - | - | 18-40-013-iCC
| 18-PZSL-61210 |  | iKA | - | - | - | 18-40-013-iCC
| 18-PZSL-62104 |  | iKA | - | - | - | 18-40-013-iCC
| 18-FZSL-61201 |  | iKA | - | - | - | 18-40-013-iCC
| 18-FZSL-61202 |  | iKA | - | - | - | 18-40-013-iCC
| 18-LZSL-61201 |  | iKA | - | - | - | 18-40-013-iCC
| 18-LZSL-61202 | 18-IJB-40-013 | iKA | - | - | - | 18-40-013-iCC
| 18-LZSL-61203 | 18-IJB-40-013 | iKA | - | - | - | 18-40-013-iCC
spare | - | - | -
spare | - | - | -
| 18-XZSH-61102 | 18-IJB-40-014 | iKA | - | - | - | 18-40-014-iCC |  | PP装置机柜间（DCS） | MiA12 | 146 | 10 | - | - | -
| 18-XZSL-61102 |  | iKA | - | - | - | 18-40-014-iCC
| 18-XZSH-61103 |  | iKA | - | - | - | 18-40-014-iCC
| 18-XZSL-61103 |  | iKA | - | - | - | 18-40-014-iCC
| 18-XZSH-61106 |  | iKA | - | - | - | 18-40-014-iCC
| 18-XZSL-61106 |  | iKA | - | - | - | 18-40-014-iCC
| 18-XZSH-61201 |  | iKA | - | - | - | 18-40-014-iCC
| 18-XZSL-61201 |  | iKA | - | - | - | 18-40-014-iCC
| 18-XZSH-61206 |  | iKA | - | - | - | 18-40-014-iCC
| 18-XZSL-61206 |  | iKA | - | - | - | 18-40-014-iCC
spare
spare
| 18-TT-61104 | 18-IJB-40-015 | iKA | - | - | - | 18-40-015-iSC |  | PP装置机柜间（DCS） | MiA12 | 145 | 8 | 300x200 | 6 | -
| 18-TT-61105 |  | iKA | - | - | - | 18-40-015-iSC
| 18-TT-61106 |  | iKA | - | - | - | 18-40-015-iSC
| 18-TT-62101 |  | iKA | - | - | - | 18-40-015-iSC
| 18-TT-62102 |  | iKA | - | - | - | 18-40-015-iSC
| 18-TT-62103 |  | iKA | - | - | - | 18-40-015-iSC
| 18-TT-62104 |  | iKA | - | - | - | 18-40-015-iSC
| 18-PT-61103 |  | iKA | - | - | - | 18-40-015-iSC
spare | - | - | -
spare | - | - | -
spare | - | - | -
spare | - | - | -
| 18-TT-61103 | 18-IJB-40-016 | iKA | - | - | - | 18-40-016-iSC |  | PP装置机柜间（DCS） | MiA8 | 145 | 7 | - | - | -
| 18-TT-61201 |  | iKA | - | - | - | 18-40-016-iSC
| 18-TT-61209 |  | iKA | - | - | - | 18-40-016-iSC
| 18-PT-63104 |  | iKA | - | - | - | 18-40-016-iSC
| 18-PDT-61211 |  | iKA | - | - | - | 18-40-016-iSC
| 18-FT-62202 |  | iKA | - | - | - | 18-40-016-iSC
| 18-LT-61202 |  | iKA | - | - | - | 18-40-016-iSC
spare | - | - | -
| 18-TV-62202 | 18-IJB-40-017 | iKA | - | - | - | 18-40-017-iSC |  | PP装置机柜间（DCS） | MiA8 | 145 | 5 | - | - | -
| 18-PXV-61103A |  | iKA | - | - | - | 18-40-017-iSC
| 18-PV-63104B |  | iKA | - | - | - | 18-40-017-iSC
| 18-LV-61202 |  | iKA | - | - | - | 18-40-017-iSC
| 18-LV-61203 |  | iKA | - | - | - | 18-40-017-iSC
spare | - | - | -
spare | - | - | -
spare | - | - | -
| 18-GT-40101 | 18-EJB-40-004 | KB | - | - | - | 18-40-004-SC |  | PP装置机柜间（GDS） | MB12 | 120 | 8 | - | - | -
| 18-GT-40102 | 18-EJB-40-004 | KB | - | - | - | 18-40-004-SC
| 18-GT-40103 | 18-EJB-40-004 | KB | - | - | - | 18-40-004-SC
| 18-GT-40104 | 18-EJB-40-004 | KB | - | - | - | 18-40-004-SC
| 18-GT-40301 | 18-EJB-40-004 | KB | - | - | - | 18-40-004-SC
| 18-GT-40302 | 18-EJB-40-004 | KB | - | - | - | 18-40-004-SC
| 18-GT-40303 | 18-EJB-40-004 | KB | - | - | - | 18-40-004-SC
| 18-GT-40401 | 18-EJB-40-004 | KB | - | - | - | 18-40-004-SC
spare | - | - | -
spare | - | - | -
spare | - | - | -
spare | - | - | -
| 18-GT-40105 | 18-EJB-40-005 | KB | - | - | - | 18-40-005-SC |  | PP装置机柜间（GDS） | MB12 | 139 | 9 | - | - | -
| 18-GT-40106 |  | KB | - | - | - | 18-40-005-SC
| 18-GT-40107 |  | KB | - | - | - | 18-40-005-SC
| 18-GT-40108 |  | KB | - | - | - | 18-40-005-SC
| 18-GT-40201 |  | KB | - | - | - | 18-40-005-SC
| 18-GT-40202 |  | KB | - | - | - | 18-40-005-SC
| 18-GT-40203 |  | KB | - | - | - | 18-40-005-SC
| 18-GT-40204 |  | KB | - | - | - | 18-40-005-SC
| 18-GT-40205 |  | KB | - | - | - | 18-40-005-SC
spare | - | - | -
spare | - | - | -
spare | - | - | -
| 18-GA-40101 | 18-EJB-40-006 | KA | - | - | - | 18-40-006-CC |  | PP装置机柜间（GDS） | MA8 |  | 4 | - | - | -
| 18-GA-40102 |  | KA | - | - | - | 18-40-006-CC
| 18-GA-40103 |  | KA | - | - | - | 18-40-006-CC
| 18-GA-40104 |  | KA | - | - | - | 18-40-006-CC
spare | - | - | -
spare | - | - | -
spare | - | - | -
spare | - | - | -
sis单拉
18-PXT-62204-iSC | 18-PXT-62204 | PP装置机柜间（SIS） | iKA | - | - | -
18-TXT-62204-iSC | 18-TXT-62204 | PP装置机柜间（SIS） | iKA | - | - | -
18-FXN-62101-CC | 18-FXN-62101 | PP装置机柜间（SIS） | KA | - | - | -
18-FXN-61103-CC | 18-FXN-61103 | PP装置机柜间（SIS） | KA | - | - | -
18-XXN-62101-CC | 18-XXN-62101 | PP装置机柜间（SIS） | KA | - | - | -
18-PXT-62201A-iSC | 18-PXT-62201A | PP装置机柜间（SIS） | iKA | - | - | -
18-PXT-62201B-iSC | 18-PXT-62201B | PP装置机柜间（SIS） | iKA | - | - | -
18-PXT-62201C-iSC | 18-PXT-62201C | PP装置机柜间（SIS） | iKA | - | - | -
18-FXN-61104-CC | 18-FXN-61104 | PP装置机柜间（SIS） | KA | - | - | -
18-XXN-61104-CC | 18-XXN-61104 | PP装置机柜间（SIS） | KA | - | - | -
18-XXN-62105-CC | 18-XXN-62105 | PP装置机柜间（SIS） | KA | - | - | -
18-XXN-61106-CC | 18-XXN-61106 | PP装置机柜间（SIS） | KA | - | - | -
18-XXN-61103-CC | 18-XXN-61103 | PP装置机柜间（SIS） | KA | - | - | -
18-XXN-61102-CC | 18-XXN-61102 | PP装置机柜间（SIS） | KA | - | - | -
| 18-XXN-62303 | PP装置机柜间（SIS） | KA | - | - | -
18-PXT-61106A-iSC | 18-PXT-61106A | PP装置机柜间（SIS） | iKA | - | - | -
18-PXT-61106B-iSC | 18-PXT-61106B | PP装置机柜间（SIS） | iKA | - | - | -
18-PXT-61106C-iSC | 18-PXT-61106C | PP装置机柜间（SIS） | iKA | - | - | -
18-PXN-61103A-CC | 18-PXN-61103A | PP装置机柜间（SIS） | KA | - | - | -
分支电缆 BRANCH CABLE 起点: 18-PDT-61104; 分支电缆 BRANCH CABLE 终点: PP装置机柜间（DCS）; 分支电缆 BRANCH CABLE 类型: iKA; 分支电缆 BRANCH CABLE 长度: -; 桥架TRAY 规格: -; 桥架TRAY 长度: - | 防雷仪表
分支电缆 BRANCH CABLE 起点: 18-PDT-62101; 分支电缆 BRANCH CABLE 终点: PP装置机柜间（DCS）; 分支电缆 BRANCH CABLE 类型: iKA; 分支电缆 BRANCH CABLE 长度: -; 桥架TRAY 规格: -; 桥架TRAY 长度: - | 防雷仪表
| 18-LS-61207 | PP装置机柜间（DCS） | KA | - | - | -
18-HS-61101B-CC | 18-HS-61101B | PP装置机柜间（DCS） | KA | - | - | -

## 数量统计
工段 | 点数
1812 | 106
1830 | 258
1840 | 171
类型 |  | 卡数 | 每卡平均
AIR-IS | 72 | 6
AIR-NIS | 9 | 1
AI-IS | 68 | 6
AI-NIS | 23 | 2
AOR-IS | 52 | 5
AOR-NIS | 10 | 2
DIR-MI | 1 | 1
DI-MI | 101 | 4
DIR-RE | 8 | 1
DI-RE | 100 | 4
DIR-IS | 3 | 1
DI-IS | 2 | 1
DOR-24V |  | 1
DO-24V | 12 | 1
DOR-Dry | 30 | 3
DO-Dry | 18 | 1

## 仪表索引
|  |  | 仪表索引表 INSTRUMENT INDEX |  |  |  | 文件编号 DOC NO |  |  | 版次REV
[7 empty] | 页数 SHEET NO |  |  | C01
用户 Client: 天津渤化化工发展有限公司
回路号 | 仪表位号 | 仪表类型 | 用途 | 流程图号 | 位置 | 管线或设备号 | I/O 类型 | 供货方 | 备注
LOOP NO | TAG NO | INSTRUMENT TYPE | SERVICE | P&ID NO | LOCATION | LINE OR EQIUQUIP NO | I/O TYPE | SUPPLIER | REMARKS
- | 18-TI-61102 | DCS | GC TO TA-6101 TEMP. INDIC. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-TT-61102 | Integral Temperature Transmitter | GC TO TA-6101 TEMP. INDIC. | 1840-PS07-611 | On-line | 18-100-GC-61105-B2A-N | DCS-AI | - | - | C01
- | 18-TI-61103 | DCS | GC FROM TA-6101 TOP TEMP. INDIC. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-TT-61103 | Integral Temperature Transmitter | GC FROM TA-6101 TOP TEMP. INDIC. | 1840-PS07-611 | On-line | 18-150-GC-61107-B2A-N | DCS-AI | - | - | C01
- | 18-TI-61104 | DCS | TA-6101 TEMP. INDIC. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-TT-61104 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | Equip. | 18-TA-6101/T1 | DCS-AI | - | - | C01
- | 18-TIC-61105 | DCS | TA-6101 TEMP. INDIC., CONTR. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-TT-61105 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC., CONTR. | 1840-PS07-611 | Equip. | 18-TA-6101/T2 | DCS-AI | - | - | C01
- | 18-TI-61106 | DCS | TA-6101 TEMP. INDIC. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-TT-61106 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | Equip. | 18-TA-6101/T3 | DCS-AI | - | - | C01
- | 18-TI-61107 | DCS | TA-6101 TEMP. INDIC. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-TT-61107 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | Equip. | 18-TA-6101/T4 | DCS-AI | - | - | C01
- | 18-TI-61108 | DCS | TA-6101 TEMP. INDIC. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-TT-61108 | Integral Temperature Transmitter | TA-6101 TEMP. INDIC. | 1840-PS07-611 | Equip. | 18-TA-6101/T5 | DCS-AI | - | - | C01
- | 18-TI-61109 | DCS | GC FROM ET-6101 TEMP. INDIC. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-TT-61109 | Integral Temperature Transmitter | GC FROM ET-6101 TEMP. INDIC. | 1840-PS07-611 | On-line | 18-300-GC-61109-B2A-H | DCS-AI | - | - | C01
- | 18-TI-61110 | DCS | HCS FROM TA-6101 BOTTOM TEMP. INDIC. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-TT-61110 | Integral Temperature Transmitter | HCS FROM TA-6101 BOTTOM TEMP. INDIC. | 1840-PS07-611 | On-line | 18-80-PR-61101-B2A-N | DCS-AI | - | - | C01
- | 18-TI-61201 | DCS | ETH TO ET-6103 TEMP. INDIC. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-TT-61201 | Integral Temperature Transmitter | ETH TO ET-6103 TEMP. INDIC. | 1840-PS07-612 | On-line | 18-50-ETH-61204-B2A-C | DCS-AI | - | - | C01
- | 18-TI-61203 | DCS | ETH TO VE-6103 TEMP. INDIC. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-TT-61203 | Integral Temperature Transmitter | ETH TO VE-6103 TEMP. INDIC. | 1840-PS07-612 | On-line | 18-100-ETH-61201-B2A-C | DCS-AI | - | - | C01
- | 18-TI-61205 | DCS | TA-6102 TEMP. INDIC. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-TT-61205 | Integral Temperature Transmitter | TA-6102 TEMP. INDIC. | 1840-PS07-612 | Equip. | 18-TA-6102/T1 | DCS-AI | - | - | C01
- | 18-TI-61206 | DCS | TA-6102 TEMP. INDIC. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-TT-61206 | Integral Temperature Transmitter | TA-6102 TEMP. INDIC. | 1840-PS07-612 | Equip. | 18-TA-6102/T2 | DCS-AI | - | - | C01
- | 18-TICA-61207 | DCS | TA-6102 TEMP. INDIC., CONTR., ALARM | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-TT-61207 | Integral Temperature Transmitter | TA-6102 TEMP. INDIC., CONTR., ALARM | 1840-PS07-612 | Equip. | 18-TA-6102/T3 | DCS-AI | - | - | C01
- | 18-TIA-61208 | DCS | GC TO OSBL TEMP. INDIC., ALARM | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-TT-61208 | Integral Temperature Transmitter | GC TO OSBL TEMP. INDIC., ALARM | 1840-PS07-612 | On-line | 18-50-GC-61219-D21A-D | DCS-AI | - | - | C01
- | 18-TIA-61209 | DCS | ETH FROM ET-6103 TEMP. NDIC., ALARM | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-TT-61209 | Integral Temperature Transmitter | ETH FROM ET-6103 TEMP. NDIC., ALARM | 1840-PS07-612 | On-line | 18-80-ETH-61209-B2A-E | DCS-AI | - | - | C01
- | 18-TI-62101 | DCS | TA-6201 TEMP. INDIC. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-TT-62101 | Integral Temperature Transmitter | TA-6201 TEMP. INDIC. | 1840-PS07-621 | Equip. | 18-TA-6201/T1 | DCS-AI | - | - | C01
- | 18-TI-62102 | DCS | TA-6201 TEMP. INDIC. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-TT-62102 | Integral Temperature Transmitter | TA-6201 TEMP. INDIC. | 1840-PS07-621 | Equip. | 18-TA-6201/T2 | DCS-AI | - | - | C01
- | 18-TI-62103 | DCS | TA-6201 TEMP. INDIC. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-TT-62103 | Integral Temperature Transmitter | TA-6201 TEMP. INDIC. | 1840-PS07-621 | Equip. | 18-TA-6201/T3 | DCS-AI | - | - | C01
- | 18-TI-62104 | DCS | TA-6201 TEMP. INDIC. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-TT-62104 | Integral Temperature Transmitter | TA-6201 TEMP. INDIC. | 1840-PS07-621 | Equip. | 18-TA-6201/T4 | DCS-AI | - | - | C01
- | 18-TI-62107 | DCS | PR TO VE-6202 TEMP. INDIC. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-TT-62107 | Integral Temperature Transmitter | PR TO VE-6202 TEMP. INDIC. | 1840-PS07-621 | On-line | 18-250-PR-62106-B2A-N | DCS-AI | - | - | C01
- | 18-TI-62108 | DCS | P TO VE-6203 TEMP. INDIC. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-TT-62108 | Integral Temperature Transmitter | P TO VE-6203 TEMP. INDIC. | 1840-PS07-621 | On-line | 18-40-P-62101-A2A-N | DCS-AI | - | - | C01
- | 18-TIC-62202 | DCS | PR TO ET-6201 TEMP. INDIC., CONTR. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-TT-62202 | Integral Temperature Transmitter | PR TO ET-6201 TEMP. INDIC., CONTR. | 1840-PS07-622 | On-line | 18-350-PR-62205-B2A-H | DCS-AI | - | - | C01
- | 18-TV-62202 | Globe | CWR FROM ET-61202 FOR PR TEMP. CONTR. | 1840-PS07-622 | In-line | 18-200-CWR-62201-B1K-N | DCS-AO | - | - | C01
- | 18-TI-62203 | DCS | PR TO VE-6201 TEMP. INDIC. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-TT-62203 | Integral Temperature Transmitter | PR TO VE-6201 TEMP. INDIC. | 1840-PS07-622 | On-line | 18-400-PR-62102-A2A-H | DCS-AI | - | - | C01
- | 18-TIA-62204 | DCS | PR TO ET-6202 TEMP. INDIC., ALARM | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-TXSHH-62204 | SIS | PR TO ET-6202 TEMP | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-TXT-62204 | Integral Temperature Transmitter | PR TO ET-6202 TEMP. INDIC., ALARM | 1840-PS07-622 | On-line | 18-350-PR-62204-B2A-E | SIS-AI | - | - | C01
- | 18-TISA-62205 | DCS | PR TO PC-6201 TEMP. INDIC., ALA | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-TT-62205 | Integral Temperature Transmitter | PR TO PC-6201 TEMP. INDIC., ALA., INTERL. | 1840-PS07-622 | On-line | 18-400-PR-62203-A2A-E | DCS-AI | - | - | C01
- | 18-TI-62301 | DCS | VE-6203 TEMP. INDIC. | 1840-PS07-623 | CCR | - | - | - | - | C01
- | 18-TT-62301 | Integral Temperature Transmitter | VE-6203 TEMP. INDIC. | 1840-PS07-623 | Equip. | 18-VE-6203/T | DCS-AI | - | - | C01
- | 18-TI-62302 | DCS | P FROM VE-6203 TEMP. INDIC. | 1840-PS07-623 | CCR | - | - | - | - | C01
- | 18-TT-62302 | Integral Temperature Transmitter | P FROM VE-6203 TEMP. INDIC. | 1840-PS07-623 | On-line | 18-50-P-62312-A2A-E | DCS-AI | - | - | C01
- | 18-TIA-63101 | DCS | COOL. TO ET-6301 TEMP. INDIC., ALARM | 1840-PS07-631 | CCR | - | - | - | - | C01
- | 18-TT-63101 | Integral Temperature Transmitter | COOL. TO ET-6301 TEMP. INDIC., ALARM | 1840-PS07-631 | On-line | 18-300-PR-63105-B2A-P | DCS-AI | - | - | C01
- | 18-TG-62105 | Bimetal Thermometer | TA-6201 TEMP. LOCAL INDIC. | 1840-PS07-621 | Equip. | 18-TA-6201/T5 | - | - | - | C01
- | 18-TG-62106 | Bimetal Thermometer | PRTO ET-6201 TEMP. LOCAL INDIC. | 1840-PS07-621 | On-line | 18-350-PR-62205-B2A-H | - | - | - | C01
- | 18-TG-63102 | Bimetal Thermometer | VE-6304 LOCAL TEMP. INDIC. | 1840-PS07-631 | Equip. | 18-VE-6304/T4 | - | - | - | C01
- | 18-TW-61101 | Thermowell | CWR FROM ET-6106 TEMP. INDIC. | 1840-PS07-611 | On-line | 18-150-CWR-61101-B2A-N | - | - | - | C01
- | 18-TW-61202 | Thermowell | PR FROM ET-6102 TEMP. INDIC. | 1840-PS07-612 | On-line | 18-200-PR-61204-B2A-R | - | - | - | C01
- | 18-TW-61204 | Thermowell | PR FROM ET-6104 TEMP. INDIC. | 1840-PS07-612 | On-line | 18-200-PR-61205-B2A-R | - | - | - | C01
- | 18-TW-62201 | Thermowell | CWR FROM ET-6202 TEMP. INDIC. | 1840-PS07-622 | On-line | 18-200-CWR-62201-B1K-N | - | - | - | C01
- | 18-TW-63103 | Thermowell | CWR FROM ET-6301 TEMP. INDIC. | 1840-PS07-631 | On-line | 18-400-CWR-63101-B2A-N | - | - | - | C01
- | 18-PICA-61103 | DCS | GC TO TA-6101 PRES. INDIC., CONTR., ALA. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PT-61103 | Pressure Transmitter | GC TO TA-6101 PRES. INDIC., CONTR., ALA. | 1840-PS07-611 | Off-line | 18-100-GC-61104-B2A-N | DCS-AI | - | - | C01
- | 18-PXV-61103A | Globe | GC TO TA-6101 PRESSURE CONTROL | 1840-PS07-611 | In-line | 18-100-GC-61104-B2A-N | DCS-AO | - | - | C01
- | 18-PXN-61103A | Solenoid Valve | - | 1840-PS07-611 | On-off | - | SIS-DO | - | - | C01
- | 18-PZSL-61103A | Limit Switch(Close) | - | 1840-PS07-611 | On-off | - | DCS-DI | - | - | C01
- | 18-PV-61103B | Globe | CWS FOR TA-6101 PRES. CONTROL | 1840-PS07-611 | In-line | 18-150-CWS-61101-B2A-N | DCS-AO | - | - | C01
- | 18-PIA-61106A | DCS | TA-6101 TOP PRES. INDIC., ALA. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PXSHH-61106A | SIS | TA-6101 TOP PRES. INTERL. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PXT-61106A | Pressure Transmitter | TA-6101 TOP PRES. INDIC., ALA., INTERL. | 1840-PS07-611 | Off-line | 18-150-GC-61107-B2A-N | SIS-AI | - | - | C01
- | 18-PIA-61106B | DCS | TA-6101 TOP PRES. INDIC., ALA. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PXSHH-61106B | SIS | TA-6101 TOP PRES. INTERL. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PXT-61106B | Pressure Transmitter | TA-6101 TOP PRES. INDIC., ALA., INTERL. | 1840-PS07-611 | Off-line | 18-150-GC-61107-B2A-N | SIS-AI | - | - | C01
- | 18-PIA-61106C | DCS | TA-6101 TOP PRES. INDIC., ALA. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PXSHH-61106C | SIS | TA-6101 TOP PRES. INTERL. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PXT-61106C | Pressure Transmitter | TA-6101 TOP PRES. INDIC., ALA., INTERL. | 1840-PS07-611 | CCR | 18-150-GC-61107-B2A-N | SIS-AI | - | - | C01
- | 18-PISA-61108 | DCS | LLS TO ET-6101 PRES. INDI., ALA., INTER. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PT-61108 | Pressure Transmitter | LLS TO ET-6101 PRES. INDI., ALA., INTER. | 1840-PS07-611 | Off-line | 18-150-LLS-61101-B1A-H | DCS-AI | - | - | C01
- | 18-PICA-61109 | DCS | GC TO TA-6106 PRES. INDIC., CONTR., ALA. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PT-61109 | Pressure Transmitter | GC TO TA-6106 PRES. INDIC., CONTR., ALA. | 1840-PS07-611 | Off-line | 18-100-GC-61101-B1K-P | DCS-AI | - | - | C01
- | 18-PV-61109 | Globe | GC TO FLARE FOR GC TO ET-6106 PRES. CONTR. | 1840-PS07-611 | In-line | 18-150-BFHP-61101-B1K-P | DCS-AO | - | - | C01
- | 18-PIC-61202 | DCS | COOL. FROM ET-6102 PRES. INDIC., CONTR. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-PT-61202 | Pressure Transmitter | COOL. FROM ET-6102 PRES. INDIC., CONTR. | 1840-PS07-612 | CCR | 18-200-PR-61204-B2A-C | DCS-AI | - | - | C01
- | 18-PV-61202 | Globe | COOL. FROM ET-6102 FOR PRES. CONTR. | 1840-PS07-612 | In-line | 18-200-PR-61204-B2A-C | DCS-AO | - | - | C01
- | 18-PZSL-61202 | Limit Switch(Close) | - | 1840-PS07-612 | On-off | - | DCS-DI | - | - | C01
- | 18-PIC-61204 | DCS | GC ENDS TO ET-6105 PRES. INDIC., CONTR. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-PT-61204 | Pressure Transmitter | GC ENDS TO ET-6105 PRES. INDIC., CONTR. | 1840-PS07-612 | Off-line | 18-50-GC-61221-B2A-C | DCS-AI | - | - | C01
- | 18-PV-61204 | Globe | HCS TO ET-6105 FOR ET-6102 PRES. CONTR. | 1840-PS07-612 | In-line | 18-50-GC-61221-D21A-C | DCS-AO | - | - | C01
- | 18-PZSL-61204 | Limit Switch(Close) | - | 1840-PS07-612 | On-off | - | DCS-DI | - | - | C01
- | 18-PIC-61210 | DCS | COOL. FROM ET-6104 PRES. INDIC., CONTR. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-PT-61210 | Pressure Transmitter | COOL. FROM ET-6104 PRES. INDIC., CONTR. | 1840-PS07-612 | Off-line | 18-200-PR-61205-B2A-C | DCS-AI | - | - | C01
- | 18-PV-61210 | Globe | COOL. FROM ET-6104 FOR ET-6104 PRES. CONTR. | 1840-PS07-612 | In-line | 18-200-PR-61205-B2A-C | DCS-AO | - | - | C01
- | 18-PZSL-61210 | Limit Switch(Close) | - | 1840-PS07-612 | On-off | - | DCS-DI | - | - | C01
- | 18-PI-62103 | DCS | TA-6201 BOTTOM PRES. INDIC. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-PT-62103 | Pressure Transmitter | TA-6201 BOTTOM PRES. INDIC. | 1840-PS07-621 | CCR | 18-TA-6201/P4 | DCS-AI | - | - | C01
- | 18-PICA-62104 | DCS | VE-6202 TOP PRES. INDIC., CONTR., ALA. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-PT-62104 | Pressure Transmitter | VE-6202 TOP PRES. INDIC., CONTR., ALA. | 1840-PS07-621 | Off-line | 18-100-PR-62122-B2A-N | DCS-AI | - | - | C01
- | 18-PV-62104 | Globe | PRE TO FLARE FOR VE-6202 PRES. CONTR. | 1840-PS07-621 | In-line | 18-50-PR-62122-B2A-N | DCS-AO | - | - | C01
- | 18-PN-62104 | Solenoid Valve | - | 1840-PS07-621 | On-off | - | DCS-DO | - | - | C01
- | 18-PZSL-62104 | Limit Switch(Close) | - | 1840-PS07-621 | On-off | - | DCS-DI | - | - | C01
- | 18-PIA-62201A | DCS | PR TO VE-6201 PRES. INDIC., ALA. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-PXSHH-62201A | SIS | PR TO VE-6201 PRES INTER. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-PXT-62201A | Pressure Transmitter | PR TO VE-6201 PRES. INDIC., ALA. INTER. | 1840-PS07-622 | Off-line | 18-400-PR-62102-A2A-H | SIS-AI | - | - | C01
- | 18-PIA-62201B | DCS | PR TO VE-6201 PRES. INDIC., ALA. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-PXSHH-62201B | SIS | PR TO VE-6201 PRES INTER. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-PXT-62201B | Pressure Transmitter | PR TO VE-6201 PRES. INDIC., ALA., INTERL. | 1840-PS07-622 | Off-line | 18-400-PR-62102-A2A-H | SIS-AI | - | - | C01
- | 18-PIA-62201C | DCS | PR TO VE-6201 PRES. INDIC., ALA. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-PXSHH-62201C | SIS | PR TO VE-6201 PRES INTER. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-PXT-62201C | Pressure Transmitter | PR TO VE-6201 PRES. INDIC., ALA., INTERL. | 1840-PS07-622 | CCR | 18-400-PR-62102-A2A-H | SIS-AI | - | - | C01
- | 18-PICSA-62202 | DCS | PR TO VE-6201 PRES. INDIC., CONTR. ALA., INTERL. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-PT-62202 | Pressure Transmitter | PR TO VE-6201 PRES. INDIC., CONTR. ALA., INTERL. | 1840-PS07-622 | Off-line | 18-400-PR-62102-A2A-H | DCS-AI | - | - | C01
- | 18-PIA-62204 | DCS | PC-6201 OUTLET PR PRES. INDIC.ALA | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-PXSHH-62204 | SIS | PC-6201 OUTLET PR PRES. INTERL. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-PXT-62204 | Pressure Transmitter With Diaphragm Seal | PC-6201 OUTLET PR PRES. INDIC.,ALA., INTERL. | 1840-PS07-622 |  | 18-350-PR-62204-B2A-ET | SIS-AI | - | - | C01
- | 18-PICSA-62301 | DCS | VE-6203 TO PRES. INDIC., CONTR. ALA., INTERL. | 1840-PS07-623 | CCR | - | - | - | - | C01
- | 18-PT-62301 | Pressure Transmitter With Diaphragm Seal | VE-6203 TO P PRES. INDIC.,CONTR. ALA. | 1840-PS07-623 | CCR | 18-50-P-62312-A2A-ET | DCS-AI | - | - | C01
- | 18-PV-62301 | Globe | P TO OSBL PRES. CONTR. | 1840-PS07-623 | In-line | 18-50-P-62312-A2A-ET | DCS-AO | - | - | C01
- | 18-PISA-62302 | DCS | LLS TO ET-6203 PRES. INDIC., ALA., INTERL. | 1840-PS07-623 | CCR | - | - | - | - | C01
- | 18-PT-62302 | Pressure Transmitter | LLS TO ET-6203 PRES. INDIC., ALA., INTERL. | 1840-PS07-623 | Off-line | 18-25-LLS-62310-A2A-H | DCS-AI | - | - | C01
- | 18-PI-62303 | DCS | P TO POSM PRES. INDIC. | 1840-PS07-623 | CCR | - | - | - | - | C01
- | 18-PT-62303 | Pressure Transmitter | P TO POSM PRES. INDIC. | 1840-PS07-623 | In-line | 18-50-P-62314-A2A-H | DCS-AI | - | - | C01
- | 18-PICA-63104 | DCS | VE-6303 PRES. INDIC., CONTR. ALA. | 1840-PS07-631 | CCR | - | - | - | - | C01
- | 18-PT-63104 | Pressure Transmitter With Diaphragm Seal | VE-6303 PRES. INDIC., CONTR. ALA. | 1840-PS07-631 | In-line | 18-100-PR-63103-B2A-N | DCS-AI | - | - | C01
- | 18-PV-63104A | Globe | COOL. TO VE-6303 FOR PESS. CONTR. | 1840-PS07-631 | In-line | 18-50-PR-63106-B2A-P | DCS-AO | - | - | C01
- | 18-PV-63104B | Globe | COOL. TO FLARE FOR VE-6303 PESS. CONTR. | 1840-PS07-631 | In-line | 18-50-PR-63103-B2A-C | DCS-AO | - | - | C01
- | 18-PDIA-61104 | DCS | TA-6101 PRES.DIFFER. INDIC., ALARNM | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PDT-61104 | D/P Transmitter | TA-6101 PRES.DIFFER. INDIC., ALARNM | 1840-PS07-611 | Equip. | 18-50-GC-TA6101P1-D2A 18-50-GC-TA6101P2-D2A 18-50-GC-TA6101P3-D2A | DCS-AI | - | - | C01
- | 18-PDIA-61211 | DCS | TA-6102 PRES.DIFFER. INDIC., ALARM | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-PDT-61211 | D/P Transmitter | TA-6102 PRES.DIFFER. INDIC., ALARM | 1840-PS07-612 | Equip. | 18-50-GC-TA6102P1-D2A 18-50-GC-TA6102P2-D2A | DCS-AI | - | - | C01
- | 18-PDIA-62101 | DCS | TA-6201 PRES.DIFFER. INDIC., ALARM | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-PDT-62101 | D/P Transmitter | TA-6201 PRES.DIFFER. INDIC., ALARM | 1840-PS07-621 | Equip. | 18-50-PR-TA6201P1-A2A-H 18-50-PR-TA6201P2-A2A-H 18-50-PR-TA6201P3-A2A-H | DCS-AI | - | - | C01
- | 18-PDISA-62108 | DCS | PR TO ET-3101 PRES.DIFFER. INDIC., ALA., INTERL. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-PDT-62108 | D/P Transmitter With Diaphragm Seal | PR TO ET-3101 PRES.DIFFER. INDIC., ALA., INTERL. | 1840-PS07-621 | Off-line | 18-80-PR-62112-B2A-N | DCS-AI | - | - | C01
- | 18-PG-61102 | Pressure Gauge | GC TO TA-6101 LOCAL PRES. INDIC. | 1840-PS07-611 | On-line | 18-100-GC-61104-B2A-N | - | - | - | C01
- | 18-PG-61105 | Pressure Gauge | TA-6101 TOP LOCAL PRES. INDIC. | 1840-PS07-611 | On-line | 18-150-GC-61107-B2A-N | - | - | - | C01
- | 18-PG-61201 | Pressure Gauge | VE-6102 LOCAL PRES. INDIC. | 1840-PS07-612 | Equip. | 18-VE-6102 | - | - | - | C01
- | 18-PG-61203 | Pressure Gauge | VE-6103 TOP LOCAL PRES. INDIC. | 1840-PS07-612 | On-line | 18-50-ETH-61202-B2A-C | - | - | - | C01
- | 18-PG-61206 | Vibration-proof Pressure Gauge | PP-6102A OUTLET GC LOCAL PRES. INDIC. | 1840-PS07-612 | On-line | 18-100-GC-61217-B2A-C | - | - | - | C01
- | 18-PG-61207 | Vibration-proof Pressure Gauge | PP-6102B OUTLET GC LOCAL PRES. INDIC. | 1840-PS07-612 | On-line | 18-100-GC-61216-B2A-C | - | - | - | C01
- | 18-PG-61209 | Vibration-proof Pressure Gauge | PP-6103 OUTLET ETH LOCAL PRES. INDIC. | 1840-PS07-612 | On-line | 18-100-ETH-61204-B2A-C | - | - | - | C01
- | 18-PG-62102 | Pressure Gauge | TA-6201 TOP LOCAL PRES. INDIC. | 1840-PS07-621 | On-line | 18-400-PR-62102-A2A-H | - | - | - | C01
- | 18-PG-62105 | Pressure Gauge | VE-6202 TOP LOCAL PRES. INDIC. | 1840-PS07-621 | On-line | 18-100-PR-62123-B2A-N | - | - | - | C01
- | 18-PG-62106 | Vibration-proof Pressure Gauge | PP-6202A OUTLET PR LOCAL PRES. INDI. | 1840-PS07-621 | On-line | 18-80-PR-62109-B2A-N | - | - | - | C01
- | 18-PG-62107 | Vibration-proof Pressure Gauge | PP-6202B OUTLET PR LOCAL PRES. INDIC. | 1840-PS07-621 | On-line | 18-80-PR-62112-B2A-N | - | - | - | C01
- | 18-PG-62207 | Pressure Gauge With Diaphragm Seal | VE-6201 TOP LOCAL PRES. INDIC. | 1840-PS07-622 | On-line | 18-400-PR-62203-A2A-ET | - | - | - | C01
- | 18-PG-63101 | Pressure Gauge | VE-6304 TOP LOCAL PRES. INDIC. | 1840-PS07-631 | On-line | 18-25-BFHP-63105-A2A-N | - | - | - | C01
- | 18-PG-63102 | Pressure Gauge | PR START-UP TO VE-6303 LOCAL PRES. INDIC. | 1840-PS07-631 | On-line | 18-40-PR-63112-D2A-N | - | - | - | C01
- | 18-PG-63103 | Pressure Gauge | VE-6303 LOCAL PRES. INDIC. | 1840-PS07-631 | On-line | 18-100-PR-63103-B2A-N | - | - | - | C01
- | 18-PG-63105 | Vibration-proof Pressure Gauge | PR START-UP TO UP-6301 LOCAL PRES. INDIC. | 1840-PS07-631 | On-line | 18-40-PR-63120-D21S-ET | - | - | - | C01
- | 18-FIA-61101 | DCS | GC TO TA-6101 FLOW | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-FT-61101 | VORTEX FLOWMETER | GC TO TA-6101 FLOW | 1840-PS07-611 | In-line | 18-100-GC-61104-B2A-N | DCS-AI | - | - | C01
- | 18-FICA-61103 | DCS | GC TO TA-6101 FLOW | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-FT-61103 | VORTEX FLOWMETER | GC TO TA-6101 FLOW | 1840-PS07-611 | In-line | 18-100-GC-61105-B2A-N | DCS-AI | - | - | C01
- | 18-FXV-61103 | Globe | GC TO TA-6101 FLOW CONTROL | 1840-PS07-611 | In-line | 18-100-GC-61105-B2A-N | DCS-AO | - | - | C01
- | 18-FXN-61103 | Solenoid Valve | - | 1840-PS07-611 | On-off | - | SIS-DO | - | - | C01
- | 18-FZSL-61103 | Limit Switch(Close) | - | 1840-PS07-611 | On-off | - | DCS-DI | - | - | C01
- | 18-FICA-61104 | DCS | LLS TO ET-6101 FLOW | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-FT-61104 | VORTEX FLOWMETER | LLS TO ET-6101 FLOW | 1840-PS07-611 | In-line | 18-150-LLS-61101-B1A-H | DCS-AI | - | - | C01
- | 18-FXV-61104 | Globe | LLS TO ET-6101 FLOW CONTROL | 1840-PS07-611 | In-line | 18-150-LLS-61101-B1A-H | DCS-AO | - | - | C01
- | 18-FXN-61104 | Solenoid Valve | - | 1840-PS07-611 | On-off | - | SIS-DO | - | - | C01
- | 18-FZSL-61104 | Limit Switch(Close) | - | 1840-PS07-611 | On-off | - | DCS-DI | - | - | C01
- | 18-FIC-61201 | DCS | RECO. ETHY. TO TA-6102 FLOW | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-FT-61201 | VORTEX FLOWMETER | RECO. ETHY. TO TA-6102 FLOW | 1840-PS07-612 | In-line | 18-80-ETH-61205-B2A-C | DCS-AI | - | - | C01
- | 18-FV-61201 | Globe | RECOV. ETHY. TO TA-6102 FLOW CONTROL | 1840-PS07-612 | In-line | 18-80-ETH-61205-B2A-C | DCS-AO | - | - | C01
- | 18-FZSL-61201 | Limit Switch(Close) | - | 1840-PS07-612 | On-off | - | DCS-DI | - | - | C01
- | 18-FIC-61202 | DCS | HCS TO TA-6101 FLOW | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-FT-61202 | VORTEX FLOWMETER | HCS TO TA-6101 FLOW | 1840-PS07-612 | In-line | 18-100-GC-61218-B2A-C | DCS-AI | - | - | C01
- | 18-FV-61202 | Globe | HCS TO TA-6101 REFLUX FLOW CONTROL | 1840-PS07-612 | In-line | 18-100-GC-61218-B2A-C | DCS-AO | - | - | C01
- | 18-FZSL-61202 | Limit Switch(Close) | - | 1840-PS07-612 | On-off | - | DCS-DI | - | - | C01
- | 18-FIA-61205 | DCS | C3 HCS TO TA-6201 FLOW | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-FT-61205 | Coriolis Mass Flowmeter | GC TO ET-6105 FLOW INDICA., ALARM | 1840-PS07-612 | In-line | 18-50-GC-61221-D21A-C | DCS-AI | - | - | C01
- | 18-FI-61206 | DCS | C2 OFFSPEC TO OSBL FLOW | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-FT-61206 | Coriolis Mass Flowmeter | C2 OFFSPEC TO OSBL FLOW | 1840-PS07-612 | In-line | 18-80-GC-61233-B2A-ET | DCS-AI | - | - | C01
- | 18-FIC-62101 | DCS | C3 HCS TO TA-6201 FLOW | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-FT-62101 | VORTEX FLOWMETER | C3 HCS TO TA-6201 FLOW | 1840-PS07-621 | In-line | 18-80-PR-61101-B2A-N | DCS-AI | - | - | C01
- | 18-FXV-62101 | Globe | C3 TO TA-6201 FLOW CONTROL | 1840-PS07-621 | In-line | 18-80-PR-61101-B2A-N | DCS-AO | - | - | C01
- | 18-FXN-62101 | Solenoid Valve | - | 1840-PS07-621 | On-off | - | SIS-DO | - | - | C01
- | 18-FZSL-62101 | Limit Switch(Close) | - | 1840-PS07-621 | On-off | - | DCS-DI | - | - | C01
- | 18-FIC-62103 | DCS | C3 HCS TO TA-6201 REFL. FLOW | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-FT-62103 | VORTEX FLOWMETER | C3 HCS TO TA-6201 REFL. FLOW | 1840-PS07-621 | In-line | 18-250-PR-62116-B2A-N | DCS-AI | - | - | C01
- | 18-FV-62103 | Globe | C3 TO TA-6201 REFLUX FLOW CONTROL | 1840-PS07-621 | In-line | 18-250-PR-62116-B2A-N | DCS-AO | - | - | C01
- | 18-FQICA-62104 | DCS | P TO VE-6203 FLOW | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-FT-62104 | Coriolis Mass Flowmeter | P TO VE-6203 FLOW | 1840-PS07-621 | In-line | 18-40-P-62101-A2A-N | DCS-AI | - | - | C01
- | 18-FV-62104 | Globe | PROPANE FROM TA-6201 FLOW CONTROL | 1840-PS07-621 | In-line | 18-40-P-62101-A2A-N | DCS-AO | - | - | C01
- | 18-FZSL-62104 | Limit Switch(Close) | - | 1840-PS07-621 | On-off | - | DCS-DI | - | - | C01
- | 18-FICQ-62105 | DCS | PR TO ET-3101 FLOW | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-FT-62105 | Coriolis Mass Flowmeter | PR TO ET-3101 FLOW | 1840-PS07-621 | In-line | 18-80-PR-62112-B2A-N | DCS-AI | - | - | C01
- | 18-FV-62105 | Globe | PR TO OSBL TANK FLOW CONTR. | 1840-PS07-621 | In-line | 18-80-PR-62112-B2A-N | DCS-AO | - | - | C01
- | 18-FZSL-62105 | Limit Switch(Close) | - | 1840-PS07-621 | On-off | - | DCS-DI | - | - | C01
- | 18-FI-62201 | DCS | PR TO PC-6201 FLOW INDICA. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-FT-62201 | VORTEX FLOWMETER | PR TO PC-6201 FLOW INDICA. | 1840-PS07-622 | In-line | 18-400-PR-62203-A2A-ET | DCS-AI | - | - | C01
- | 18-FI-62202 | DCS | PR TO PC-6201 BYPASS FLOW | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-FT-62202 | VORTEX FLOWMETER | PR TO PC-6201 BYPASS FLOW | 1840-PS07-622 | In-line | 18-250-PR-62220-B2A-H | DCS-AI | - | - | C01
- | 18-FICA-62301 | DCS | LLS TO ET-6203 FLOW | 1840-PS07-623 | CCR | - | - | - | - | C01
- | 18-FT-62301 | VORTEX FLOWMETER | LLS TO ET-6203 FLOW | 1840-PS07-623 | In-line | 18-25-LLS-62310-A2A-H | DCS-AI | - | - | C01
- | 18-FV-62301 | Globe | LLS TO ET-6203 FLOW CONTROL | 1840-PS07-623 | In-line | 18-25-LLS-62310-A2A-H | DCS-AO | - | - | C01
- | 18-FG-63101 | Variable Area Flowmeter | PR TO VE-6303 FLOW LOCAL INDIC. | 1840-PS07-631 | In-line | 18-40-PR-63112-D2A-N | - | - | - | C01
- | 18-FG-84101 | Variable Area Flowmeter | LN TO BFHP FLARE FLOW GAUGE | 1840-PS07-841 | In-line | 18-25-LN-63012-CA2A-N | - | - | - | C01
- | 18-FG-84102 | Variable Area Flowmeter | LN TO DL FLARE FLOW ORIFI. | 1840-PS07-841 | In-line | 18-25-LN-63013-CA2A-N | - | - | - | C01
- | 18-FG-84103 | Variable Area Flowmeter | LN TO BFC FLARE FLOW ORIFI. | 1840-PS07-841 | In-line | 18-25-LN-63014-CA2A-N | - | - | - | C01
- | 18-FO-61207 | Restriction Orifice | HCS TO VE-6102 BACK FLOW ORIF. | 1840-PS07-612 | In-line | 18-50-GC-61220-B2A-C | - | - | - | C01
- | 18-FO-61208 | Restriction Orifice | ETH TO VE-6103 BACK FLOW ORIF. | 1840-PS07-612 | In-line | 18-50-ETH-61207-B2A-C | - | - | - | C01
- | 18-FO-62102 | Restriction Orifice | PR TO VE-6202 BACK FLOW ORIFI. | 1840-PS07-621 | In-line | 18-50-PR-62119-B2A-N | - | - | - | C01
- | 18-FO-84101 | Restriction Orifice | LN TO BFHP FLARE FLOW ORIFI. | 1840-PS07-841 | In-line | 18-25-LN-63012-A2A-N | - | - | - | C01
- | 18-FO-84102 | Restriction Orifice | LN TO DL FLARE FLOW ORIFI. | 1840-PS07-841 | In-line | 18-25-LN-63013-A2A-N | - | - | - | C01
- | 18-FO-84103 | Restriction Orifice | LN TO BFC FLARE FLOW ORIFI. | 1840-PS07-841 | In-line | 18-25-LN-63014-A21K-N | - | - | - | C01
- | 18-LICSA-61101 | DCS | 18-VE-6101 | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-LT-61101 | Displacer Transmitter | 18-VE-6101 | 1840-PS07-611 | Equip. | 18-VE-6101/L3,4 | DCS-AI | - | - | C01
- | 18-LICSA-61103 | DCS | TA-6101 LEVEL INDIC., CONTR., ALA., INTERL. | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-LT-61103 | Displacer Transmitter | TA-6101 LEVEL INDIC., CONTR., ALA., INTERL. | 1840-PS07-611 | Equip. | 18-TA-6101/L1,2 | DCS-AI | - | - | C01
- | 18-LICA-61201 | DCS | ET-6104 LEVEL INDIC., CONTR., ALA. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-LT-61201 | D/P Level Transmitter With Diaphgram Seal | ET-6104 LEVEL INDIC., CONTR., ALA. | 1840-PS07-612 | Equip. | 18-ET-6104 | DCS-AI | - | - | C01
- | 18-LV-61201 | Globe | COOL. TO ET-6104 LEVEL CONTROL | 1840-PS07-612 | In-line | 18-80-PR-63101-B2A-N | DCS-AO | - | - | C01
- | 18-LZSL-61201 | Limit Switch(Close) | - | 1840-PS07-612 | On-off | - | DCS-DI | - | - | C01
- | 18-LICA-61202 | DCS | ET-6102 LEVEL INDIC., CONTR., ALA. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-LT-61202 | D/P Level Transmitter With Diaphgram Seal | ET-6102 LEVEL INDIC., CONTR., ALA. | 1840-PS07-612 | Equip. | 18-ET-6102 | DCS-AI | - | - | C01
- | 18-LV-61202 | Globe | COOL. TO ET-6102 LEVEL CONTR. | 1840-PS07-612 | In-line | 18-80-PR-63102-B2A-C | DCS-AO | - | - | C01
- | 18-LZSL-61202 | Limit Switch(Close) | - | 1840-PS07-612 | On-off | - | DCS-DI | - | - | C01
- | 18-LICSA-61203 | DCS | VE-6103 LEVEL INDIC., CONTR., ALA., INTERL. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-LT-61203 | Displacer Transmitter | VE-6103 LEVEL INDIC., CONTR., ALA., INTERL. | 1840-PS07-612 | Equip. | VE-6103/L3,4 | DCS-AI | - | - | C01
- | 18-LV-61203 | Globe | C2 OFFSPEC TO OSBL FOR VE-6103 LEVEL CONTR. | 1840-PS07-612 | In-line | 18-80-GC-61233-B2A-D | DCS-AO | - | - | C01
- | 18-LZSL-61203 | Limit Switch(Close) | - | 1840-PS07-612 | On-off | - | DCS-DI | - | - | C01
- | 18-LICSA-61205 | DCS | VE-6102 LEVEL INDIC., CONT., ALA., INTERL. | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-LT-61205 | Displacer Transmitter | VE-6102 LEVEL INDIC., CONT., ALA., INTERL. | 1840-PS07-612 | Equip. | VE-6102/L3,4 | DCS-AI | - | - | C01
- | 18-LICSA-62101 | DCS | TA-6201 LEVEL INDIC., CON., ALA., INTERL. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-LT-62101 | Displacer Transmitter | TA-6201 LEVEL INDIC., CON., ALA., INTERL. | 1840-PS07-621 | Equip. | TA-6201/L1,2 | DCS-AI | - | - | C01
- | 18-LICSA-62105 | DCS | VE-6202 LEVEL INDIC., CON., ALA., INTERL. | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-LT-62105 | Displacer Transmitter | VE-6202 LEVEL INDIC., CON., ALA., INTERL. | 1840-PS07-621 | Equip. | VE-6202/L3,4 | DCS-AI | - | - | C01
- | 18-LISA-62201 | DCS | VE-6201 LEVEL INDIC., ALA., INTERL. | 1840-PS07-622 | CCR | - | - | - | - | C01
- | 18-LT-62201 | Displacer Transmitter | VE-6201 LEVEL INDIC., ALA., INTERL. | 1840-PS07-622 | Equip. | VE-6201/L1,2 | DCS-AI | - | - | C01
- | 18-LICSA-62301 | DCS | VE-6203 LEVEL INDIC., CON. ALA.INTERL. | 1840-PS07-623 | CCR | - | - | - | - | C01
- | 18-LT-62301 | D/P Level Transmitter With Diaphgram Seal | VE-6203 LEVEL INDIC., CON. ALA.INTERL. | 1840-PS07-623 | Equip. | 18-VE-6203/L1 L2 | DCS-AI | - | - | C01
- | 18-LIA-63103 | DCS | VE-6303 LEVEL INDIC., ALAR. | 1840-PS07-631 | CCR | - | - | - | - | C01
- | 18-LT-63103 | Displacer Transmitter | VE-6303 LEVEL INDIC., ALAR. | 1840-PS07-631 | Equip. | VE-6303/L3,4 | DCS-AI | - | - | C01
- | 18-LSL-61207 | DCS | PP-6103 INLET LEVEL SWITCH | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-LS-61207 | Tuning Folk | PP-6103 INLET LEVEL SWITCH | 1840-PS07-612 | Equip. | 18-100-ETH-61203-B2A-C | DCS-DI | - | - | C01
- | 18-XXV-61102 | Ball | RECOV. MONO. FROM UP-6501 | 1840-PS07-611 | In-line | 18-50-PR-61111-B2A-N | - | - | - | C01
- | 18-XXN-61102 | Solenoid Valve | - | 1840-PS07-611 | On-off Valve | - | SIS-DO | - | - | C01
- | 18-XZSH-61102 | Limit Switch(Open) | - | 1840-PS07-611 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-61102 | Limit Switch(Close) | - | 1840-PS07-611 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XXV-61103 | Ball | GEP FROM PP-3201 | 1840-PS07-611 | In-line | 18-80-GEP-61101-D2A-N | - | - | - | C01
- | 18-XXN-61103 | Solenoid Valve | - | 1840-PS07-611 | On-off Valve | - | SIS-DO | - | - | C01
- | 18-XZSH-61103 | Limit Switch(Open) | - | 1840-PS07-611 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-61103 | Limit Switch(Close) | - | 1840-PS07-611 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XXV-61104 | Ball | LLS TO ET-6101 | 1840-PS07-611 | In-line | 18-150-LLS-61101-B1A-H | - | - | - | C01
- | 18-XXN-61104 | Solenoid Valve | - | 1840-PS07-611 | On-off Valve | - | SIS-DO | - | - | C01
- | 18-XZSH-61104 | Limit Switch(Open) | - | 1840-PS07-611 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-61104 | Limit Switch(Close) | - | 1840-PS07-611 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XV-61105 | Ball | LLSC FROM ET-6101 | 1840-PS07-611 | In-line | 18-40-LLSC-61102-B1A-H | - | - | - | C01
- | 18-XN-61105 | Solenoid Valve | - | 1840-PS07-611 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-61105 | Limit Switch(Open) | - | 1840-PS07-611 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-61105 | Limit Switch(Close) | - | 1840-PS07-611 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XXV-61106 | Ball | GC TO ET-6106 ON-OFF VALVE | 1840-PS07-611 | In-line | 18-100-GC-61101-B2A-P | - | - | - | C01
- | 18-XXN-61106 | Solenoid Valve | - | 1840-PS07-611 | On-off Valve | - | SIS-DO | - | - | C01
- | 18-XZSH-61106 | Limit Switch(Open) | - | 1840-PS07-611 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-61106 | Limit Switch(Close) | - | 1840-PS07-611 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XV-61201 | Ball | RECOV. ETHY. TO VE-6103 ON-OFF VALVE | 1840-PS07-612 | In-line | 18-100-ETH-61201-B2A-C | - | - | - | C01
- | 18-XN-61201 | Solenoid Valve | - | 1840-PS07-612 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-61201 | Limit Switch(Open) | - | 1840-PS07-612 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-61201 | Limit Switch(Close) | - | 1840-PS07-612 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XV-61206 | Ball | C2 OFFSPEC TO OSBL ON-OFF VALVE | 1840-PS07-612 | In-line | 18-80-GC-61233-B2A-D | - | - | - | C01
- | 18-XN-61206 | Solenoid Valve | - | 1840-PS07-612 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-61206 | Limit Switch(Open) | - | 1840-PS07-612 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-61206 | Limit Switch(Close) | - | 1840-PS07-612 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XXV-62101 | Ball | C3 TO TA-6201 ON-OFF VALVE | 1840-PS07-621 | In-line | 18-80-PR-61101-B2A-N | - | - | - | C01
- | 18-XXN-62101 | Solenoid Valve | - | 1840-PS07-621 | On-off Valve | - | SIS-DO | - | - | C01
- | 18-XZSH-62101 | Limit Switch(Open) | - | 1840-PS07-621 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-62101 | Limit Switch(Close) | - | 1840-PS07-621 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XXV-62105 | Ball | PRTO ET-3101 ON-OFF VALVE | 1840-PS07-621 | In-line | 18-80-PR-62112-B2A-N | - | - | - | C01
- | 18-XXN-62105 | Solenoid Valve | - | 1840-PS07-621 | On-off Valve | - | SIS-DO | - | - | C01
- | 18-XZSH-62105 | Limit Switch(Open) | - | 1840-PS07-621 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-62105 | Limit Switch(Close) | - | 1840-PS07-621 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XV-62106 | Ball | RECO. PR FROM VE-6202 ON-OFF VALVE | 1840-PS07-621 | In-line | 18-100-PR-62107-B2A-N | - | - | - | C01
- | 18-XN-62106 | Solenoid Valve | - | 1840-PS07-621 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-62106 | Limit Switch(Open) | - | 1840-PS07-621 | On-off Valve | - | DCS-DI | - | 联锁 | C01
- | 18-XZSL-62106 | Limit Switch(Close) | - | 1840-PS07-621 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XV-62301 | Ball | LLS TO ET-6203 ON-OFF VALVE | 1840-PS07-623 | In-line | 18-25-LLS-62310-A2A-H | - | - | - | C01
- | 18-XN-62301 | Solenoid Valve | - | 1840-PS07-623 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-62301 | Limit Switch(Open) | - | 1840-PS07-623 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-62301 | Limit Switch(Close) | - | 1840-PS07-623 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XV-62302 | Ball | LLSC FROM ET-6203 ON-OFF VALVE | 1840-PS07-623 | In-line | 18-25-LLSC-62311-A2A-P | - | - | - | C01
- | 18-XN-62302 | Solenoid Valve | - | 1840-PS07-623 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-62302 | Limit Switch(Open) | - | 1840-PS07-623 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-62302 | Limit Switch(Close) | - | 1840-PS07-623 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XXV-62303 | Ball | P TO POSM ON-OFF VALVE | 1840-PS07-623 | In-line | 18-50-P-62314-A2A-H | - | - | - | C01
- | 18-XXN-62303 | Solenoid Valve | - | 1840-PS07-623 | On-off Valve | - | SIS-DO | - | - | C01
- | 18-XZSH-62303 | Limit Switch(Open) | - | 1840-PS07-623 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-62303 | Limit Switch(Close) | - | 1840-PS07-623 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-HS-61101A | Pushbutton | RUD | 1840-PS07-611 | CCR | Console | DCS-DI | - | - | C01
- | 18-HS-61101B | Pushbutton | RUD | 1840-PS07-611 | Field | Field | DCS-DI | - | - | C01
- | 18-HS-61102 | Pushbutton | RUD RESET | 1840-PS07-611 | CCR | Console | DCS-DI | - | - | C01
- | 18-UA-61101 | Soft Lamp | RUD | 1840-PS07-611 | CCR | - | - | - | - | C01
- | 18-PIA-61281A | DCS | 18-PP-6102A | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-PT-61281A | Pressure Transmitter | 18-PP-6102A | 1840-PS07-612 | On-line | PP-6102A | DCS-AI | RUHRPUMPEN | - | C01
- | 18-PIA-61281B | DCS | 18-PP-6102B | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-PT-61281B | Pressure Transmitter | 18-PP-6102B | 1840-PS07-612 | On-line | PP-6102B | DCS-AI | RUHRPUMPEN | - | C01
- | 18-PIA-61283 | DCS | 18-PP-6103 | 1840-PS07-612 | CCR | - | - | - | - | C01
- | 18-PT-61283 | Pressure Transmitter | 18-PP-6103 | 1840-PS07-612 | On-line | PP-6103 | DCS-AI | RUHRPUMPEN | - | C01
- | 18-PIA-62181A | DCS | 18-PP-6202A | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-PT-62181A | Pressure Transmitter | 18-PP-6202A | 1840-PS07-621 | On-line | PP-6202A | DCS-AI | RUHRPUMPEN | - | C01
- | 18-PIA-62181B | DCS | 18-PP-6202B | 1840-PS07-621 | CCR | - | - | - | - | C01
- | 18-PT-62181B | Pressure Transmitter | 18-PP-6202B | 1840-PS07-621 | On-line | PP-6202B | DCS-AI | RUHRPUMPEN | - | C01
- | 18-HS-61201P | DCS | 18-PP-6102A STOP | 1840-PS07-612 | MCC | 18-PP-6102A | DCS-DO | - | - | C01
- | 18-YL-61201R | DCS | 18-PP-6102A RUN | 1840-PS07-612 | MCC | 18-PP-6102A | DCS-DI | - | - | C01
- | 18-YL-61201F | DCS | 18-PP-6102A FAULT | 1840-PS07-612 | MCC | 18-PP-6102A | DCS-DI | - | - | C01
- | 18-HS-61202P | DCS | 18-PP-6102B STOP | 1840-PS07-612 | MCC | 18-PP-6102B | DCS-DO | - | - | C01
- | 18-YL-61202R | DCS | 18-PP-6102B RUN | 1840-PS07-612 | MCC | 18-PP-6102B | DCS-DI | - | - | C01
- | 18-YL-61202F | DCS | 18-PP-6102B FAULT | 1840-PS07-612 | MCC | 18-PP-6102B | DCS-DI | - | - | C01
- | 18-HS-61203P | DCS | 18-PP-6103 STOP | 1840-PS07-612 | MCC | 18-PP-6103 | DCS-DO | - | - | C01
- | 18-YL-61203R | DCS | 18-PP-6103 RUN | 1840-PS07-612 | MCC | 18-PP-6103 | DCS-DI | - | - | C01
- | 18-YL-61203F | DCS | 18-PP-6103 FAULT | 1840-PS07-612 | MCC | 18-PP-6103 | DCS-DI | - | - | C01
- | 18-HS-62101S | DCS | 18-PP-6202A START | 1840-PS07-621 | MCC | 18-PP-6202A | DCS-DO | - | - | C01
- | 18-HS-62101P | DCS | 18-PP-6202A STOP | 1840-PS07-621 | MCC | 18-PP-6202A | DCS-DO | - | - | C01
- | 18-YL-62101L | DCS | 18-PP-6202A REMOTE | 1840-PS07-621 | MCC | 18-PP-6202A | DCS-DI | - | - | C01
- | 18-YL-62101R | DCS | 18-PP-6202A RUN | 1840-PS07-621 | MCC | 18-PP-6202A | DCS-DI | - | - | C01
- | 18-YL-62101F | DCS | 18-PP-6202A FAULT | 1840-PS07-621 | MCC | 18-PP-6202A | DCS-DI | - | - | C01
- | 18-II-62101 | DCS | 18-PP-6202A CURRENT | 1840-PS07-621 | MCC | 18-PP-6202A | DCS-AI | - | - | C01
- | 18-HS-62102S | DCS | 18-PP-6202B START | 1840-PS07-621 | MCC | 18-PP-6202B | DCS-DO | - | - | C01
- | 18-HS-62102P | DCS | 18-PP-6202B STOP | 1840-PS07-621 | MCC | 18-PP-6202B | DCS-DO | - | - | C01
- | 18-YL-62102L | DCS | 18-PP-6202B REMOTE | 1840-PS07-621 | MCC | 18-PP-6202B | DCS-DI | - | - | C01
- | 18-YL-62102R | DCS | 18-PP-6202B RUN | 1840-PS07-621 | MCC | 18-PP-6202B | DCS-DI | - | - | C01
- | 18-YL-62102F | DCS | 18-PP-6202B FAULT | 1840-PS07-621 | MCC | 18-PP-6202B | DCS-DI | - | - | C01
- | 18-II-62102 | DCS | 18-PP-6202B CURRENT | 1840-PS07-621 | MCC | 18-PP-6202B | DCS-AI | - | - | C01
- | 18-GIA-40101 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | UP-6301 | - | - | - | C01
- | 18-GT-40101 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | UP-6301 | GDS-AI | - | - | C01
- | 18-GIA-40102 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | UP-6301 | - | - | - | C01
- | 18-GT-40102 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | UP-6301 | GDS-AI | - | - | C01
- | 18-GIA-40103 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | PC-6201 | - | - | - | C01
- | 18-GT-40103 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | PC-6201 | GDS-AI | - | - | C01
- | 18-GIA-40104 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | PC-6201 | - | - | - | C01
- | 18-GT-40104 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | PC-6201 | GDS-AI | - | - | C01
- | 18-GIA-40105 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 2-2/2-C | - | - | - | C01
- | 18-GT-40105 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 2-2/2-C | GDS-AI | - | - | C01
- | 18-GIA-40106 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 2-2/2-B | - | - | - | C01
- | 18-GT-40106 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 2-2/2-B | GDS-AI | - | - | C01
- | 18-GIA-40107 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 2-4/2-C | - | - | - | C01
- | 18-GT-40107 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 2-4/2-C | GDS-AI | - | - | C01
- | 18-GIA-40108 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 2-4/2-B | - | - | - | C01
- | 18-GT-40108 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 2-4/2-B | GDS-AI | - | - | C01
- | 18-GIA-40201 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 2-2/2-C | - | - | - | C01
- | 18-GT-40201 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 2-2/2-C | GDS-AI | - | - | C01
- | 18-GIA-40202 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 2-2/2-B | - | - | - | C01
- | 18-GT-40202 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 2-2/2-B | GDS-AI | - | - | C01
- | 18-GIA-40203 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 2-4/2-C | - | - | - | C01
- | 18-GT-40203 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 2-4/2-C | GDS-AI | - | - | C01
- | 18-GIA-40204 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | TA-6102 | - | - | - | C01
- | 18-GT-40204 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | TA-6102 | GDS-AI | - | - | C01
- | 18-GIA-40205 | GDS | H2 | - | Field | 2-2/2-C | - | - | - | C01
- | 18-GIA-40205 | Combustible Detector | H2 | - | Field | 2-2/2-C | - | - | - | C01
- | 18-GIA-40301 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 2-2/2-C | - | - | - | C01
- | 18-GT-40301 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 2-2/2-C | GDS-AI | - | - | C01
- | 18-GIA-40302 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 2-3/2-B | - | - | - | C01
- | 18-GT-40302 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 2-3/2-B | GDS-AI | - | - | C01
- | 18-GIA-40303 | GDS | H2 | - | Field | TA-6102 | - | - | - | C01
- | 18-GT-40303 | Combustible Detector | H2 | - | Field | TA-6102 | GDS-AI | - | - | C01
- | 18-GIA-40401 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 2-3/2-B | - | - | - | C01
- | 18-GT-40401 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 2-3/2-B | GDS-AI | - | - | C01
- | 18-GA-40101 | 声光报警器 | - | - | Field | - | GDS-DO | - | - | C01
- | 18-GA-40102 | 声光报警器 | - | - | Field | - | GDS-DO | - | - | C01
- | 18-GA-40103 | 声光报警器 | - | - | Field | - | GDS-DO | - | - | C01
- | 18-GA-40104 | 声光报警器 | - | - | Field | - | GDS-DO | - | - | C01
1812
- | 18-TISA-17104 | DCS | VE-1705 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-TT-17104 | Temperature Transmitter | VE-1705 | 1812-PS07-171 | Equip. | VE-1705/T | DCS-AI | - | - | C01
- | 18-PG-17101 | Pressure Gauge With Diaphragm Seal | PP-1703 DISCHARGE | 1812-PS07-171 | On-line | 18-25-WO-17102-A1K-E | - | - | - | C01
- | 18-PG-17105 | Pressure Gauge With In-Line Diaphragm Seal | LP NITROGEN TO VE-1701 / VE-1702 | 1812-PS07-171 | On-line | 18-25-LN-17101-B1B-E | - | - | - | C01
- | 18-PG-17107 | Pressure Gauge With In-Line Diaphragm Seal | LP NITROGEN TO VE-1701 | 1812-PS07-171 | On-line | 18-80-CT-17105-B1B-E | - | - | - | C01
- | 18-PG-17108 | Pressure Gauge With In-Line Diaphragm Seal | LP NITROGEN TO TEA CONTAINER | 1812-PS07-171 | On-line | 18-25-LN-17103-B1B-E | - | - | - | C01
- | 18-PG-17109 | Pressure Gauge With In-Line Diaphragm Seal | TEA TO VE-1701 | 1812-PS07-171 | On-line | 18-25-CT-17101-B1B-E | - | - | - | C01
- | 18-PG-17111 | Pressure Gauge With In-Line Diaphragm Seal | OFFGAS FROM VE-1705 | 1812-PS07-171 | On-line | 18-80-WO-17107-B1B-N | - | - | - | C01
- | 18-PG-17121 | PRESSURE GAUGE | LP NITROGEN TO WHITE OIL DRUM | 1812-PS07-171 | On-line | 18-25-LN-17107-CA2A-N | - | - | - | C01
- | 18-PG-17201 | Pressure Gauge With In-Line Diaphragm Seal | TEA FROM PP-1701A | 1812-PS07-172 | On-line | 18-25-CT-17211-D21L-E | - | - | - | C01
- | 18-PG-17203 | Pressure Gauge With In-Line Diaphragm Seal | TEA FROM PP-1702A | 1812-PS07-172 | On-line | 18-15-CT-17213-D21L-E | - | - | - | C01
- | 18-PG-17205 | Pressure Gauge With In-Line Diaphragm Seal | TEA FROM PP-1701B | 1812-PS07-172 | On-line | 18-25-CT-17212-D21L-E | - | - | - | C01
- | 18-PG-17207 | Pressure Gauge With In-Line Diaphragm Seal | TEA FROM PP-1702B | 1812-PS07-172 | On-line | 18-15-CT-17225-D21L-E | - | - | - | C01
- | 18-PG-17301 | Pressure Gauge With Diaphragm Seal | LP NITROGEN/WHITE OIL TO FLARE | 1812-PS07-173 | On-line | 18-50-WO-17305-A1K-ET | - | - | - | C01
- | 18-PG-17302 | Pressure Gauge With Diaphragm Seal | PP-1704 DISCHARGE | 1812-PS07-173 | On-line | 18-25-WO-17101-A1K-ET | - | - | - | C01
- | 18-PICSA-17106 | DCS | LP NITROGEN TO VE-1701 / VE-1702 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-PT-17106 | Pressure Transmitter With In-Line Diaphragm Seal | LP NITROGEN TO VE-1701 / VE-1702 | 1812-PS07-171 | On-line | 18-80-CT-17105-B1B-E | DCS-AI | - | - | C01
- | 18-PV-17106A | Globe | LP NITROGEN TO VE-1701 | 1812-PS07-171 | In-line | 18-25-LN-17101-CA2A-N | DCS-AO | - | - | C01
- | 18-PV-17106B | Ball | LP NITROGEN TO VE-1702 | 1812-PS07-171 | In-line | 18-25-CT-17105-B1B-E | DCS-AO | - | - | C01
- | 18-PIA-17202 | DCS | TEA FROM PP-1701A | 1812-PS07-172 | CCR | - | - | - | - | C01
- | 18-PT-17202 | Pressure Transmitter With In-Line Diaphragm Seal | TEA FROM PP-1701A | 1812-PS07-172 | On-line | 18-25-CT-17211-D21L-E | DCS-AI | - | - | C01
- | 18-PIA-17204 | DCS | TEA FROM PP-1702A | 1812-PS07-172 | CCR | - | - | - | - | C01
- | 18-PT-17204 | Pressure Transmitter With In-Line Diaphragm Seal | TEA FROM PP-1702A | 1812-PS07-172 | On-line | 18-15-CT-17213-D21L-E | DCS-AI | - | - | C01
- | 18-PIA-17206 | DCS | TEA FROM PP-1701B | 1812-PS07-172 | CCR | - | - | - | - | C01
- | 18-PT-17206 | Pressure Transmitter With In-Line Diaphragm Seal | TEA FROM PP-1701B | 1812-PS07-172 | On-line | 18-25-CT-17212-D21L-E | DCS-AI | - | - | C01
- | 18-PIA-17208 | DCS | TEA FROM PP-1702B | 1812-PS07-172 | CCR | - | - | - | - | C01
- | 18-PT-17208 | Pressure Transmitter With In-Line Diaphragm Seal | TEA FROM PP-1702B | 1812-PS07-172 | On-line | 18-15-CT-17225-D21L-E | DCS-AI | - | - | C01
- | 18-PIC-17301 | DCS | PP-1704 DISCHARGE | 1812-PS07-173 | CCR | - | - | - | - | C01
- | 18-PT-17301 | Pressure Transmitter With Diaphragm Seal | PP-1704 DISCHARGE | 1812-PS07-173 | On-line | 18-25-WO-17101-A1K-ET | DCS-AI | - | - | C01
- | 18-PV-17301 | Globe | White Oil return to VE-1701 | 1812-PS07-173 | In-line | 18-20-WO-17304-A1K-ET | DCS-AO | - | - | C01
- | 18-PICA-17302 | DCS | LP NITROGEN/WHITE OIL TO FLARE | 1812-PS07-173 | CCR | - | - | - | - | C01
- | 18-PT-17302 | Pressure Transmitter With Diaphragm Seal | LP NITROGEN/WHITE OIL TO FLARE | 1812-PS07-173 | On-line | 18-25-WO-17305-A1K-ET | DCS-AI | - | - | C01
- | 18-PV-17302A | Globe | LP NITROGEN TO VE-1703 | 1812-PS07-173 | In-line | 18-25-LN-17302-A1K-N | DCS-AO | - | - | C01
- | 18-PV-17302B | Globe | NITROGEN/White Oil TO FLARE | 1812-PS07-173 | In-line | 18-25-WO-17305-A1K-ET | DCS-AO | - | - | C01
- | 18-FO-17102 | RESTRICITION ORIFICE | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | In-line | 18-25-CIP-17101-D21A-N | - | - | - | C01
- | 18-FO-17104 | RESTRICITION ORIFICE | LP NITROGEN TO WHITE OIL DRUM | 1812-PS07-171 | In-line | 18-25-LN-17107-CA2A-N | - | - | - | C01
- | 18-FO-17106 | RESTRICITION ORIFICE | FLUSHING TO VE-1705 | 1812-PS07-171 | In-line | 18-15-CT-17130-D21L-E | - | - | - | C01
- | 18-FO-17107 | RESTRICITION ORIFICE | LP NITROGEN TO VE-1705 | 1812-PS07-171 | In-line | 18-25-LN-17108-B1B-N | - | - | - | C01
- | 18-FO-17109 | RESTRICITION ORIFICE | NITROGEN TO TEA CONTAINER | 1812-PS07-171 | In-line | 18-25-LN-17105-B1B-N | - | - | - | C01
- | 18-FG-17115 | VARIABLE AREA FLOWMETER | LP NITROGEN TO 17SP120 | 1812-PS07-171 | In-line | 18-25-LN-17110-CA2A-N | - | - | - | C01
- | 18-FQIA-17101 | DCS | TEA TO VE-1701 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-FT-17101 | CORIOLIS MASS FLOWMETER | TEA TO VE-1701 | 1812-PS07-171 | In-line | 18-25-CT-17101-B1B-E | DCS-AI | - | - | C01
- | 18-FI-17105B | Local Indicator | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | Field | Local Panel | DCS-AO | - | - | C01
- | 18-FI-17105 | DCS | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-FT-17105 | CORIOLIS MASS FLOWMETER | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | In-line | 18-25-CIP-17101-D21A-N | DCS-AI | - | - | C01
- | 18-FQISA-17108 | DCS | NITROGEN TO TEA CONTAINER | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-FT-17108 | VORTEX FLOWMETER | NITROGEN TO TEA CONTAINER | 1812-PS07-171 | In-line | 18-25-LN-17105-B1B-N | DCS-AI | - | - | C01
- | 18-FQI-17114 | DCS | WHITE OIL FLUSH FROM PP-1703 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-FT-17114 | CORIOLIS MASS FLOWMETER | WHITE OIL FLUSH FROM PP-1703 | 1812-PS07-171 | In-line | 18-25-WO-17101-A1K-E | DCS-AI | - | - | C01
- | 18-LISA-17101 | DCS | VE-1701 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-LT-17101 | RADAR LEVEL TRANS. | VE-1701 | 1812-PS07-171 | Equip. | VE-1701/L2 | DCS-AI | - | - | C01
- | 18-LI-17102 | Local Indicator | VE-1701 | 1812-PS07-171 | Field | Field | DCS-AO | - | - | C01
- | 18-LISA-17102 | DCS | VE-1701 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-LT-17102 | RADAR LEVEL TRANS. | VE-1701 | 1812-PS07-171 | Equip. | VE-1701/L1 | DCS-AI | - | - | C01
- | 18-LI-17103 | Local Indicator | VE-1702 | 1812-PS07-171 | Field | Field | DCS-AO | - | - | C01
- | 18-LISA-17103 | DCS | VE-1702 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-LT-17103 | D/P Level Transmitter with Extended Diaphgram Seal | VE-1702 | 1812-PS07-171 | Equip. | VE-1702/L1 L2 | DCS-AI | - | - | C01
- | 18-LI-17104B | Local Indicator | VE-1702 | 1812-PS07-171 | Field | Local Panel | DCS-AO | - | - | C01
- | 18-LISA-17104 | DCS | VE-1705 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-LT-17104 | D/P Level Transmitter with Extended Diaphgram Seal | VE-1705 | 1812-PS07-171 | Equip. | VE-1705/L1 L2 | DCS-AI | - | - | C01
- | 18-LIA-17107 | DCS | VE-1706 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-LT-17107 | D/P Level Transmitter with Diaphgram Seal | VE-1706 | 1812-PS07-171 | Equip. | VE-1706 | DCS-AI | - | - | C01
- | 18-LAH-17108 | DCS | VE-1705 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-LS-17108 | LEVEL SWITCH | VE-1705 | 1812-PS07-171 | Equip. | VE-1705/L3 | DCS-DI | - | - | C01
- | 18-LISA-17301 | DCS | VE-1703 | 1812-PS07-173 | CCR | - | - | - | - | C01
- | 18-LT-17301 | D/P Level Transmitter with Diaphgram Seal | VE-1703 | 1812-PS07-173 | Equip. | VE-1703/L1 L2 | DCS-AI | - | - | C01
- | 18-XV-17101 | Ball | LP N2 FROM HEADER | 1812-PS07-171 | In-line | 18-25-LN-17106-CA2A-N | - | - | - | C01
- | 18-XN-17101 | Solenoid Valve | LP N2 FROM HEADER | 1812-PS07-171 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-17101 | Limit Switch | LP N2 FROM HEADER | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-17101 | Limit Switch | LP N2 FROM HEADER | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XV-17102 | Ball | LP NITROGEN TO VE-1701 | 1812-PS07-171 | In-line | 18-25-LN-17105-B1B-E | - | - | - | C01
- | 18-XN-17102 | Solenoid Valve | LP NITROGEN TO VE-1701 | 1812-PS07-171 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-17102 | Limit Switch | LP NITROGEN TO VE-1701 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-17102 | Limit Switch | LP NITROGEN TO VE-1701 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XV-17103 | Ball | LP NITROGEN TO VE-1702 | 1812-PS07-171 | In-line | 18-25-LN-17106-B1B-E | - | - | - | C01
- | 18-XN-17103 | Solenoid Valve | LP NITROGEN TO VE-1702 | 1812-PS07-171 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-17103 | Limit Switch | LP NITROGEN TO VE-1702 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-17103 | Limit Switch | LP NITROGEN TO VE-1702 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XV-17104 | Ball | TEA TO VE-1701 | 1812-PS07-171 | In-line | 18-25-CT-17101-B1B-E | - | - | - | C01
- | 18-XN-17104 | Solenoid Valve | TEA TO VE-1701 | 1812-PS07-171 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-17104 | Limit Switch | TEA TO VE-1701 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-17104 | Limit Switch | TEA TO VE-1701 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-HS-17108 | Pushbutton | XV-17105 RESET | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-XV-17105 | Ball | TEA CONTAINER ISOLATION VALVE | 1812-PS07-171 | In-line | 18-25-CT-17101-B1B-E | - | - | - | C01
- | 18-XN-17105 | Solenoid Valve | TEA CONTAINER ISOLATION VALVE | 1812-PS07-171 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-17105 | Limit Switch | TEA CONTAINER ISOLATION VALVE | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-17105 | Limit Switch | TEA CONTAINER ISOLATION VALVE | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XV-17106 | Ball | FLUSHING TO VE-1705 | 1812-PS07-171 | In-line | 18-15-CT-17130-D21L-E | - | - | - | C01
- | 18-XN-17106 | Solenoid Valve | FLUSHING TO VE-1705 | 1812-PS07-171 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-17106 | Limit Switch | FLUSHING TO VE-1705 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-17106 | Limit Switch | FLUSHING TO VE-1705 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XHSO-17106 | Pushbutton | FLUSHING TO VE-1705 | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-XHSC-17106 | Pushbutton | FLUSHING TO VE-1705 | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-XV-17107 | Ball | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | In-line | 18-25-CIP-17101-D21A-N | - | - | - | C01
- | 18-XN-17107 | Solenoid Valve | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-17107 | Limit Switch | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-17107 | Limit Switch | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XHSO-17107 | Pushbutton | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-XHSC-17107 | Pushbutton | ISOPROPANOL TO VE-1705 | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-XXV-17108 | Ball | WASTE WHITE OIL FROM VE-1705 TO DRUM | 1812-PS07-171 | In-line | 18-15-CT-17139-B1B-E | - | - | - | C01
- | 18-XXN-17108 | Solenoid Valve | WASTE WHITE OIL FROM VE-1705 TO DRUM | 1812-PS07-171 | On-off Valve | - | SIS-DO | - | - | C01
- | 18-XZSH-17108 | Limit Switch | WASTE WHITE OIL FROM VE-1705 TO DRUM | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-17108 | Limit Switch | WASTE WHITE OIL FROM VE-1705 TO DRUM | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XXHSO-17108 | Pushbutton | WASTE WHITE OIL FROM VE-1705 TO DRUM | 1812-PS07-171 | Field | Local Panel | SIS-DI | - | - | C01
- | 18-XXHSC-17108 | Pushbutton | WASTE WHITE OIL FROM VE-1705 TO DRUM | 1812-PS07-171 | Field | Local Panel | SIS-DI | - | - | C01
- | 18-XV-17111 | Ball | White Oil to VE-1701 | 1812-PS07-171 | In-line | 18-25-WO-17101-A1K-ET | - | - | - | C01
- | 18-XN-17111 | Solenoid Valve | White Oil to VE-1701 | 1812-PS07-171 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-17111 | Limit Switch | White Oil to VE-1701 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-17111 | Limit Switch | White Oil to VE-1701 | 1812-PS07-171 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XHSO-17111 | Pushbutton | White Oil to VE-1701 | 1812-PS07-171 | Field | Field | DCS-DI | - | - | C01
- | 18-XHSC-17111 | Pushbutton | White Oil to VE-1701 | 1812-PS07-171 | Field | Field | DCS-DI | - | - | C01
- | 18-PCV-17103 | PRESSURE REGULATOR | LP NITROGEN TO TEA CONTAINER | 1812-PS07-171 | In-line | 18-25-LN-17106-CA2A-N | - | - | - | C01
- | 18-PCV-17110 | PRESSURE REGULATOR | LP NITROGEN TO VE-1705 | 1812-PS07-171 | In-line | 18-25-LN-17108-CA2A-N | - | - | - | C01
- | 18-PCV-17113 | PRESSURE REGULATOR | LP NITROGEN TO WHITE OIL DRUM | 1812-PS07-171 | In-line | 18-25-LN-17107-CA2A-N | - | - | - | C01
- | 18-YSA-17101 | DCS | WHITE OIL DRUM | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-YS-17101 | STATIC GROUDING SYSTEM | WHITE OIL DRUM | 1812-PS07-171 | Field | Tea Area | DCS-DI | - | - | C01
- | 18-YSA-17102 | DCS | TEA CONTAINER | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-YS-17102 | STATIC GROUDING SYSTEM | TEA CONTAINER | 1812-PS07-171 | Field | Tea Area | DCS-DI | - | - | C01
- | 18-GIA-12101 | GDS | Propylene/Ethylene | - | Field | - | - | - | - | C01
- | 18-GT-12101 | Combustible Detector | Propylene/Ethylene | - | Field | - | GDS-AI | - | - | C01
- | 18-BXSH-17101 | Infra Red Fire Detector | FIRE ALARM TEA CONTAINER | 1812-PS07-171 | Field | Tea Area | SIS-DI | Telecom | - | C01
- | 18-BXSH-17102 | Infra Red Fire Detector | FIRE ALARM TEA CONTAINER | 1812-PS07-171 | Field | Tea Area | SIS-DI | Telecom | - | C01
- | 18-BXSH-17201 | Infra Red Fire Detector | FIRE ALARM AT PP-1701A | 1812-PS07-172 | Field | Tea Area | SIS-DI | Telecom | - | C01
- | 18-BXSH-17202 | Infra Red Fire Detector | FIRE ALARM AT PP-1701B | 1812-PS07-172 | Field | Tea Area | SIS-DI | Telecom | - | C01
- | 18-BXSH-17203 | Infra Red Fire Detector | FIRE ALARM AT PP-1702A | 1812-PS07-172 | Field | Tea Area | SIS-DI | Telecom | - | C01
- | 18-BXSH-17204 | Infra Red Fire Detector | FIRE ALARM AT PP-1702B | 1812-PS07-172 | Field | Tea Area | SIS-DI | Telecom | - | C01
- | 18-HS-17101 | Soft Button | CHANGE TEA CONTAINER | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-HS-17102A | Soft Button | TEA CONTAINER OFFLINE | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-HS-17102B | Pushbutton | TEA CONTAINER OFFLINE | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-HS-17103 | Pushbutton | SYSTEM FLUSH | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-HS-17104 | Pushbutton | SYSTEM PRESSURE | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-HS-17105 | Pushbutton | SYSTEM DEPRESSURE | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-HS-17106 | Pushbutton | TEA CONTAINER ONLINE | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-HXS-17107A | Pushbutton | FIRE ALARM TEA CONTAINER | 1812-PS07-171 | Field | Field | SIS-DI | - | - | C01
- | 18-HXS-17107B | Pushbutton | LOCAL FIRE ALARM TEA CONTAINER | 1812-PS07-171 | Field | Local Panel | SIS-DI | - | - | C01
- | 18-HXS-17107C | Pushbutton | FIRE ALARM TEA CONTAINER | 1812-PS07-171 | CCR | Console | SIS-DI | - | - | C01
- | 18-HXS-17107D | Pushbutton | FIRE ALARM TEA CONTAINER 15M AWAY | 1812-PS07-171 | Field | Field | SIS-DI | - | - | C01
- | 18-UA-17109 | Soft Lamp | FIRE ALARM TEA CONTAINER | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-UL-17110A | Soft Lamp | TEA CONTAINER SEQUENCE | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-UL-17110B | Status Lamp | TEA CONTAINER SEQUENCE | 1812-PS07-171 | Field | Local Panel | DCS-DO | - | - | C01
- | 18-XL-17121 | Status Lamp | TEA CONTAINER READY TO CHANGE | 1812-PS07-171 | Field | Local Panel | DCS-DO | - | - | C01
- | 18-HXS-17208 | Pushbutton | TEA PUMPS SHUTDOWN | 1812-PS07-172 | Field | Field | SIS-DI | - | - | C01
- | 18-HS-17109A | Pushbutton | PA-1705 START | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-HS-17109B | Pushbutton | PA-1705 STOP | 1812-PS07-171 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-PSH-17211 | DCS | 18-PP-1701A DIAPHRAGM | 1812-PS07-172 | CCR | - | - | - | - | C01
- | 18-PS-17211 | Pressure Switch | 18-PP-1701A DIAPHRAGM | 1812-PS07-172 | Equip. | PP-1701A | DCS-DI | LEWA | - | C01 | 非本安，单拉
- | 18-PSH-17212 | DCS | 18-PP-1701B DIAPHRAGM | 1812-PS07-172 | CCR | - | - | - | - | C01
- | 18-PS-17212 | Pressure Switch | 18-PP-1701B DIAPHRAGM | 1812-PS07-172 | Equip. | PP-1701B | DCS-DI | LEWA | - | C01 | 非本安，单拉
- | 18-PSH-17213 | DCS | 18-PP-1702A DIAPHRAGM | 1812-PS07-172 | CCR | - | - | - | - | C01
- | 18-PS-17213 | Pressure Switch | 18-PP-1702A DIAPHRAGM | 1812-PS07-172 | Equip. | PP-1702A | DCS-DI | LEWA | - | C01 | 非本安，单拉
- | 18-PSH-17214 | DCS | 18-PP-1702B DIAPHRAGM | 1812-PS07-172 | CCR | - | - | - | - | C01
- | 18-PS-17214 | Pressure Switch | 18-PP-1702B DIAPHRAGM | 1812-PS07-172 | Equip. | PP-1702B | DCS-DI | LEWA | - | C01 | 非本安，单拉
- | 18-PSH-17303 | DCS | 18-PP-1704 DIAPHRAGM | 1812-PS07-173 | CCR | - | - | - | - | C01
- | 18-PS-17303 | Pressure Switch | 18-PP-1704 DIAPHRAGM | 1812-PS07-173 | Equip. | PP-1704 | DCS-DI | LEWA | - | C01 | 非本安，单拉
- | 18-LISA-17109 | DCS | PA-1705 | 1812-PS07-171 | CCR | - | - | - | - | C01
- | 18-LT-17109 | Level Transmitter | PA-1705 | 1812-PS07-171 | Equip. | PA-1705 | DCS-AI | EKATO | - | C01 | 本安，单拉
- | 18-HS-17201P | DCS | PP-1701A STOP | 1812-PS07-172 | MCC | - | DCS-DO | - | - | C01
- | 18-YL-17201R | DCS | PP-1701A RUN | 1812-PS07-172 | MCC | - | DCS-DI | - | - | C01
- | 18-YL-17201F | DCS | PP-1701A FAULT | 1812-PS07-172 | MCC | - | DCS-DI | - | - | C01
- | 18-SI-17201 | DCS | PP-1701A SPEED | 1812-PS07-172 | MCC | - | DCS-AI | - | - | C01
- | 18-SC-17201 | DCS | PP-1701A SPEED CONTROL | 1812-PS07-172 | MCC | - | DCS-AO | - | - | C01
- | 18-HS-17202P | DCS | PP-1701B STOP | 1812-PS07-172 | MCC | - | DCS-DO | - | - | C01
- | 18-YL-17202R | DCS | PP-1701B RUN | 1812-PS07-172 | MCC | - | DCS-DI | - | - | C01
- | 18-YL-17202F | DCS | PP-1701B FAULT | 1812-PS07-172 | MCC | - | DCS-DI | - | - | C01
- | 18-SI-17202 | DCS | PP-1701B SPEED | 1812-PS07-172 | MCC | - | DCS-AI | - | - | C01
- | 18-SC-17202 | DCS | PP-1701B SPEED CONTROL | 1812-PS07-172 | MCC | - | DCS-AO | - | - | C01
- | 18-HS-17203P | DCS | PP-1702A STOP | 1812-PS07-172 | MCC | - | DCS-DO | - | - | C01
- | 18-YL-17203R | DCS | PP-1702A RUN | 1812-PS07-172 | MCC | - | DCS-DI | - | - | C01
- | 18-YL-17203F | DCS | PP-1702A FAULT | 1812-PS07-172 | MCC | - | DCS-DI | - | - | C01
- | 18-SI-17203 | DCS | PP-1702A SPEED | 1812-PS07-172 | MCC | - | DCS-AI | - | - | C01
- | 18-SC-17203 | DCS | PP-1702A SPEED CONTROL | 1812-PS07-172 | MCC | - | DCS-AO | - | - | C01
- | 18-HS-17204P | DCS | PP-1702B STOP | 1812-PS07-172 | MCC | - | DCS-DO | - | - | C01
- | 18-YL-17204R | DCS | PP-1702B RUN | 1812-PS07-172 | MCC | - | DCS-DI | - | - | C01
- | 18-YL-17204F | DCS | PP-1702B FAULT | 1812-PS07-172 | MCC | - | DCS-DI | - | - | C01
- | 18-SI-17204 | DCS | PP-1702B SPEED | 1812-PS07-172 | MCC | - | DCS-AI | - | - | C01
- | 18-SC-17204 | DCS | PP-1702B SPEED CONTROL | 1812-PS07-172 | MCC | - | DCS-AO | - | - | C01
- | 18-HS-17301P | DCS | PP-1704 STOP | 1812-PS07-173 | MCC | - | DCS-DO | - | - | C01
- | 18-YL-17301R | DCS | PP-1704 RUN | 1812-PS07-173 | MCC | - | DCS-DI | - | - | C01
- | 18-YL-17301F | DCS | PP-1704 FAULT | 1812-PS07-173 | MCC | - | DCS-DI | - | - | C01
- | 18-SI-17301 | DCS | PP-1704 SPEED | 1812-PS07-173 | MCC | - | DCS-AI | - | - | C01
- | 18-SC-17301 | DCS | PP-1704 SPEED CONTROL | 1812-PS07-173 | MCC | - | DCS-AO | - | - | C01
- | 18-HS-17109P | DCS | PP-1705 STOP | 1812-PS07-173 | MCC | - | DCS-DO | - | - | C01
- | 18-YL-17109R | DCS | PP-1705 RUN | 1812-PS07-173 | MCC | - | DCS-DI | - | - | C01
- | 18-YL-17109F | DCS | PP-1705 FAULT | 1812-PS07-173 | MCC | - | DCS-DI | - | - | C01
1830
- | 18-TIA-21101 | DCS | PEROXIDE DOSING ROOM TEMPERATURE | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-TT-21101 | Integral Temperature Transmitter | PEROXIDE DOSING ROOM | 1830-PS07-211 | FIELD | PEROXIDE DOSING ROOM | DCS-AI | - | - | C01
- | 18-TI-21101 | Local Indicator | PEROXIDE DOSING ROOM | 1830-PS07-211 | Field | PEROXIDE DOSING ROOM | DCS-AO | - | - | C01
C01
- | 18-TISA-21102 | DCS | PEROXIDE FROM PP-2101 | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-TT-21102 | Integral Temperature Transmitter | PEROXIDE FROM PP-2101 | 1830-PS07-211 | On-line | 18-25-CP-21101-A21A-N | DCS-AI | - | - | C01
C01
- | 18-TISA-21104 | DCS | VE-2101 TEMPERATURE | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-TT-21104 | Integral Temperature Transmitter | VE-2101 | 1830-PS07-211 | Equip. | 18-VE-2101/T | DCS-AI | - | - | C01
C01
- | 18-TIA-23101 | DCS | VE-2301 TEMPERATURE | 1830-PS07-231 | CCR | - | - | - | - | C01
- | 18-TT-23101 | Integral Temperature Transmitter | VE-2301 | 1830-PS07-231 | Equip. | 18-VE-2301/T | DCS-AI | - | - | C01
C01
- | 18-TIA-23102 | DCS | VE-2302 TEMPERATURE | 1830-PS07-231 | CCR | - | - | - | - | C01
- | 18-TT-23102 | Integral Temperature Transmitter | VE-2302 | 1830-PS07-231 | Equip. | 18-VE-2302/T | DCS-AI | - | - | C01
C01
- | 18-TIA-36102 | DCS | COOLING WATER TO PX PIPE TEMPERATURE | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-TT-36102 | Integral Temperature Transmitter | COOLING WATER TO PX PIPE | 1830-PS07-211 | On-line | 18-40-CWS-36101-CA2W-N | DCS-AI | - | - | C01
C01
- | 18-TIA-36201 | DCS | OFFGAS TO ET-6602 TEMPERATURE | 1830-PS07-362 | CCR | - | - | - | - | C01
- | 18-TT-36201 | Integral Temperature Transmitter | OFFGAS TO ET-6602 | 1830-PS07-362 | On-line | 18-150-GFA-36202-A1D | PLC-AI | UP-3601 VENDOR | - | C01
C01
- | 18-TIA-66101 | DCS | OFFGAS FROM ET-6602 TEMPERATURE | 1830-PS07-661 | CCR | - | - | - | - | C01
- | 18-TT-66101 | Integral Temperature Transmitter | OFFGAS FROM ET-6602 | 1830-PS07-661 | On-line | 18-100-GFA-66101-A1D-N | DCS-AI | - | - | C01
C01
- | 18-TIA-66104 | DCS | ET-6601X outlet | 1830-PS07-661 | CCR | - | - | - | - | C01
- | 18-TT-66104 | Temperature Transmitter | ET-6601X outlet | 1830-PS07-661 | On-line | UP-6601 SKID | DCS-AI | UP-6601 VENDOR | - | C01
C01
- | 18-TI-92101 | DCS | WASTE WATER TO OSBL TEMPERATURE | 1830-PS07-921 | CCR | - | - | - | - | C01
- | 18-TT-92101 | Integral Temperature Transmitter | WASTE WATER TO OSBL | 1830-PS07-921 | On-line | 18-100-PD-92104-H1A-ET | DCS-AI | - | - | C01
C01
- | 18-TIA-92102 | DCS | VP-9201 SURFACE WATER COLLECTION TEMPERATURE | 1830-PS07-921 | CCR | - | - | - | - | C01
- | 18-TT-92102 | Integral Temperature Transmitter | VP-9201 SURFACE WATER COLLECTION | 1830-PS07-921 | Equip. | 18-VP-9201 | DCS-AI | - | - | C01
C01
- | 18-TG-36101 | Bimetal Thermometer | COOLING WATER TO PX PIPE | 1830-PS07-211 | On-line | 18-40-CWS-36101-CA2W-N | - | - | - | C01
C01
- | 18-TW-21106 | Thermowell | CWR FROM PX FEED PIPE | 1830-PS07-211 | On-line | 18-40-CWR-21101-CA2W-N | - | - | - | C01
C01
- | 18-TW-37101 | Thermowell | CWR FROM EP-3702AX/BX | 1830-PS07-371 | On-line | 18-350-CWR-37101-CA2W-N | - | - | - | C01
C01
- | 18-TW-66102 | Thermowell | CWR FROM ET-6602 | 1830-PS07-661 | On-line | 18-50-CWR-66101-CA2W-N | - | - | - | C01
C01
- | 18-TW-66103 | Thermowell | CWR FROM ET-6601X | 1830-PS07-661 | On-line | 18-50-CWR-66102-CA2W-N | - | - | - | C01
C01
- | 18-PISA-21103 | DCS | PEROXIDE FROM PP-2102 PRESSURE | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-PT-21103 | Pressure Transmitter With In-Line Diaphragm Seal | PEROXIDE FROM PP-2102 | 1830-PS07-211 | Off-line | 18-20-CP-21107-A21A-N | DCS-AI | - | - | C01
C01
- | 18-PISA-21105 | DCS | PEROXIDE FROM PP-2101 PRESSURE | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-PT-21105 | Pressure Transmitter With In-Line Diaphragm Seal | PEROXIDE FROM PP-2101 | 1830-PS07-211 | Off-line | 18-20-CP-21006-A21A-N | DCS-AI | - | - | C01
C01
- | 18-PISA-21108 | DCS | PEROXIDE FROM PP-2101 PRESSURE | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-PT-21108 | Pressure Transmitter With In-Line Diaphragm Seal | PEROXIDE FROM PP-2101 | 1830-PS07-211 | Off-line | 18-25-CP-21101-A21A-N | DCS-AI | - | - | C01
C01
- | 18-PICSA-21110 | DCS | PEROXIDE FROM PP-2101 PRESSURE | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-PT-21110 | Pressure Transmitter With In-Line Diaphragm Seal | PEROXIDE FROM PP-2101 | 1830-PS07-211 | Off-line | 18-25-CP-21101-A21A-N | DCS-AI | - | - | C01
- | 18-PV-21110 | Ball | PEROXIDE TO VE-2101 | 1830-PS07-211 | In-line | 18-25-CP-21105-A21A-N | DCS-AO | - | - | C01
C01
- | 18-PIA-22403 | DCS | VENT GAS TO VE-2201 | 1830-PS07-224 | CCR | - | - | - | - | C01
- | 18-PT-22403 | Pressure Transmitter | VENT GAS TO VE-2201 | 1830-PS07-224 | Off-line | 18-200-BV-22303-A21A-N | PLC-AI | - | 上海博隆 | C01
C01
- | 18-PICA-23101 | DCS | LP NITROGEN TO VE-2301 PRESSURE | 1830-PS07-231 | CCR | - | - | - | - | C01
- | 18-PT-23101 | Pressure Transmitter With Diaphragm Seal | LP NITROGEN TO VE-2301 | 1830-PS07-231 | Off-line | 18-25-LN-23101-A21A-N | DCS-AI | - | - | C01
- | 18-PV-23101A | Globe | LP NITROGEN TO VE-2301 | 1830-PS07-231 | In-line | 18-25-LN-23101-A21A-E | DCS-AO | - | - | C01
- | 18-PV-23101B | Globe | NITROGEN TO ATM. | 1830-PS07-231 | In-line | 18-25-LN-23101-A21A-E | DCS-AO | - | - | C01
C01
- | 18-PICA-24101 | DCS | NITROGEN TO VE-2401 PRESSURE | 1830-PS07-241 | CCR | - | - | - | - | C01
- | 18-PT-24101 | Pressure Transmitter | NITROGEN TO VE-2401 | 1830-PS07-241 | Off-line | 18-25-LN-24105-A21A-N | DCS-AI | - | - | C01
- | 18-PV-24101A | Globe | LP NITROGEN TO VE-2401 | 1830-PS07-241 | In-line | 18-25-LN-24105-A21A-N | DCS-AO | - | - | C01
- | 18-PV-24101B | Globe | LP NITROGEN LIQUID ADDITIVE DRUM | 1830-PS07-241 | In-line | 18-25-LN-24105-A21A-N | DCS-AO | - | - | C01
C01
- | 18-PICA-66101 | DCS | OFFGAS TO ET-6602 PRESSURE | 1830-PS07-661 | CCR | - | - | - | - | C01
- | 18-PT-66101 | Pressure Transmitter | OFFGAS TO ET-6602 | 1830-PS07-661 | Off-line | 18-150-GFA-36201-A1D-P | DCS-AI | - | - | C01
- | 18-PV-66101 | Control Valve | By-pass pressure control valve | 1830-PS07-661 | In-line | UP-6601 SKID | DCS-AO | UP-6601 VENDOR | - | C01
C01
- | 18-PICA-66102 | DCS | OFFGAS TO ATM AT SAFE LOCATION PRESSURE | 1830-PS07-661 | CCR | - | - | - | - | C01
- | 18-PT-66102 | Pressure Transmitter | OFFGAS TO ATM AT SAFE LOCATION | 1830-PS07-661 | Off-line | 18-80-GFA-66103-A1K-N | DCS-AI | - | - | C01
- | 18-PV-66102 | Globe | VACUMM OFFGAS TO OSBL | 1830-PS07-661 | In-line | 18-80-GFA-66104-A1K-N | DCS-AO | - | - | C01
- | 18-PN-66102 | Solenoid Valve | - | 1830-PS07-661 | On-off | - | DCS-DO | - | - | C01
- | 18-PZSL-66102 | Limit Switch(Close) | - | 1830-PS07-661 | On-off | - | DCS-DI | - | - | C01
C01
- | 18-PI-92101 | DCS | WASTE WATER TO OSBL | 1830-PS07-921 | CCR | - | - | - | - | C01
- | 18-PT-92101 | Pressure Transmitter With Diaphragm Seal | WASTE WATER TO OSBL | 1830-PS07-921 | Off-line | 18-100-PD-92104-H1A-ET | DCS-AI | - | - | C01
C01
- | 18-PDIA-23105 | DCS | FL-2301A/B PRESSURE | 1830-PS07-231 | CCR | - | - | - | - | C01
- | 18-PDT-23105 | D/P Transmitter With In-Line Diaphragm Seal | FL-2301A/B | 1830-PS07-231 | Off-line | 18-25-CLA-23102-A21A-ET 18-25-CLA-23103-A21A-ET | DCS-AI | - | - | C01
C01
- | 18-PDIA-24103 | DCS | FL-2401 PRESSURE | 1830-PS07-241 | CCR | - | - | - | - | C01
- | 18-PDT-24103 | D/P Transmitter With In-Line Diaphragm Seal | FL-2401 | 1830-PS07-241 | Off-line | 18-25-CLA-24102-A21A-ET 18-25-CLA-24103-A21A-ET | DCS-AI | - | - | C01
C01
- | 18-PG-21101 | Vibration-proof Pressure Gauge | PLANT AIR TO PP-2102 | 1830-PS07-211 | On-line | 18-25-PA-21101-CA2A-N | - | - | 删除 | C01
C01
- | 18-PG-21109 | Vibration-proof PG With In-Line Diaphragm Seal | PEROXIDE FROM PP-2101 | 1830-PS07-211 | On-line | 18-25-CP-21101-A21A-N | - | - | - | C01
C01
- | 18-PG-21112 | Pressure Gauge | NITROGEN TO VE-2101 | 1830-PS07-211 | On-line | 18-15-LNF-21107-A21A-N | - | - | - | C01
C01
- | 18-PG-22301 | Pressure Gauge | LP NITROGEN TO VH-2205 | 1830-PS07-223 | On-line | 18-20-LNF-22301-A21A-N | - | - | - | C01
C01
- | 18-PG-22401 | Pressure Gauge | LP NITROGEN TO VH-2202AX | 1830-PS07-224 | On-line | 18-20-LNF-22402-A21A-N | - | - | 上海博隆 | C01
C01
- | 18-PG-22411 | Pressure Gauge | LP NITROGEN TO VH-2202BX | 1830-PS07-224 | On-line | 18-20-LNF-22401-A21A-N | - | - | 上海博隆 | C01
C01
- | 18-PG-23102 | Pressure Gauge With In-Line Diaphragm Seal | VE-2302 | 1830-PS07-231 | On-line | 18-80-CLA-23013-A21A-ET | - | - | - | C01
C01
- | 18-PG-23103 | Pressure Gauge With In-Line Diaphragm Seal | FL-2301A | 1830-PS07-231 | On-line | 18-25-CLA-23101-A21A-ET | - | - | - | C01
C01
- | 18-PG-23104 | Pressure Gauge With In-Line Diaphragm Seal | FL-2301B | 1830-PS07-231 | On-line | 18-25-CLA-23102-A21A-ET | - | - | - | C01
C01
- | 18-PG-23106 | Vibration-proof PG With In-Line Diaphragm Seal | MELT. ADDITIVES FROM PP-2301A | 1830-PS07-231 | On-line | 18-18-CLA-23109-S82A-ET | - | - | - | C01
C01
- | 18-PG-23107 | Vibration-proof PG With In-Line Diaphragm Seal | MELT. ADDITIVES FROM PP-2301B | 1830-PS07-231 | On-line | 18-18-CLA-23105-S82A-ET | - | - | - | C01
C01
- | 18-PG-24102 | Pressure Gauge | NITROGEN TO VE-2401 | 1830-PS07-241 | On-line | 18-80-LN-24104-A21A-ET | - | - | - | C01
C01
- | 18-PG-24104 | Pressure Gauge With Diaphragm Seal | FL-2401 | 1830-PS07-241 | On-line | 18-25-CLA-24102-A21A-ET | - | - | - | C01
C01
- | 18-PG-24105 | Vibration-proof PG With Diaphragm Seal | PP-2402 DISCHARGE | 1830-PS07-241 | On-line | 18-40-CLA-24101-A21A-ET | - | - | - | C01
C01
- | 18-PG-24106 | Vibration-proof PG With In-Line Diaphragm Seal | PP-2401 DISCHARGE | 1830-PS07-241 | On-line | 18-25-CLA-24104-S82A-ET | - | - | - | C01
C01
- | 18-PG-24121 | Pressure Gauge | LP N2 TO LIQUID ADDITIVE DRUM | 1830-PS07-241 | On-line | 18-25-LN-24101-CA2A-N | - | - | - | C01
C01
- | 18-PG-35204 | Pressure Gauge With Diaphragm Seal | COOLING WATER RETURN | 1830-PS07-352 | On-line | 18-150-CWR-35201-CA2W-N | - | - | - | C01
C01
- | 18-PG-36103 | Pressure Gauge With Diaphragm Seal | LP NITROGEN TO UP-3601 | 1830-PS07-361 | On-line | 18-25-DW-36101-SA2A-E | - | - | - | C01
C01
- | 18-PG-36104 | Pressure Gauge | LIQ./MELT. ADDITIVES TO PJ-3601X | 1830-PS07-361 | On-line | 18-25-LNF-36101-A21A-N | - | - | - | C01
C01
- | 18-PG-36201 | Pressure Gauge With In-Line Diaphragm Seal | OFFGAS PJ-3601X TO ET-6602 | 1830-PS07-362 | On-line | 18-25-CLA-24104-S82A-E | - | - | - | C01
C01
- | 18-PG-36202 | Pressure Gauge | LP NITROGEN TO VE-3601 | 1830-PS07-362 | On-line | 18-150-GFA-36202-A1D-P | - | - | - | C01
C01
- | 18-PG-36203 | Pressure Gauge | LP NITROGEN TO VE-3601 | 1830-PS07-362 | On-line | 18-25-LN-36406-A1D-N | - | - | - | C01
C01
- | 18-PG-66103 | Pressure Gauge | LP NITROGEN TO PV-6601X | 1830-PS07-661 | On-line | 18-25-LN-66101-A1D-N | - | - | - | C01
C01
- | 18-PG-66202 | Pressure Gauge | LP NITROGEN TO VE-6602 | 1830-PS07-662 | On-line | 18-20-LN-66202-CA2A-N | - | - | - | C01
C01
- | 18-PG-66203 | Pressure Gauge | EQUALIZING LINE TO VE-6602 | 1830-PS07-662 | On-line | 18-80-GFA-66102-A1D-N | - | - | - | C01
C01
- | 18-FISA-21102 | DCS | LP NITROGEN TO VE-2101 FLOW | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-FT-21102 | Variable Area Flowmeter | LP NITROGEN TO VE-2101 | 1830-PS07-211 | In-line | 18-15-LNF-21107-A21A-N | DCS-AI | - | - | C01
C01
- | 18-FIA-21107 | DCS | COOLING WATER FLOW | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-FT-21107 | Variable Area Flowmeter | COOLING WATER | 1830-PS07-211 | In-line | 18-40-CWR-21101-CA2W-N | DCS-AI | - | - | C01
C01
- | 18-FISA-21109 | DCS | LP NITROGEN TO PEROXIDE DRUM FLOW | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-FT-21109 | Variable Area Flowmeter | LP NITROGEN TO PEROXIDE DRUM | 1830-PS07-211 | In-line | 18-15-LNF-21102-A21A-N | DCS-AI | - | - | C01
C01
- | 18-FICSA-21103 | DCS | PEROXIDE TO PJ-3601X FLOW | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-FT-21103 | Coriolis Mass Flowmeter | PEROXIDE TO PJ-3601X | 1830-PS07-211 | In-line | 18-15-CP-21101-A21A-K | DCS-AI | - | - | C01
- | 18-FV-21103A | Ball | PEROXIDE TO UP-3601 | 1830-PS07-211 | In-line | 18-15-CP-21101-A21A-N | DCS-AO | - | - | C01
- | 18-FV-21103B | Ball | PEROXIDE TO UP-3601 | 1830-PS07-211 | In-line | 18-15-CP-21101-A21A-N | DCS-AO | - | - | C01
C01
- | 18-FIA-22301 | DCS | LP NITROGEN TO VH-2205 FLOW | 1830-PS07-223 | CCR | - | - | - | - | C01
- | 18-FT-22301 | Variable Area Flowmeter | LP NITROGEN TO VH-2205 | 1830-PS07-223 | In-line | 18-18-CLA-23109-S82A-ET | PLC-AI | - | 上海博隆 | C01
C01
- | 18-FIA-22401 | DCS | LP NITROGEN TO VH-2202AX FLOW | 1830-PS07-224 | CCR | - | - | - | - | C01
- | 18-FT-22401 | Variable Area Flowmeter | LP NITROGEN TO VH-2202AX | 1830-PS07-224 | In-line | 18-20-LNF-22402-A21A-N | PLC-AI | - | 上海博隆 | C01
C01
- | 18-FIA-22411 | DCS | LP NITROGEN TO VH-2202BX FLOW | 1830-PS07-224 | CCR | - | - | - | - | C01
- | 18-FT-22411 | Variable Area Flowmeter | LP NITROGEN TO VH-2202BX | 1830-PS07-224 | In-line | 18-20-LNF-22401-A21A-N | PLC-AI | - | 上海博隆 | C01
C01
- | 18-FICA-23101 | DCS | MELTABLE ADDITIVES TO PJ-3601X FLOW | 1830-PS07-231 | CCR | - | - | - | - | C01
- | 18-FT-23101 | Coriolis Mass Flowmeter | MELTABLE ADDITIVES TO PJ-3601X | 1830-PS07-231 | In-line | 18-20-CLA-23109-S82A-ET | DCS-AI | - | - | C01
C01
- | 18-FICA-24101 | DCS | LIQUID ADDITIVES TO PJ-3601X FLOW | 1830-PS07-241 | CCR | - | - | - | - | C01
- | 18-FT-24101 | Coriolis Mass Flowmeter | LIQUID ADDITIVES TO PJ-3601X | 1830-PS07-241 | In-line | 18-25-CLA-24104-S82A-ET | DCS-AI | - | - | C01
C01
- | 18-FXSLL-36102 | SIS | PP POWDER TO UP-3601 | 1830-PS07-361 | CCR | - | - | - | - | C01
- | 18-FXT-36102 | Microwave Flowmeter | PP POWDER TO UP-3601 | 1830-PS07-361 | On-line | 18-400-PPD-36101-A21P-N | SIS-AI | - | - | C01
C01
- | 18-FICSA-36103 | DCS | DEMIN. WATER TO PJ-3601X FLOW | 1830-PS07-361 | CCR | - | - | - | - | C01
- | 18-FT-36103 | Coriolis Mass Flowmeter | DEMIN. WATER TO PJ-3601X | 1830-PS07-361 | In-line | 18-25-DW-36101-SA2A-E | DCS-AI | - | - | C01
- | 18-FV-36103 | Globe | DEMINERALIZED WATER FROM HEADER TO UP-3601 | 1830-PS07-361 | In-line | 18-25-DW-36101-SA2A-E | DCS-AO | - | - | C01
C01
- | 18-FIA-36104 | DCS | LP NITROGEN TO UP-3601 FLOW | 1830-PS07-361 | CCR | - | - | - | - | C01
- | 18-FT-36104 | Variable Area Flowmeter | LP NITROGEN TO UP-3601 | 1830-PS07-361 | In-line | 18-25-LNF-36101-A21A-N | PLC-AI | - | 挤出机 | C01
C01
- | 18-FQI-92102 | DCS | WASTE W ATER TO OSBL FLOW | 1830-PS07-921 | CCR | - | - | - | - | C01
- | 18-FT-92102 | Magnetic Flowmeter | WASTE W ATER TO OSBL | 1830-PS07-921 | In-line | 18-100-PD-92104-H1A-E | DCS-AI | - | - | C01
C01
- | 18-FG-37101 | Variable Area Flowmeter | LP STEAM TO VE3701X | 1830-PS07-371 | In-line | 18-80-LLS-37101-CA2D-H | - | - | - | C01
C01
- | 18-FG-66101 | Variable Area Flowmeter | LP NITROGEN TO PV-6601X | 1830-PS07-661 | In-line | 18-25-LN-66101-A1D-N | - | - | - | C01
C01
- | 18-FG-66102 | Variable Area Flowmeter | DEMIN. WATER TO UP-6601 | 1830-PS07-661 | In-line | 18-25-DW1-66101-SA2A-E | - | - | - | C01
C01
- | 18-FG-66201 | Variable Area Flowmeter | LP NITROGEN TO VE-6602 | 1830-PS07-662 | In-line | 18-20-LN-66202-CA2A-N | - | - | - | C01
C01
- | 18-FG-92101 | Variable Area Flowmeter | LP STEAM TO VP-9201 | 1830-PS07-921 | In-line | 18-50-LLS-92101-CA2D-H | - | - | - | C01
C01
- | 18-FO-21101 | Restriction Orifice | LP NITROGEN TO VE-2101 | 1830-PS07-211 | In-line | 18-15-LNF-21107-A21A-N | - | - | - | C01
C01
- | 18-FO-21104 | Restriction Orifice | PEROXIDE FROM PP-2101 | 1830-PS07-211 | In-line | 18-15-CP-21101-A21A-N | - | - | - | C01
C01
- | 18-FO-21110 | Restriction Orifice | LP NITROGEN TO VE-2101 | 1830-PS07-211 | In-line | 18-15-LNF-21102-A21A-N | - | - | - | C01
C01
- | 18-FO-24103 | Restriction Orifice | LP NITROGEN TO LIQUID ADDITIVE DRUM | 1830-PS07-241 | In-line | 18-25-LN-24101-CA2A-N | - | - | - | C01
C01
- | 18-LISA-21101 | DCS | 18-VE-2101 | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-LT-21101 | D/P Level Transmitter With Diaphgram Seal | 18-VE-2101 | 1830-PS07-211 | Equip. | 18-VE-2101 | DCS-AI | - | - | C01
- | 18-LI-21101 | Local Indicator | 18-VE-2101 | 1830-PS07-211 | Field | Local Panel | DCS-AO | - | - | C01
C01
- | 18-LIA-22403 | DCS | 18-VE-2201 | 1830-PS07-224 | CCR | - | - | - | - | C01
- | 18-LT-22403 | D/P Level Transmitter With Diaphgram Seal | 18-VE-2201 | 1830-PS07-224 | Equip. | 18-VE-2201 | PLC-AI | - | 上海博隆18-LT-22411 | C01
C01
- | 18-LISA-23101 | DCS | 18-VE-2301 | 1830-PS07-231 | CCR | - | - | - | - | C01
- | 18-LT-23101 | D/P Level Transmitter With Extended Diaphgram Seal | 18-VE-2301 | 1830-PS07-231 | Equip. | 18-VE-2301/L1 L2 | DCS-AI | - | - | C01
- | 18-LI-23101 | Local Indicator | 18-VE-2301 | 1830-PS07-231 | Field | Field | DCS-AO | - | - | C01
C01
- | 18-LISA-23102 | DCS | 18-VE-2302 | 1830-PS07-231 | CCR | - | - | - | - | C01
- | 18-LT-23102 | D/P Level Transmitter With Extended Diaphgram Seal | 18-VE-2302 | 1830-PS07-231 | Equip. | 18-VE-2302/L1 L2 | DCS-AI | - | - | C01
C01
- | 18-LISA-24101 | DCS | 18-VE-2401 | 1830-PS07-241 | CCR | - | - | - | - | C01
- | 18-LT-24101 | D/P Level Transmitter With Extended Diaphgram Seal | 18-VE-2401 | 1830-PS07-241 | Equip. | 18-VE-2401/L1 L2 | DCS-AI | - | - | C01
- | 18-LI-24101 | Local Indicator | 18-VE-2401 | 1830-PS07-241 | Field | Field | DCS-AO | - | - | C01
C01
- | 18-LISA-92101 | DCS | VP-9201 SURFACE WATER COLLECTION | 1830-PS07-921 | CCR | - | - | - | - | C01
- | 18-LT-92101 | Radar Level Transmitter | VP-9201 SURFACE WATER COLLECTION | 1830-PS07-921 | Equip. | 18-VP-9201 | DCS-AI | - | - | C01
C01
- | 18-LISA-66101 | DCS | 18-VE-6601X | 1830-PS07-661 | CCR | - | - | - | - | C01
- | 18-LT-66101 | Level Transmitter | 18-VE-6601X | 1830-PS07-661 | Equip. | UP-6601 SKID | DCS-AI | UP-6601 VENDOR | - | C01
C01
- | 18-LICA-66202 | DCS | 18-VE-6602 | 1830-PS07-662 | CCR | - | - | - | - | C01
- | 18-LT-66202 | Displacer Transmitter | 18-VE-6602 | 1830-PS07-662 | Equip. | 18-VE-6602/L1 L2 | DCS-AI | - | - | C01
- | 18-LV-66202 | Globe | WASTE WATER TO VP-9201 | 1830-PS07-662 | In-line | 18-50-PD-66203-H1A-N | DCS-AO | - | - | C01
C01
- | 18-LIA-66203 | DCS | 18-VE-6602 | 1830-PS07-662 | CCR | - | - | - | - | C01
- | 18-LT-66203 | Displacer Transmitter | 18-VE-6602 | 1830-PS07-662 | Equip. | 18-VE-6603/L3 L4 | DCS-AI | - | - | C01
C01
- | 18-LSA-22301 | DCS | 18-VH-2205 | 1830-PS07-223 | CCR | - | - | - | - | C01
- | 18-LS-22301 | Tuning Folk | 18-VH-2205 | 1830-PS07-223 | Equip. | 18-VH-2205 | PLC-DI | - | 上海博隆 | C01
C01
- | 18-LA-22302 | DCS | 18-VH-2205 | 1830-PS07-223 | CCR | - | - | - | - | C01
- | 18-LS-22302 | Tuning Folk | 18-VH-2205 | 1830-PS07-223 | Equip. | 18-VH-2205 | PLC-DI | - | 上海博隆 | C01
C01
- | 18-LSL-36202 | DCS | 18-VE-36202 | 1830-PS07-362 | CCR | - | - | - | - | C01
- | 18-LS-36202 | Tuning Folk | 18-VE-36202 | 1830-PS07-362 | Equip. | 18-VE-36202 | DCS-DI | - | - | C01
C01
- | 18-HIC-36105 | DCS | PEROXIDE FROM PP-2101 TO UP-3601 | 1830-PS07-361 | CCR | - | - | - | - | C01
- | 18-HV-36105 | Ball | PEROXIDE FROM PP-2101 TO UP-3601 | 1830-PS07-361 | In-line | 18-15-CP-21101-A21A-ET | DCS-AO | - | - | C01
C01
- | 18-HIC-66102 | DCS | OFFGAS TO ATM AT SAFE LOCATION | 1830-PS07-661 | CCR | - | - | - | - | C01
- | 18-HV-66102 | Globe | OFFGAS TO ATM AT SAFE LOCATION | 1830-PS07-661 | In-line | 18-80-BV-66103-A1K-N | DCS-AO | - | - | C01
- | 18-HZSH-66102 | Limit Switch(Open) | - | 1830-PS07-661 | On-off | - | DCS-DI | - | - | C01
- | 18-HZSL-66102 | Limit Switch(Close) | - | 1830-PS07-661 | On-off | - | DCS-DI | - | - | C01
C01
- | 18-XV-21101 | Ball | PEROXIDE FROM PP-2102 | 1830-PS07-211 | In-line | 18-20-CP-21103-A21A-N | - | - | - | C01
- | 18-XN-21101 | Solenoid Valve | - | 1830-PS07-211 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-21101 | Limit Switch(Open) | - | 1830-PS07-211 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-21101 | Limit Switch(Close) | - | 1830-PS07-211 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XHSO-21101 | Pushbutton | PEROXIDE FROM PP-2102 | 1830-PS07-211 | Field | Local Panel | DCS-DI | - | - | C01
- | 18-XHSC-21101 | Pushbutton | PEROXIDE FROM PP-2102 | 1830-PS07-211 | Field | Local Panel | DCS-DI | - | - | C01
C01
- | 18-XV-21102 | Ball | PLANT AIR TO PP-2102 | 1830-PS07-211 | In-line | 18-25-PA-21101-CA2A-N | - | - | 删除 | C01
- | 18-XN-21102 | Solenoid Valve | - | 1830-PS07-211 | On-off Valve | - | DCS-DO | - | 删除 | C01
- | 18-XZSH-21102 | Limit Switch(Open) | - | 1830-PS07-211 | On-off Valve | - | DCS-DI | - | 删除 | C01
- | 18-XZSL-21102 | Limit Switch(Close) | - | 1830-PS07-211 | On-off Valve | - | DCS-DI | - | 删除 | C01
- | 18-XHSO-21102 | Pushbutton | PLANT AIR TO PP-2102 | 1830-PS07-211 | Field | Local Panel | DCS-DI | - | 删除 | C01
- | 18-XHSC-21102 | Pushbutton | PLANT AIR TO PP-2102 | 1830-PS07-211 | Field | Local Panel | DCS-DI | - | 删除 | C01
C01
- | 18-XV-21103 | Ball | PEROXIDE TO PP-2101 | 1830-PS07-211 | In-line | 18-25-CP-21104-A21A-N | - | - | - | C01
- | 18-XN-21103 | Solenoid Valve | - | 1830-PS07-211 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-21103 | Limit Switch(Open) | - | 1830-PS07-211 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-21103 | Limit Switch(Close) | - | 1830-PS07-211 | On-off Valve | - | DCS-DI | - | - | C01
C01
- | 18-XV-21104 | Ball | FIRE WATER TO PX DOSING ROOM | 1830-PS07-211 | In-line | 18-65-FW-21101-BA2B-ET | - | - | - | C01
- | 18-XN-21104 | Solenoid Valve | - | 1830-PS07-211 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-21104 | Limit Switch(Open) | - | 1830-PS07-211 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-21104 | Limit Switch(Close) | - | 1830-PS07-211 | On-off Valve | - | DCS-DI | - | - | C01
C01
- | 18-XV-23101 | Ball | MELTABLE ADD. TO VE-2302 | 1830-PS07-231 | In-line | 18-50-CLA-23112-A21A | - | - | - | C01
- | 18-XN-23101 | Solenoid Valve | - | 1830-PS07-231 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-23101 | Limit Switch(Open) | - | 1830-PS07-231 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-23101 | Limit Switch(Close) | - | 1830-PS07-231 | On-off Valve | - | DCS-DI | - | - | C01
C01
- | 18-XV-24102 | Ball/Rotary | LIQUID ADDITIVES TO VE-2401 | 1830-PS07-241 | In-line | 18-40-CLA-24101-A21A-E | - | - | - | C01
- | 18-XN-24102 | Solenoid Valve | - | 1830-PS07-241 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-24102 | Limit Switch(Open) | - | 1830-PS07-241 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-24102 | Limit Switch(Close) | - | 1830-PS07-241 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XHSO -24102 | Pushbutton | LIQUID ADDITIVES TO VE-2401 | 1830-PS07-241 | Field | Field | DCS-DI | - | - | C01
- | 18-XHSC -24102 | Pushbutton | LIQUID ADDITIVES TO VE-2401 | 1830-PS07-241 | Field | Field | DCS-DI | - | - | C01
C01
- | 18-XXV-36101 | 3-way Valve | PEROXIDE FROM PP-2101 TO UP-3601 | 1830-PS07-361 | In-line | 18-15-CP-21101-A21A-K | - | - | - | C01
- | 18-XN-36101A | Solenoid Valve | - | 1830-PS07-361 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XXN-36101B | Solenoid Valve | - | 1830-PS07-361 | On-off Valve | - | SIS-DO | - | - | C01
- | 18-XZSH-36101 | Limit Switch(Open) | - | 1830-PS07-361 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-36101 | Limit Switch(Close) | - | 1830-PS07-361 | On-off Valve | - | DCS-DI | - | - | C01
C01
- | 18-XXV-36102 | Ball | PEROXIDE FROM PP-2101 TO UP-3601 | 1830-PS07-361 | In-line | 18-15-CP-21101-A22A-K | - | - | - | C01
- | 18-XN-36102A | Solenoid Valve | - | 1830-PS07-361 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XXN-36102B | Solenoid Valve | - | 1830-PS07-361 | On-off Valve | - | SIS-DO | - | - | C01
- | 18-XZSH-36102 | Limit Switch(Open) | - | 1830-PS07-361 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-36102 | Limit Switch(Close) | - | 1830-PS07-361 | On-off Valve | - | DCS-DI | - | - | C01
C01
- | 18-XV-66101 | Ball | OFFGAS FROM UP-3601 | 1830-PS07-661 | In-line | 18-150-GFA-36201-A1D-P | - | - | - | C01
- | 18-XN-66101 | Solenoid Valve | - | 1830-PS07-661 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-66101 | Limit Switch(Open) | - | 1830-PS07-661 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-66101 | Limit Switch(Close) | - | 1830-PS07-661 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XHSO-66101 | Pushbutton | - | 1830-PS07-661 | Field | Field | DCS-DI | - | - | C01
- | 18-XHSC-66101 | Pushbutton | - | 1830-PS07-661 | Field | Field | DCS-DI | - | - | C01
C01
- | 18-XV-66105 | Ball | VE-6601X Water makeup | 1830-PS07-661 | In-line | UP-6601 SKID | - | UP-6601 VENDOR | - | C01
- | 18-XN-66105 | Solenoid Valve | - | 1830-PS07-661 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-66105 | Limit Switch(Open) | - | 1830-PS07-661 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-66105 | Limit Switch(Close) | - | 1830-PS07-661 | On-off Valve | - | DCS-DI | - | - | C01
C01
- | 18-XV-66106 | Ball | VE-6601X Waste water outlet | 1830-PS07-661 | In-line | UP-6601 SKID | - | UP-6601 VENDOR | - | C01
- | 18-XN-66106 | Solenoid Valve | - | 1830-PS07-661 | On-off Valve | - | DCS-DO | - | - | C01
- | 18-XZSH-66106 | Limit Switch(Open) | - | 1830-PS07-661 | On-off Valve | - | DCS-DI | - | - | C01
- | 18-XZSL-66106 | Limit Switch(Close) | - | 1830-PS07-661 | On-off Valve | - | DCS-DI | - | - | C01
C01
- | 18-PCV-21111 | Pressure Reducing Regulator | LP NITROGEN TO VE-2101 | 1830-PS07-211 | In-line | 18-15-LNF-21107-A21A-N | - | - | - | C01
C01
- | 18-PCV-21113 | Pressure Reducing Regulator | LP NITROGEN TO PEROXIDE DRUM | 1830-PS07-211 | In-line | 18-15-LNF-21102-A21A-N | - | - | - | C01
C01
- | 18-PCV-22302 | Pressure Reducing Regulator | LP NITROGEN TO VH-2205 | 1830-PS07-223 | In-line | 18-20-LNF-22301-A21A-N | - | - | - | C01
C01
- | 18-PCV-22402 | Pressure Reducing Regulator | LP NITROGEN TO VH-2202AX | 1830-PS07-224 | In-line | 18-20-LNF-22402-A21A-N | - | - | 上海博隆 | C01
C01
- | 18-PCV-22412 | Pressure Reducing Regulator | LP NITROGEN TO VH-2202BX | 1830-PS07-224 | In-line | 18-20-LNF-22401-A21A-N | - | - | 上海博隆 | C01
C01
- | 18-PCV-24108 | Pressure Reducing Regulator | LP NITROGEN LIQUID ADDITIVE DRUM | 1830-PS07-241 | In-line | 18-25-LN-24101-CA2A-N | - | - | - | C01
C01
- | 18-PCV-36107 | Pressure Reducing Regulator | LP N2 (filtered) TO UP-3601 | 1830-PS07-361 | In-line | 18-25-LNF-36101-A21A-N | - | - | - | C01
C01
- | 18-PCV-36204 | Pressure Reducing Regulator | LP N2 TO UP-3601 | 1830-PS07-362 | In-line | 18-25-LN-36406-A1D-N | - | - | - | C01
C01
- | 18-PCV-36205 | Pressure Reducing Regulator | LP N2 TO UP-3601 | 1830-PS07-362 | In-line | 18-15-LN-36405-CA2A-N | - | - | - | C01
C01
- | 18-PCV-66201 | Pressure Reducing Regulator | LP N2 FROM HEADER TO VE-6602 | 1830-PS07-662 | In-line | 18-20-LN-66202-CA2A-N | - | - | - | C01
C01
- | 18-AXA-21101B | Local Indicator | PEROXIDE DOSING ROOM | 1830-PS07-211 | Field | Local Alarm | SIS-DO | - | - | C01
- | 18-AXSL-21101A | SIS | PEROXIDE DOSING ROOM | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-AXT-21101 | O2 ANALYZER | PEROXIDE DOSING ROOM | 1830-PS07-211 | FIELD | PEROXIDE DOSING ROOM | SIS-AI | - | - | C01
C01
- | 18-BXS-21101 | Infra Red Fire Detector | FIRE ALARM PEROXIDE DOSING ROOM | 1830-PS07-211 | Field | PEROXIDE DOSING ROOM | SIS-DI | Telecom | - | C01
C01
- | 18-HXS-21101A | Pushbutton | ESD PEROXIDE DOSING | 1830-PS07-211 | Field | Field | SIS-DI | - | - | C01
- | 18-HXS-21101B | Pushbutton | ESD PEROXIDE DOSING | 1830-PS07-211 | CCR | Console | SIS-DI | - | - | C01
- | 18-GIA-30101 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 电梯井 | - | - | - | C01
- | 18-GT-30101 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 电梯井 | GDS-AI | - | - | C01
- | 18-GIA-30102 | GDS | Propylene/Ethylene/Propane/Ethane | - | Field | 过氧化物间 | - | - | - | C01
- | 18-GT-30102 | Combustible Detector | Propylene/Ethylene/Propane/Ethane | - | Field | 过氧化物间 | GDS-AI | - | - | C01
- | 18-GIA-30103 | GDS | Propylene Propane | - | Field | 相分离间 | - | - | - | C01
- | 18-GT-30103 | Combustible Detector | Propylene Propane | - | Field | 相分离间 | GDS-AI | - | - | C01
- | 18-GIA-30201 | GDS | O2 IN AIR | - | Field | PF-3601 | - | - | - | C01
- | 18-GT-30201 | Oxygen Detector | O2 IN AIR | - | Field | PF-3601 | GDS-AI | - | - | C01
- | 18-GIA-30301 | GDS | O2 IN AIR | - | Field | PF-3501X | - | - | - | C01
- | 18-GT-30301 | Oxygen Detector | O2 IN AIR | - | Field | PF-3501X | GDS-AI | - | - | C01
- | 18-GIA-30401 | GDS | O2 IN AIR | - | Field | VH-2204X | - | - | - | C01
- | 18-GT-30401 | Oxygen Detector | O2 IN AIR | - | Field | VH-2204X | GDS-AI | - | - | C01
- | 18-GIA-30402 | GDS | Propylene Propane | - | Field | 真空系统间 | - | - | - | C01
- | 18-GT-30402 | Combustible Detector | Propylene Propane | - | Field | 真空系统间 | GDS-AI | - | - | C01
- | 18-GIA-30501 | GDS | O2 IN AIR | - | Field | VH-2203 | - | - | - | C01
- | 18-GT-30501 | Oxygen Detector | O2 IN AIR | - | Field | VH-2203 | GDS-AI | - | - | C01
- | 18-GIA-30502 | GDS | O2 IN AIR | - | Field | PZ-2201X | - | - | - | C01
- | 18-GT-30502 | Oxygen Detector | O2 IN AIR | - | Field | PZ-2201X | GDS-AI | - | - | C01
- | 18-GA-30101 | 声光报警器 | - | - | Field | - | GDS-DO | - | - | C01
- | 18-GA-30102 | 声光报警器 | - | - | Field | - | GDS-DO | - | - | C01
- | 18-GA-30103 | 声光报警器 | - | - | Field | - | GDS-DO | - | - | C01
- | 18-GA-30104 | 声光报警器 | - | - | Field | - | GDS-DO | - | - | C01
- | 18-GA-30105 | 声光报警器 | - | - | Field | - | GDS-DO | - | - | C01
- | 18-GA-30401 | 声光报警器 | - | - | Field | - | GDS-DO | - | - | C01
- | 18-AISA-66101 | DCS | O2 IN OFFGAS FROM UP-6601 | 1830-PS07-661 | CCR | - | - | - | - | C01
- | 18-AT-66101 | O2 Analyzer | O2 IN OFFGAS FROM UP-6601 | 1830-PS07-661 | Off-line | 18-15-GFA-66105-A1K-N | DCS-AI | - | - | C01
- | 18-YSA-24103 | DCS | LIQUID ADDITIVE DRUM | 1830-PS07-241 | CCR | - | - | - | - | C01
- | 18-YS-24103 | Static Grounding Transmitter | LIQUID ADDITIVE DRUM | 1830-PS07-241 | Field | - | DCS-DI | - | - | C01
- | 18-HXS-36102A | Pushbutton | EUD | 1830-PS07-361 | CCR | Local Panel | SIS-DI | - | - | C01
- | 18-HXS-36102B | Pushbutton | EUD | 1830-PS07-361 | CCR | Console | SIS-DI | - | - | C01
- | 18-HXS-36103 | Pushbutton | EUD RESET | 1830-PS07-361 | CCR | Console | SIS-DI | - | - | C01
| 18-UA-36103 | Soft Lamp | EUD | 1830-PS07-361 | CCR | - | - | - | - | C01
- | 18-PSH-21104 | DCS | 18-PP-2101 DIAPHRAGM | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-PS-21104 | Pressure Switch | 18-PP-2101 DIAPHRAGM | 1830-PS07-211 | Equip. | 18-PP-2101 | DCS-DI | LEWA | - | C01
- | 18-PSH-21102 | DCS | 18-PP-2102 DIAPHRAGM | 1830-PS07-211 | CCR | - | - | - | - | C01
- | 18-PS-21102 | Pressure Switch | 18-PP-2102 DIAPHRAGM | 1830-PS07-211 | Equip. | 18-PP-2102 | DCS-DI | LEWA | - | C01
- | 18-LISA-23103 | DCS | 18-PA-2301 | 1830-PS07-231 | CCR | - | - | - | - | C01
- | 18-LT-23103 | Level Transmitter | 18-PA-2301 | 1830-PS07-231 | Equip. | 18-PA-2301 | DCS-AI | EKATO | - | C01
- | 18-YL-21103R | DCS | 18-PP-2101 RUN | 1830-PS07-211 | MCC | 18-PP-2101 | DCS-DI | - | - | C01
- | 18-YL-21103F | DCS | 18-PP-2101 FAULT | 1830-PS07-211 | MCC | 18-PP-2101 | DCS-DI | - | - | C01
- | 18-HS-21103P | DCS | 18-PP-2101 STOP | 1830-PS07-211 | MCC | 18-PP-2101 | DCS-DO | - | - | C01
C01
- | 18-HS-21104P | DCS | 18-PP-2102 STOP | 1830-PS07-211 | MCC | 18-PP-2102 | DCS-DO | - | - | C01
- | 18-YL-21104R | DCS | 18-PP-2102 RUN | 1830-PS07-211 | MCC | 18-PP-2102 | DCS-DI | - | - | C01
- | 18-YL-21104F | DCS | 18-PP-2102 FAULT | 1830-PS07-211 | MCC | 18-PP-2102 | DCS-DI | - | - | C01
- | 18-HS-21102P | DCS | 18-PB-2101 STOP | 1830-PS07-211 | MCC | 18-PB-2101 | DCS-DO | - | - | C01
- | 18-HS-21102S | DCS | 18-PB-2101 START | 1830-PS07-211 | MCC | 18-PB-2101 | DCS-DO | - | - | C01
- | 18-YL-21102L | DCS | 18-PB-2101 REMOTE | 1830-PS07-211 | MCC | 18-PB-2101 | DCS-DI | - | - | C01
- | 18-YL-21102R | DCS | 18-PB-2101 RUN | 1830-PS07-211 | MCC | 18-PB-2101 | DCS-DI | - | - | C01
- | 18-YL-21102F | DCS | 18-PB-2101 FAULT | 1830-PS07-211 | MCC | 18-PB-2101 | DCS-DI | - | - | C01
- | 18-HS-23101S | DCS | 18-PP-2301A DCS START | 1830-PS07-231 | MCC | 18-PP-2301A | DCS-DO | - | - | C01
- | 18-HS-23101P | DCS | 18-PP-2301A DCS STOP | 1830-PS07-231 | MCC | 18-PP-2301A | DCS-DO | - | - | C01
- | 18-YL-23101L | DCS | 18-PP-2301A REMOTE | 1830-PS07-231 | MCC | 18-PP-2301A | DCS-DI | - | - | C01
- | 18-YL-23101R | DCS | 18-PP-2301A RUNNING | 1830-PS07-231 | MCC | 18-PP-2301A | DCS-DI | - | - | C01
- | 18-YL-23101F | DCS | 18-PP-2301A FAULT | 1830-PS07-231 | MCC | 18-PP-2301A | DCS-DI | - | - | C01
- | 18-SI-23101 | DCS | 18-PP-2301A SPEED | 1830-PS07-231 | MCC | 18-PP-2301A | DCS-AI | - | - | C01
- | 18-SC-23101 | DCS | 18-PP-2301A CONTROL | 1830-PS07-231 | MCC | 18-PP-2301A | DCS-AO | - | - | C01
C01
- | 18-HS-23102S | DCS | 18-PP-2301B START | 1830-PS07-231 | MCC | 18-PP-2301B | DCS-DO | - | - | C01
- | 18-HS-23102P | DCS | 18-PP-2301B STOP | 1830-PS07-231 | MCC | 18-PP-2301B | DCS-DO | - | - | C01
- | 18-YL-23102F | DCS | 18-PP-2301B FAULT | 1830-PS07-231 | MCC | 18-PP-2301B | DCS-DI | - | - | C01
- | 18-YL-23102L | DCS | 18-PP-2301B REMOTE | 1830-PS07-231 | MCC | 18-PP-2301B | DCS-DI | - | - | C01
- | 18-YL-23102R | DCS | 18-PP-2301B RUNNING | 1830-PS07-231 | MCC | 18-PP-2301B | DCS-DI | - | - | C01
- | 18-SI-23102 | DCS | 18-PP-2301B SPEED | 1830-PS07-231 | MCC | 18-PP-2301B | DCS-AI | - | - | C01
- | 18-SC-23102 | DCS | 18-PP-2301B SPEED CONTROL | 1830-PS07-231 | MCC | 18-PP-2301B | DCS-AO | - | - | C01
C01
- | 18-HS-23105S | DCS | 18-PA-2301 START | 1830-PS07-231 | MCC | 18-PA-2301 | DCS-DO | - | - | C01
- | 18-HS-23105P | DCS | 18-PA-2301 STOP | 1830-PS07-231 | MCC | 18-PA-2301 | DCS-DO | - | - | C01
- | 18-YL-23105L | DCS | 18-PA-2301 REMOTE | 1830-PS07-231 | MCC | 18-PA-2301 | DCS-DI | - | - | C01
- | 18-YL-23105R | DCS | 18-PA-2301 RUN | 1830-PS07-231 | MCC | 18-PA-2301 | DCS-DI | - | - | C01
- | 18-YL-23105F | DCS | 18-PA-2301 FAULT | 1830-PS07-231 | MCC | 18-PA-2301 | DCS-DI | - | - | C01
- | 18-II-23105 | DCS | 18-PA-2301 CURRENT | 1830-PS07-231 | MCC | 18-PA-2301 | DCS-AI | - | - | C01
- | 18-SI-23105 | DCS | 18-PA-2301 SPEED | 1830-PS07-231 | MCC | 18-PA-2301 | DCS-AI | - | - | C01
- | 18-SC-23105 | DCS | 18-PA-2301 SPEED CONTROL | 1830-PS07-231 | MCC | 18-PA-2301 | DCS-AO | - | - | C01
C01
- | 18-HS-24101S | DCS | 18-PP-2401 START | 1830-PS07-241 | MCC | 18-PP-2401 | DCS-DO | - | - | C01
- | 18-HS-24101P | DCS | 18-PP-2401 STOP | 1830-PS07-241 | MCC | 18-PP-2401 | DCS-DO | - | - | C01
- | 18-YL-24101L | DCS | 18-PP-2401 REMOTE | 1830-PS07-241 | MCC | 18-PP-2401 | DCS-DI | - | - | C01
- | 18-YL-24101R | DCS | 18-PP-2401 RUN | 1830-PS07-241 | MCC | 18-PP-2401 | DCS-DI | - | - | C01
- | 18-YL-24101F | DCS | 18-PP-2401 FAULT | 1830-PS07-241 | MCC | 18-PP-2401 | DCS-DI | - | - | C01
- | 18-SI-24101 | DCS | 18-PP-2401 SPEED | 1830-PS07-241 | MCC | 18-PP-2401 | DCS-AI | - | - | C01
- | 18-SC-24101 | DCS | 18-PP-2401 SPEED CONTROL | 1830-PS07-241 | MCC | 18-PP-2401 | DCS-AO | - | - | C01
- | 18-HS-36106S | DCS | 18-PF-3606 START | 1830-PS07-361 | MCC | 18-PF-3606 | DCS-DO | - | - | C01
- | 18-HS-36106P | DCS | 18-PF-3606 STOP | 1830-PS07-361 | MCC | 18-PF-3606 | DCS-DO | - | - | C01
- | 18-YL-36106L | DCS | 18-PF-3606 REMOTE | 1830-PS07-361 | MCC | 18-PF-3606 | DCS-DI | - | - | C01
- | 18-YL-36106R | DCS | 18-PF-3606 RUN | 1830-PS07-361 | MCC | 18-PF-3606 | DCS-DI | - | - | C01
- | 18-YL-36106F | DCS | 18-PF-3606 FAULT | 1830-PS07-361 | MCC | 18-PF-3606 | DCS-DI | - | - | C01
- | 18-HS-66101S | DCS | 18-PV-6601X START | 1830-PS07-661 | MCC | 18-PV-6601X | DCS-DO | - | - | C01
- | 18-HS-66101P | DCS | 18-PV-6601X STOP | 1830-PS07-661 | MCC | 18-PV-6601X | DCS-DO | - | - | C01
- | 18-YL-66101L | DCS | 18-PV-6601X REMOTE | 1830-PS07-661 | MCC | 18-PV-6601X | DCS-DI | - | - | C01
- | 18-YL-66101R | DCS | 18-PV-6601X RUN | 1830-PS07-661 | MCC | 18-PV-6601X | DCS-DI | - | - | C01
- | 18-YL-66101F | DCS | 18-PV-6601X FAULT | 1830-PS07-661 | MCC | 18-PV-6601X | DCS-DI | - | - | C01
- | 18-HS-92101S | DCS | 18-PP-9201A START | 1830-PS07-921 | MCC | 18-PP-9201A | DCS-DO | - | - | C01
- | 18-HS-92101P | DCS | 18-PP-9201A STOP | 1830-PS07-921 | MCC | 18-PP-9201A | DCS-DO | - | - | C01
- | 18-YL-92101L | DCS | 18-PP-9201A REMOTE | 1830-PS07-921 | MCC | 18-PP-9201A | DCS-DI | - | - | C01
- | 18-YL-92101R | DCS | 18-PP-9201A RUN | 1830-PS07-921 | MCC | 18-PP-9201A | DCS-DI | - | - | C01
- | 18-YL-92101F | DCS | 18-PP-9201A FAULT | 1830-PS07-921 | MCC | 18-PP-9201A | DCS-DI | - | - | C01
C01
- | 18-HS-92102S | DCS | 18-PP-9201B START | 1830-PS07-921 | MCC | 18-PP-9201B | DCS-DO | - | - | C01
- | 18-HS-92102P | DCS | 18-PP-9201B STOP | 1830-PS07-921 | MCC | 18-PP-9201B | DCS-DO | - | - | C01
- | 18-YL-92102L | DCS | 18-PP-9201B REMOTE | 1830-PS07-921 | MCC | 18-PP-9201B | DCS-DI | - | - | C01
- | 18-YL-92102R | DCS | 18-PP-9201B RUN | 1830-PS07-921 | MCC | 18-PP-9201B | DCS-DI | - | - | C01
- | 18-YL-92102F | DCS | 18-PP-9201B FAULT | 1830-PS07-921 | MCC | 18-PP-9201B | DCS-DI | - | - | C01
C01
- | 18-HS-HEF102AS | DCS | 边墙风机1830-HEF-102A/103A启动 | - | MCC | 1830-HEF-102A/103A | DCS-DO | - | - | C01
- | 18-HS-HEF102BS | DCS | 边墙风机1830-HEF-102B/103B启动 | - | MCC | 1830-HEF-102B/103B | DCS-DO | - | - | C01
- | 18-HS-HEF104AS | DCS | 边墙风机1830-HEF-104A启动 | - | MCC | 1830-HEF-104A | DCS-DO | - | - | C01
- | 18-HS-HEF104BS | DCS | 边墙风机1830-HEF-104B/105B启动 | - | MCC | 1830-HEF-104B/105B | DCS-DO | - | - | C01
上海博隆
添加剂系统
- | 18-HS-22112AL | PLC | 自动控制大袋粒料添加剂料斗18-VH-2204X拍打装置 开/关 | 1830-PS07-221 | Field | 18-LP-2204 | PLC-DI | - | - | C01
- | 18-HS-22112A | PLC | 手动控制大袋粒料添加剂料斗18-VH-2204X拍打装置开/关 | 1830-PS07-221 | Field | 18-LP-2204 | PLC-DI | - | - | C01
- | 18-HS-22111AL | PLC | 气动滑板阀18-XV-22111自动(远程)模式 | 1830-PS07-221 | Field | 18-LP-2204 | PLC-DI | - | - | C01
- | 18-HS-22111A | PLC | 手动控制气动滑板阀18-XV-22111的开/关 | 1830-PS07-221 | Field | 18-LP-2204 | PLC-DI | - | - | C01
- | 18-XZH-22111A | PLC | 气动滑板阀18-XV-22111开状态现场指示 | 1830-PS07-221 | Field | 18-LP-2204 | PLC-DO | - | - | C01
- | 18-XZL-22111A | PLC | 气动滑板阀18-XV-22111关状态现场指示 | 1830-PS07-221 | Field | 18-LP-2204 | PLC-DO | - | - | C01
- | 18-LAH-22301A1 | PLC | 粒料添加剂储存料斗18-VH-2205高料位现场指示 | 1830-PS07-223 | Field | 18-LP-2204 | PLC-DO | - | 分一路信号到 18LCP-2203上 | C01
- | 18-XYX-22112 | PLC | 大袋粒料添加剂料斗18-VH-2204X拍打装置开/关 电磁阀 | 1830-PS07-221 | Field | 信号引至现场电磁线圈 | PLC-DO | - | - | C01
- | 18-XYX-22111 | PLC | 气动滑板阀18-XV-22111 开/关电磁阀 | 1830-PS07-221 | Field | 18-XV-22111 | PLC-DO | - | - | C01
- | 18-XZSH-22111 | PLC | 气动滑板阀18-XV-22111 开状态监测 | 1830-PS07-221 | Field | 18-XV-22111 | PLC-DI | - | - | C01
- | 18-XZSL-22111 | PLC | 气动滑板阀18-XV-22111 关状态监测 | 1830-PS07-221 | Field | 18-XV-22111 | PLC-DI | - | - | C01
- | 18-HS-22123S | PLC | 粒料添加剂排气风机18-PB-2203X电机启动控制 | 1830-PS07-221 | MCC | 18-PB-2203X主电机 | PLC-DO | - | - | C01
- | 18-HS-22123P | PLC | 粒料添加剂排气风机18-PB-2203X电机停止控制 | 1830-PS07-221 | MCC | 18-PB-2203X主电机 | PLC-DO | - | - | C01
- | 18-HS-22123L | PLC | 粒料添加剂排气风机18-PB-2203X电机自动(远程)状态 | 1830-PS07-221 | MCC | 18-PB-2203X主电机 | PLC-DI | - | - | C01
- | 18-YL-22123R | PLC | 粒料添加剂排气风机18-PB-2203X电机运行状态 | 1830-PS07-221 | MCC | 18-PB-2203X主电机 | PLC-DI | - | - | C01
- | 18-YL-22123F | PLC | 粒料添加剂排气风机18-PB-2203X电机故障状态 | 1830-PS07-221 | MCC | 18-PB-2203X主电机 | PLC-DI | - | - | C01
- | 18-HS-22122S | PLC | 粒料添加剂排气过滤器18-FL-2203X振动电机启动控制 | 1830-PS07-221 | MCC | 18-FL-2203X主电机 | PLC-DO | - | -
- | 18-HS-22122P | PLC | 粒料添加剂排气过滤器18-FL-2203X振动电机停止控制 | 1830-PS07-221 | MCC | 18-FL-2203X主电机 | PLC-DO | - | -
- | 18-HS-22122L | PLC | 粒料添加剂排气过滤器18-FL-2203X振动电机自动(远 程)状态 | 1830-PS07-221 | MCC | 18-FL-2203X主电机 | PLC-DI | - | -
- | 18-YL-22122R | PLC | 粒料添加剂排气过滤器18-FL-2203X振动电机运行状态 | 1830-PS07-221 | MCC | 18-FL-2203X主电机 | PLC-DI | - | -
- | 18-YL-22122F | PLC | 粒料添加剂排气过滤器18-FL-2203X振动电机故障状态 | 1830-PS07-221 | MCC | 18-FL-2203X主电机 | PLC-DI | - | -
- | 18-HS-22121AL | PLC | 气动滑板阀18-XV-22121自动(远程)模式 | 1830-PS07-221 | Field | 18-LP-2203 | PLC-DI | - | - | C01
- | 18-HS-22121A | PLC | 手动控制气动滑板阀18-XV-22121的开/关 | 1830-PS07-221 | Field | 18-LP-2203 | PLC-DI | - | - | C01
- | 18-XZH-22121A | PLC | 气动滑板阀18-XV-22121开状态现场指示 | 1830-PS07-221 | Field | 18-LP-2203 | PLC-DO | - | - | C01
- | 18-XZL-22121A | PLC | 气动滑板阀18-XV-22121关状态现场指示 | 1830-PS07-221 | Field | 18-LP-2203 | PLC-DO | - | - | C01
- | 18-PDAH-22121A | PLC | 粒料添加剂排气过滤器18-FL-2203X差压高报现场指示 | 1830-PS07-221 | Field | 18-LP-2203 | PLC-DO | - | - | C01
- | 18-LAH-22301A2 | PLC | 粒料添加剂储存料斗18-VH-2205高料位现场指示 | 1830-PS07-223 | Field | 18-LP-2203 | PLC-DO | - | - | C01
- | 18-ZS-22121 | PLC | 袋装粒料添加剂料斗18-VH-2203X门限关状态检测 | 1830-PS07-221 | Field | 18-VH-2203X | PLC-DI | - | - | C01
- | 18-PDT-22121 | PLC | 粒料添加剂排气过滤器18-FL-2203X差压变送器 | 1830-PS07-221 | Field | 18-FL-2203X | PLC-AI | - | - | C01
- | 18-XYX-22121 | PLC | 气动滑板阀18-XV-22121 开/关电磁阀 | 1830-PS07-221 | Field | 18-XV-22121 | PLC-DO | - | - | C01
- | 18-XZSH-22121 | PLC | 气动滑板阀18-XV-22121 开状态监测 | 1830-PS07-221 | Field | 18-XV-22121 | PLC-DI | - | - | C01
- | 18-XZSL-22121 | PLC | 气动滑板阀18-XV-22121 关状态监测 | 1830-PS07-221 | Field | 18-XV-22121 | PLC-DI | - | - | C01
- | 18-HS-22223S | PLC | 粒料添加剂排气风机18-PB-2201AX电机启动控制 | 1830-PS07-222 | MCC | 18-PB-2201AX推气风机 | PLC-DO | - | - | C01
- | 18-HS-22223P | PLC | 粒料添加剂排气风机18-PB-2201AX电机停止控制 | 1830-PS07-222 | MCC | 18-PB-2201AX推气风机 | PLC-DO | - | - | C01
- | 18-HS-22223L | PLC | 粒料添加剂排气风机18-PB-2201AX电机自动(远程)状态 | 1830-PS07-222 | MCC | 18-PB-2201AX推气风机 | PLC-DI | - | - | C01
- | 18-YL-22223R | PLC | 粒料添加剂排气风机18-PB-2201AX电机运行状态 | 1830-PS07-222 | MCC | 18-PB-2201AX推气风机 | PLC-DI | - | - | C01
- | 18-YL-22223F | PLC | 粒料添加剂排气风机18-PB-2201AX电机故障状态 | 1830-PS07-222 | MCC | 18-PB-2201AX推气风机 | PLC-DI | - | - | C01
- | 18-HS-22222S | PLC | 粒料添加剂排气过滤器18-FL-2201AX振动电机启动控制 | 1830-PS07-222 | MCC | 18-FL-2201AX振动电机 | PLC-DO | - | - | C01
- | 18-HS-22222P | PLC | 粒料添加剂排气过滤器18-FL-2201AX振动电机停止控制 | 1830-PS07-222 | MCC | 18-FL-2201AX振动电机 | PLC-DO | - | - | C01
- | 18-HS-22222L | PLC | 粒料添加剂排气过滤器18-FL-2201AX振动电机自动(远 程)状态 | 1830-PS07-222 | MCC | 18-FL-2201AX振动电机 | PLC-DI | - | - | C01
- | 18-YL-22222R | PLC | 粒料添加剂排气过滤器18-FL-2201AX振动电机运行状态 | 1830-PS07-222 | MCC | 18-FL-2201AX振动电机 | PLC-DI | - | - | C01
- | 18-YL-22222F | PLC | 粒料添加剂排气过滤器18-FL-2201AX振动电机故障状态 | 1830-PS07-222 | MCC | 18-FL-2201AX振动电机 | PLC-DI | - | - | C01
- | 18-HS-22221AL | PLC | 气动滑板阀18-XV-22221自动(远程)模式 | 1830-PS07-222 | Field | 18-LP-2201AX | PLC-DI | - | - | C01
- | 18-HS-22221A | PLC | 手动控制气动滑板阀18-XV-22221的开/关 | 1830-PS07-222 | Field | 18-LP-2201AX | PLC-DI | - | - | C01
- | 18-XZH-22221A | PLC | 气动滑板阀18-XV-22221开状态现场指示 | 1830-PS07-222 | Field | 18-LP-2201AX | PLC-DO | - | - | C01
- | 18-XZL-22221A | PLC | 气动滑板阀18-XV-22221关状态现场指示 | 1830-PS07-222 | Field | 18-LP-2201AX | PLC-DO | - | - | C01
- | 18-PDAH-22221A | PLC | 粒料添加剂排气过滤器18-FL-2201AX差压高报现场指示 | 1830-PS07-222 | Field | 18-LP-2201AX | PLC-DO | - | - | C01
- | 18-LAH-22401A | PLC | 添加剂储存料斗18-VH-2202AX高料位现场指示 | 1830-PS07-224 | Field | 18-LP-2201AX | PLC-DO | - | - | C01
- | 18-ZS-22221 | PLC | 袋装粒料添加剂料斗18-VH-2201AX门限关状态检测 | 1830-PS07-222 | Field | 18-VH-2201AX | PLC-DI | - | - | C01
- | 18-PDT-22221 | PLC | 粒料添加剂排气过滤器18-FL-2201AX差压变送器 | 1830-PS07-221 | Field | 18-FL-2201AX | PLC-AI | - | - | C01
- | 18-XYX-22221 | PLC | 气动滑板阀18-XV-22221 开/关电磁阀 | 1830-PS07-221 | Field | 18-XV-22221 | PLC-DO | - | - | C01
- | 18-XZSH-22221 | PLC | 气动滑板阀18-XV-22221 开状态监测 | 1830-PS07-221 | Field | 18-XV-22221 | PLC-DI | - | - | C01
- | 18-XZSL-22221 | PLC | 气动滑板阀18-XV-22221 关状态监测 | 1830-PS07-221 | Field | 18-XV-22221 | PLC-DI | - | - | C01
- | 18-HS-22233S | PLC | 粒料添加剂排气风机18-PB-2201BX电机启动控制 | 1830-PS07-222 | MCC | 18-PB-2201BX推气风机 | PLC-DO | - | - | C01
- | 18-HS-22233P | PLC | 粒料添加剂排气风机18-PB-2201BX电机停止控制 | 1830-PS07-222 | MCC | 18-PB-2201BX推气风机 | PLC-DO | - | - | C01
- | 18-HS-22233L | PLC | 粒料添加剂排气风机18-PB-2201BX电机自动(远程)状态 | 1830-PS07-222 | MCC | 18-PB-2201BX推气风机 | PLC-DI | - | - | C01
- | 18-YL-22233R | PLC | 粒料添加剂排气风机18-PB-2201BX电机运行状态 | 1830-PS07-222 | MCC | 18-PB-2201BX推气风机 | PLC-DI | - | - | C01
- | 18-YL-22233F | PLC | 粒料添加剂排气风机18-PB-2201BX电机故障状态 | 1830-PS07-222 | MCC | 18-PB-2201BX推气风机 | PLC-DI | - | - | C01
- | 18-HS-22322S | PLC | 粒料添加剂排气过滤器18-FL-2201BX振动电机启动控制 | 1830-PS07-222 | MCC | 18-FL-2201BX振动电机 | PLC-DO | - | - | C01
- | 18-HS-22322P | PLC | 粒料添加剂排气过滤器18-FL-2201BX振动电机停止控制 | 1830-PS07-222 | MCC | 18-FL-2201BX振动电机 | PLC-DO | - | - | C01
- | 18-HS-22322L | PLC | 粒料添加剂排气过滤器18-FL-2201BX振动电机自动(远程)状态 | 1830-PS07-222 | MCC | 18-FL-2201BX振动电机 | PLC-DI | - | - | C01
- | 18-YL-22322R | PLC | 粒料添加剂排气过滤器18-FL-2201BX振动电机运行状态 | 1830-PS07-222 | MCC | 18-FL-2201BX振动电机 | PLC-DI | - | - | C01
- | 18-YL-22322F | PLC | 粒料添加剂排气过滤器18-FL-2201BX振动电机故障状态 | 1830-PS07-222 | MCC | 18-FL-2201BX振动电机 | PLC-DI | - | - | C01
- | 18-HS-22231AL | PLC | 气动滑板阀18-XV-22231自动(远程)模式 | 1830-PS07-222 | Field | 18-LP-2201BX | PLC-DI | - | - | C01
- | 18-HS-22231A | PLC | 手动控制气动滑板阀18-XV-22231的开/关 | 1830-PS07-222 | Field | 18-LP-2201BX | PLC-DI | - | - | C01
- | 18-XZH-22231A | PLC | 气动滑板阀18-XV-22231开状态现场指示 | 1830-PS07-222 | Field | 18-LP-2201BX | PLC-DO | - | - | C01
- | 18-XZL-22231A | PLC | 气动滑板阀18-XV-22231关状态现场指示 | 1830-PS07-222 | Field | 18-LP-2201BX | PLC-DO | - | - | C01
- | 18-PDAH-22231A | PLC | 粒料添加剂排气过滤器18-FL-2201BX差压高报现场指示 | 1830-PS07-222 | Field | 18-LP-2201BX | PLC-DO | - | - | C01
- | 18-LAH-22411A | PLC | 添加剂储存料斗18-VH-2202BX高料位现场指示 | 1830-PS07-224 | Field | 18-LP-2201BX | PLC-DO | - | - | C01
- | 18-ZS-22231 | PLC | 袋装粒料添加剂料斗18-VH-2201BX门限关状态检测 | 1830-PS07-222 | Field | 18-VH-2201BX | PLC-DI | - | - | C01
- | 18-PDT-22231 | PLC | 粒料添加剂排气过滤器18-FL-2201BX差压变送器 | 1830-PS07-222 | Field | 18-FL-2201BX | PLC-AI | - | - | C01
- | 18-XYX-22231 | PLC | 气动滑板阀18-XV-22231 开/关电磁阀 | 1830-PS07-222 | Field | 18-XV-22231 | PLC-DO | - | - | C01
- | 18-XZSH-22231 | PLC | 气动滑板阀18-XV-22231 开状态监测 | 1830-PS07-222 | Field | 18-XV-22231 | PLC-DI | - | - | C01
- | 18-XZSL-22231 | PLC | 气动滑板阀18-XV-22231 关状态监测 | 1830-PS07-222 | Field | 18-XV-22231 | PLC-DI | - | - | C01
- | 18-XYX-22301 | PLC | 气动滑板阀18-XV-22301 开/关电磁阀 | 1830-PS07-223 | Field | 18-XV-22301 | PLC-DO | - | - | C01
- | 18-XZSH-22301 | PLC | 气动滑板阀18-XV-22301 开状态监测 | 1830-PS07-223 | Field | 18-XV-22301 | PLC-DI | - | - | C01
- | 18-XZSL-22301 | PLC | 气动滑板阀18-XV-22301 关状态监测 | 1830-PS07-223 | Field | 18-XV-22301 | PLC-DI | - | - | C01
- | 18-HS-22301AL | PLC | 粒料添加剂储存料斗18-VH-2205出口滑板阀自动(远 程)模式 | 1830-PS07-223 | Field | 18-LP-22301A | PLC-DI | - | - | C01
- | 18-HS-22301A | PLC | 粒料添加剂储存料斗18-VH-2205出口滑板阀手动控制 | 1830-PS07-223 | Field | 18-LP-22301A | PLC-DI | - | - | C01
- | 18-XYX-22302 | PLC | 气动滑板阀18-XV-22302 开/关电磁阀 | 1830-PS07-223 | Field | 18-XV-22302 | PLC-DO | - | - | C01
- | 18-XZSH-22302 | PLC | 气动滑板阀18-XV-22302 开状态监测 | 1830-PS07-223 | Field | 18-XV-22302 | PLC-DI | - | - | C01
- | 18-XZSL-22302 | PLC | 气动滑板阀18-XV-22302 关状态监测 | 1830-PS07-223 | Field | 18-XV-22302 | PLC-DI | - | - | C01
- | 18-HS-22305S | PLC | 粒料添加剂失重秤18-PF-2205排气过滤器振动电机启动控制 | 1830-PS07-223 | MCC | 18-PF-2205振动电机 | PLC-DO | - | - | C01
- | 18-HS-22305P | PLC | 粒料添加剂失重秤18-PF-2205排气过滤器振动电机停止控制 | 1830-PS07-223 | MCC | 18-PF-2205振动电机 | PLC-DO | - | - | C01
- | 18-HS-22305L | PLC | 粒料添加剂失重秤18-PF-2205排气过滤器振动电机自动(远程)状态 | 1830-PS07-223 | MCC | 18-PF-2205振动电机 | PLC-DI | - | - | C01
- | 18-YL-22305R | PLC | 粒料添加剂失重秤18-PF-2205排气过滤器振动电机运行状态 | 1830-PS07-223 | MCC | 18-PF-2205振动电机 | PLC-DI | - | - | C01
- | 18-YL-22305F | PLC | 粒料添加剂失重秤18-PF-2205排气过滤器振动电机故障状态 | 1830-PS07-223 | MCC | 18-PF-2205振动电机 | PLC-DI | - | - | C01
- | 18-HS-22304S | PLC | 粒料添加剂失重秤18-PF-2205搅拌器电机启动控制 | 1830-PS07-223 | MCC | 18-PF-2205搅拌电机 | PLC-DO | - | - | C01
- | 18-HS-22304P | PLC | 粒料添加剂失重秤18-PF-2205搅拌器电机停止控制 | 1830-PS07-223 | MCC | 18-PF-2205搅拌电机 | PLC-DO | - | - | C01
- | 18-HS-22304L | PLC | 粒料添加剂失重秤18-PF-2205搅拌器电机自动(远程)状态 | 1830-PS07-223 | MCC | 18-PF-2205搅拌电机 | PLC-DI | - | - | C01
- | 18-YL-22304R | PLC | 粒料添加剂失重秤18-PF-2205搅拌器电机运行状态 | 1830-PS07-223 | MCC | 18-PF-2205搅拌电机 | PLC-DI | - | - | C01
- | 18-YL-22304F | PLC | 粒料添加剂失重秤18-PF-2205搅拌器电机故障状态 | 1830-PS07-223 | MCC | 18-PF-2205搅拌电机 | PLC-DI | - | - | C01
- | 18-FFIC-22301 | PLC | 粒料添加剂失重秤18-PF-2205流量设定 | 1830-PS07-223 | Field | 18-PF-2205失重称 | PLC-AO | - | - | C01
- | 18-WAL-22301 | PLC | 粒料添加剂失重秤18-PF-2205低料位补料信号 | 1830-PS07-223 | Field | 18-PF-2205失重称 | PLC-DI | - | - | C01
- | 18-HS-22301S | PLC | 粒料添加剂失重秤18-PF-2205启动控制 | 1830-PS07-223 | Field | 18-PF-2205失重称 | PLC-DO | - | - | C01
- | 18-HS-22301P | PLC | 粒料添加剂失重秤18-PF-2205停止控制 | 1830-PS07-223 | Field | 18-PF-2205失重称 | PLC-DO | - | - | C01
- | 18-HSFR-22301 | PLC | 粒料添加剂失重秤18-PF-2205正反转控制 | 1830-PS07-223 | MCC | 18-PF-2205失重称 | PLC-DO | - | - | C01
- | 18-YL-22301R | PLC | 粒料添加剂失重秤18-PF-2205电机运行状态 | 1830-PS07-223 | MCC | 18-PF-2205失重称 | PLC-DI | - | - | C01
- | 18-YL-22301F | PLC | 粒料添加剂失重秤18-PF-2205电机故障状态 | 1830-PS07-223 | MCC | 18-PF-2205失重称 | PLC-DI | - | - | C01
- | 18-HS-22301L | PLC | 粒料添加剂失重秤18-PF-2205自动(远程)状态 | 1830-PS07-223 | Field | 18-LP-PF2205 | PLC-DI | - | - | C01
- | 18-HS-22301 | PLC | 粒料添加剂失重秤18-PF-2205就地启动 | 1830-PS07-223 | Field | 18-LP-PF2205 | PLC-DI | - | - | C01
- | 18-HS-22401 | PLC | 就地启动添加剂储存料斗18-VH-2202AX搅拌装置 | 1830-PS07-224 | Field | 18-LP-VH2202AX | PLC-DI | - | - | C01
- | 18-XL-22405 | PLC | 添加剂储存料斗18-VH-2202AX搅拌装置正在运行指示 | 1830-PS07-224 | Field | 18-LP-VH2202AX | PLC-DO | - | - | C01
- | 18-HS-22409 | PLC | 就地停止添加剂储存料斗18-VH-2202AX搅拌装置 | 1830-PS07-224 | Field | 18-LP-VH2202AX | PLC-DI | - | - | C01
- | 18-XL-22406 | PLC | 添加剂储存料斗18-VH-2202AX搅拌装置搅拌结束指示 | 1830-PS07-224 | Field | 18-LP-VH2202AX | PLC-DO | - | - | C01
- | 18-HS-22402 | PLC | 就地启动添加剂储存料斗18-VH-2202AX出料 | 1830-PS07-224 | Field | 18-LP-VH2202AX | PLC-DI | - | - | C01
- | 18-XL-22407 | PLC | 添加剂储存料斗18-VH-2202AX正在出料指示 | 1830-PS07-224 | Field | 18-LP-VH2202AX | PLC-DO | - | - | C01
- | 18-HS-22403 | PLC | 就地停止添加剂储存料斗18-VH-2202AX出料 | 1830-PS07-224 | Field | 18-LP-VH2202AX | PLC-DI | - | - | C01
- | 18-XL-22408 | PLC | 添加剂储存料斗18-VH-2202AX出料准备就绪指示 | 1830-PS07-224 | Field | 18-LP-VH2202AX | PLC-DO | - | - | C01
- | 18-XL-22410 | PLC | 允许添加剂储存料斗18-VH-2202AX搅拌装置就地控制 箱操作 | 1830-PS07-224 | Field | 18-LP-VH2202AX | PLC-DO | - | - | C01
- | 18-HSF-22401S | PLC | 添加剂搅拌器18-PA-2202AX电机高速启动控制 | 1830-PS07-224 | MCC | 18-PA-2202AX主电机 | PLC-DO | - | - | C01
- | 18-HSS-22401S | PLC | 添加剂搅拌器18-PA-2202AX电机低速启动控制 | 1830-PS07-224 | MCC | 18-PA-2202AX主电机 | PLC-DO | - | - | C01
- | 18-HS-22401P | PLC | 添加剂搅拌器18-PA-2202AX电机停止控制 | 1830-PS07-224 | MCC | 18-PA-2202AX主电机 | PLC-DO | - | - | C01
- | 18-HS-22401L | PLC | 添加剂搅拌器18-PA-2202AX电机自动(远程)状态 | 1830-PS07-224 | MCC | 18-PA-2202AX主电机 | PLC-DI | - | - | C01
- | 18-YLH-22401R | PLC | 添加剂搅拌器18-PA-2202AX电机高速运行状态 | 1830-PS07-224 | MCC | 18-PA-2202AX主电机 | PLC-DI | - | - | C01
- | 18-YLS-22401R | PLC | 添加剂搅拌器18-PA-2202AX电机低速运行状态 | 1830-PS07-224 | MCC | 18-PA-2202AX主电机 | PLC-DI | - | - | C01
- | 18-YL-22401F | PLC | 添加剂搅拌器18-PA-2202AX电机故障状态 | 1830-PS07-224 | MCC | 18-PA-2202AX主电机 | PLC-DI | - | - | C01
- | 18-ZSL-22401 | PLC | 添加剂储存料斗18-VH-2202AX人孔开状态检测 | 1830-PS07-224 | Field | 18-VH-2202AX | PLC-DI | - | 2线制,Namur,8VDC | C01
- | 18-LSH-22401 | PLC | 添加剂储存料斗18-VH-2202AX高料位检测 | 1830-PS07-224 | Field | 18-VH-2202AX | PLC-DI | - | 3线制，直流PNP 触点 | C01
- | 18-LSL-22402 | PLC | 添加剂储存料斗18-VH-2202AX低料位检测 | 1830-PS07-224 | Field | 18-VH-2202AX | PLC-DI | - | 3线制，直流PNP 触点 | C01
- | 18-LSL-22402A | PLC | 添加剂储存料斗18-VH-2202AX低料位联锁 | 1830-PS07-224 | Field | 18-VH-2202AX | PLC-DO | - | - | C01
- | 18-XYX-22401 | PLC | 气动滑板阀18-XV-22401 开/关电磁阀 | 1830-PS07-224 | Field | 18-XV-22401 | PLC-DO | - | - | C01
- | 18-XZSH-22401 | PLC | 气动滑板阀18-XV-22401 开状态监测 | 1830-PS07-224 | Field | 18-XV-22401 | PLC-DI | - | - | C01
- | 18-XZSL-22401 | PLC | 气动滑板阀18-XV-22401 关状态监测 | 1830-PS07-224 | Field | 18-XV-22401 | PLC-DI | - | - | C01
- | 18-HS-22401AL | PLC | 添加剂储存料斗18-VH-2202AX出口滑板阀自动(远程)模式 | 1830-PS07-224 | Field | 18-LP-22401A | PLC-DI | - | 安装在18-LP- 22301A | C01
- | 18-HS-22401A | PLC | 添加剂储存料斗18-VH-2202AX出口滑板阀手动控制 | 1830-PS07-224 | Field | 18-LP-22401A | PLC-DI | - | 安装在18-LP- 22301A | C01
- | 18-XYX-22402 | PLC | 气动滑板阀18-XV-22402 开/关电磁阀 | 1830-PS07-224 | Field | 18-XV-22402 | PLC-DO | - | - | C01
- | 18-XZSH-22402 | PLC | 气动滑板阀18-XV-22402 开状态监测 | 1830-PS07-224 | Field | 18-XV-22402 | PLC-DI | - | - | C01
- | 18-XZSL-22402 | PLC | 气动滑板阀18-XV-22402 关状态监测 | 1830-PS07-224 | Field | 18-XV-22402 | PLC-DI | - | - | C01
- | 18-HS-22426S | PLC | 添加剂失重秤18-PF-2201A排气过滤器振动电机启动控制 | 1830-PS07-224 | MCC | 18-PF-2201A排气过滤器振动主电机 | PLC-DO | - | - | C01
- | 18-HS-22426P | PLC | 添加剂失重秤18-PF-2201A排气过滤器振动电机停止控制 | 1830-PS07-224 | MCC | 18-PF-2201A排气过滤器振动主电机 | PLC-DO | - | - | C01
- | 18-HS-22426L | PLC | 添加剂失重秤18-PF-2201A排气过滤器振动电机自动(远程)状态 | 1830-PS07-224 | MCC | 18-PF-2201A排气过滤器振动主电机 | PLC-DI | - | - | C01
- | 18-YL-22426R | PLC | 添加剂失重秤18-PF-2201A排气过滤器振动电机运行状态 | 1830-PS07-224 | MCC | 18-PF-2201A排气过滤器振动主电机 | PLC-DI | - | - | C01
- | 18-YL-22426F | PLC | 添加剂失重秤18-PF-2201A排气过滤器振动电机故障状态 | 1830-PS07-224 | MCC | 18-PF-2201A排气过滤器振动主电机 | PLC-DI | - | - | C01
- | 18-HS-22425S | PLC | 添加剂失重秤18-PF-2201A搅拌器电机启动控制 | 1830-PS07-224 | MCC | 18-PF-2201A搅拌器主电机 | PLC-DO | - | - | C01
- | 18-HS-22425P | PLC | 添加剂失重秤18-PF-2201A搅拌器电机停止控制 | 1830-PS07-224 | MCC | 18-PF-2201A搅拌器主电机 | PLC-DO | - | - | C01
- | 18-HS-22425L | PLC | 添加剂失重秤18-PF-2201A搅拌器电机自动(远程)状态 | 1830-PS07-224 | MCC | 18-PF-2201A搅拌器主电机 | PLC-DI | - | - | C01
- | 18-YL-22425R | PLC | 添加剂失重秤18-PF-2201A搅拌器电机运行状态 | 1830-PS07-224 | MCC | 18-PF-2201A搅拌器主电机 | PLC-DI | - | - | C01
- | 18-YL-22425F | PLC | 添加剂失重秤18-PF-2201A搅拌器电机故障状态 | 1830-PS07-224 | MCC | 18-PF-2201A搅拌器主电机 | PLC-DI | - | - | C01
- | 18-FFIC-22403 | PLC | 添加剂失重秤18-PF-2201A流量设定 | 1830-PS07-224 | Field | 18-PF-2201A失重称 | PLC-AO | - | - | C01
- | 18-WAL-22403 | PLC | 添加剂失重秤18-PF-2201A低料位补料信号 | 1830-PS07-224 | Field | 18-PF-2201A失重称 | PLC-DI | - | - | C01
- | 18-HS-22403S | PLC | 添加剂失重秤18-PF-2201A启动控制 | 1830-PS07-224 | Field | 18-PF-2201A失重称 | PLC-DO | - | - | C01
- | 18-HS-22403P | PLC | 添加剂失重秤18-PF-2201A停止控制 | 1830-PS07-224 | Field | 18-PF-2201A失重称 | PLC-DO | - | - | C01
- | 18-HSFR-22403 | PLC | 添加剂失重秤18-PF-2201A正反转控制 | 1830-PS07-224 | MCC | 18-PF-2201A失重称 | PLC-DO | - | - | C01
- | 18-YL-22403R | PLC | 添加剂失重秤18-PF-2201A电机运行状态 | 1830-PS07-224 | MCC | 18-PF-2201A失重称 | PLC-DI | - | - | C01
- | 18-YL-22403F | PLC | 添加剂失重秤18-PF-2201A电机故障状态 | 1830-PS07-224 | MCC | 18-PF-2201A失重称 | PLC-DI | - | - | C01
- | 18-HS-22403L | PLC | 粒料添加剂失重秤18-PF-2201A自动(远程)状态 | 1830-PS07-224 | Field | 18-LP-PF2201A/B | PLC-DI | - | - | C01
- | 18-HS-22403 | PLC | 粒料添加剂失重秤18-PF-2201A就地启动 | 1830-PS07-224 | Field | 18-LP-PF2201A/B | PLC-DI | - | - | C01
- | 18-HS-22411 | PLC | 就地启动添加剂储存料斗18-VH-2202BX搅拌装置 | 1830-PS07-224 | Field | 18-LP-VH2202BX | PLC-DI | - | - | C01
- | 18-XL-22415 | PLC | 添加剂储存料斗18-VH-2202BX搅拌装置正在运行指示 | 1830-PS07-224 | Field | 18-LP-VH2202BX | PLC-DO | - | - | C01
- | 18-HS-22419 | PLC | 就地停止添加剂储存料斗18-VH-2202BX搅拌装置 | 1830-PS07-224 | Field | 18-LP-VH2202BX | PLC-DI | - | - | C01
- | 18-XL-22416 | PLC | 添加剂储存料斗18-VH-2202BX搅拌装置搅拌结束指示 | 1830-PS07-224 | Field | 18-LP-VH2202BX | PLC-DO | - | - | C01
- | 18-HS-22412 | PLC | 就地启动添加剂储存料斗18-VH-2202BX出料 | 1830-PS07-224 | Field | 18-LP-VH2202BX | PLC-DI | - | - | C01
- | 18-XL-22417 | PLC | 添加剂储存料斗18-VH-2202BX正在出料指示 | 1830-PS07-224 | Field | 18-LP-VH2202BX | PLC-DO | - | - | C01
- | 18-HS-22413 | PLC | 就地停止添加剂储存料斗18-VH-2202BX出料 | 1830-PS07-224 | Field | 18-LP-VH2202BX | PLC-DI | - | - | C01
- | 18-XL-22418 | PLC | 添加剂储存料斗18-VH-2202BX出料准备就绪指示 | 1830-PS07-224 | Field | 18-LP-VH2202BX | PLC-DO | - | - | C01
- | 18-XL-22420 | PLC | 允许添加剂储存料斗18-VH-2202BX搅拌装置就地控制 箱操作 | 1830-PS07-224 | Field | 18-LP-VH2202BX | PLC-DO | - | - | C01
- | 18-HSF-22411S | PLC | 添加剂搅拌器18-PA-2202BX电机高速启动控制 | 1830-PS07-224 | MCC | 18-PA-2202BX主电机 | PLC-DO | - | - | C01
- | 18-HSS-22411S | PLC | 添加剂搅拌器18-PA-2202BX电机低速启动控制 | 1830-PS07-224 | MCC | 18-PA-2202BX主电机 | PLC-DO | - | - | C01
- | 18-HS-22411P | PLC | 添加剂搅拌器18-PA-2202BX电机停止控制 | 1830-PS07-224 | MCC | 18-PA-2202BX主电机 | PLC-DO | - | - | C01
- | 18-HS-22411L | PLC | 添加剂搅拌器18-PA-2202BX电机自动(远程)状态 | 1830-PS07-224 | MCC | 18-PA-2202BX主电机 | PLC-DI | - | - | C01
- | 18-YLH-22411R | PLC | 添加剂搅拌器18-PA-2202BX电机高速运行状态 | 1830-PS07-224 | MCC | 18-PA-2202BX主电机 | PLC-DI | - | - | C01
- | 18-YLS-22411R | PLC | 添加剂搅拌器18-PA-2202BX电机低速运行状态 | 1830-PS07-224 | MCC | 18-PA-2202BX主电机 | PLC-DI | - | - | C01
- | 18-YL-22411F | PLC | 添加剂搅拌器18-PA-2202BX电机故障状态 | 1830-PS07-224 | MCC | 18-PA-2202BX主电机 | PLC-DI | - | - | C01
- | 18-ZSL-22411 | PLC | 添加剂储存料斗18-VH-2202BX人孔开状态检测 | 1830-PS07-224 | Field | 18-VH-2202BX | PLC-DI | - | 2线 制,Namur,8VDC | C01
- | 18-LSH-22411 | PLC | 添加剂储存料斗18-VH-2202BX高料位检测 | 1830-PS07-224 | Field | 18-VH-2202BX | PLC-DI | - | 3线制，直流PNP 触点 | C01
- | 18-LSL-22412 | PLC | 添加剂储存料斗18-VH-2202BX低料位检测 | 1830-PS07-224 | Field | 18-VH-2202BX | PLC-DI | - | 3线制，直流PNP 触点 | C01
- | 18-LSL-22412A | PLC | 添加剂储存料斗18-VH-2202BX低料位联锁 | 1830-PS07-224 | Field | 18-VH-2202BX | PLC-DO | - | - | C01
- | 18-XYX-22411 | PLC | 气动滑板阀18-XV-22411 开/关电磁阀 | 1830-PS07-224 | Field | 18-XV-22411 | PLC-DO | - | - | C01
- | 18-XZSH-22411 | PLC | 气动滑板阀18-XV-22411 开状态监测 | 1830-PS07-224 | Field | 18-XV-22411 | PLC-DI | - | - | C01
- | 18-XZSL-22411 | PLC | 气动滑板阀18-XV-22411 关状态监测 | 1830-PS07-224 | Field | 18-XV-22411 | PLC-DI | - | - | C01
- | 18-HS-22411AL | PLC | 添加剂储存料斗18-VH-2202BX出口滑板阀自动(远程)模式 | 1830-PS07-224 | Field | 18-LP- 22301A | PLC-DI | - | 安装在18-LP- 22301A | C01
- | 18-HS-22411A | PLC | 添加剂储存料斗18-VH-2202BX出口滑板阀手动控制 | 1830-PS07-224 | Field | 18-LP- 22301A | PLC-DI | - | 安装在18-LP- 22301A | C01
- | 18-XYX-22412 | PLC | 气动滑板阀18-XV-22412 开/关电磁阀 | 1830-PS07-224 | Field | 18-XV-22412 | PLC-DO | - | - | C01
- | 18-XZSH-22412 | PLC | 气动滑板阀18-XV-22412 开状态监测 | 1830-PS07-224 | Field | 18-XV-22412 | PLC-DI | - | - | C01
- | 18-XZSL-22412 | PLC | 气动滑板阀18-XV-22412 关状态监测 | 1830-PS07-224 | Field | 18-XV-22412 | PLC-DI | - | - | C01
- | 18-HS-22436S | PLC | 添加剂失重秤18-PF-2201B排气过滤器振动电机启动控制 | 1830-PS07-224 | MCC | 18-PF-2201B排气过滤器振动主电机 | PLC-DO | - | - | C01
- | 18-HS-22436P | PLC | 添加剂失重秤18-PF-2201B排气过滤器振动电机停止控制 | 1830-PS07-224 | MCC | 18-PF-2201B排气过滤器振动主电机 | PLC-DO | - | - | C01
- | 18-HS-22436L | PLC | 添加剂失重秤18-PF-2201B排气过滤器振动电机自动(远程)状态 | 1830-PS07-224 | MCC | 18-PF-2201B排气过滤器振动主电机 | PLC-DI | - | - | C01
- | 18-YL-22436R | PLC | 添加剂失重秤18-PF-2201B排气过滤器振动电机运行状态 | 1830-PS07-224 | MCC | 18-PF-2201B排气过滤器振动主电机 | PLC-DI | - | - | C01
- | 18-YL-22436F | PLC | 添加剂失重秤18-PF-2201B排气过滤器振动电机故障状态 | 1830-PS07-224 | MCC | 18-PF-2201B排气过滤器振动主电机 | PLC-DI | - | - | C01
- | 18-HS-22435S | PLC | 添加剂失重秤18-PF-2201B搅拌器电机启动控制 | 1830-PS07-224 | MCC | 18-PF-2201B搅拌器主电机 | PLC-DO | - | - | C01
- | 18-HS-22435P | PLC | 添加剂失重秤18-PF-2201B搅拌器电机停止控制 | 1830-PS07-224 | MCC | 18-PF-2201B搅拌器主电机 | PLC-DO | - | - | C01
- | 18-HS-22435L | PLC | 添加剂失重秤18-PF-2201B搅拌器电机自动(远程)状态 | 1830-PS07-224 | MCC | 18-PF-2201B搅拌器主电机 | PLC-DI | - | - | C01
- | 18-YL-22435R | PLC | 添加剂失重秤18-PF-2201B搅拌器电机运行状态 | 1830-PS07-224 | MCC | 18-PF-2201B搅拌器主电机 | PLC-DI | - | - | C01
- | 18-YL-22435F | PLC | 添加剂失重秤18-PF-2201B搅拌器电机故障状态 | 1830-PS07-224 | MCC | 18-PF-2201B搅拌器主电机 | PLC-DI | - | - | C01
- | 18-FFIC-22413 | PLC | 添加剂失重秤18-PF-2201B流量设定 | 1830-PS07-224 | Field | 18-PF-2201B失重称 | PLC-AO | - | - | C01
- | 18-WAL-22413 | PLC | 添加剂失重秤18-PF-2201B低料位补料信号 | 1830-PS07-224 | Field | 18-PF-2201B失重称 | PLC-DI | - | - | C01
- | 18-HS-22413S | PLC | 添加剂失重秤18-PF-2201B启动控制 | 1830-PS07-224 | Field | 18-PF-2201B失重称 | PLC-DO | - | - | C01
- | 18-HS-22413P | PLC | 添加剂失重秤18-PF-2201B停止控制 | 1830-PS07-224 | Field | 18-PF-2201B失重称 | PLC-DO | - | - | C01
- | 18-HSFR-22413 | PLC | 添加剂失重秤18-PF-2201B正反转控制 | 1830-PS07-224 | MCC | 18-PF-2201B失重称 | PLC-DO | - | - | C01
- | 18-YL-22413R | PLC | 添加剂失重秤18-PF-2201B电机运行状态 | 1830-PS07-224 | MCC | 18-PF-2201B失重称 | PLC-DI | - | - | C01
- | 18-YL-22413F | PLC | 添加剂失重秤18-PF-2201B电机故障状态 | 1830-PS07-224 | MCC | 18-PF-2201B失重称 | PLC-DI | - | - | C01
- | 18-HS-22413L | PLC | 粒料添加剂失重秤18-PF-2201B自动(远程)状态 | 1830-PS07-224 | Field | 18-LP-PF2201A/B | PLC-DI | - | - | C01
- | 18-HS-22413 | PLC | 粒料添加剂失重秤18-PF-2201B就地启动 | 1830-PS07-224 | Field | 18-LP-PF2201A/B | PLC-DI | - | - | C01
- | 18-FI-36101A | PLC | 主粉料计量秤18-PF-3601粉料流量显示 | 1830-PS07-361 | Field | 18-PF-3601主粉料计量秤 | PLC-AI | - | 同时送至DCS和SIS | C01
- | 18-FI-36101B | PLC | 主粉料计量秤18-PF-3601流量设定 | 1830-PS07-361 | Field | 18-PF-3601主粉料计量秤 | PLC-AO | - | - | C01
- | 18-HSFR-35101 | PLC | 粉料仓旋转加料器18-PF-3501X正反转控制 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-DO | - | - | C01
- | 18-HS-35101S | PLC | 粉料仓旋转加料器18-PF-3501X电机启动控制 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-DO | - | - | C01
- | 18-HS-35101P | PLC | 粉料仓旋转加料器18-PF-3501X电机停止控制 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-DO | - | - | C01
- | 18-HS-35101SL | PLC | 粉料仓旋转加料器18-PF-3501X电机允许启/停 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-DO | - | - | C01
- | 18-HS-35101L | PLC | 粉料仓旋转加料器18-PF-3501X电机远程状态 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-DI | - | - | C01
- | 18-HS-35101E | PLC | 粉料仓旋转加料器18-PF-3501X电机驱动使能 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-DI | - | - | C01
- | 18-YLF-35101R | PLC | 粉料仓旋转加料器18-PF-3501X电机正转运行状态 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-DI | - | - | C01
- | 18-YLR-35101R | PLC | 粉料仓旋转加料器18-PF-3501X电机反转运行状态 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-DI | - | - | C01
- | 18-SC-35101 | PLC | 粉料仓旋转加料器18-PF-3501X电机速度调整 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-AO | - | - | C01
- | 18-II-35101 | PLC | 粉料仓旋转加料器18-PF-3501X电机电流变送 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-AI | - | - | C01
- | 18-YL-35101F | PLC | 粉料仓旋转加料器18-PF-3501X电机故障状态 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-DI | - | - | C01
- | 18-FIC-35101 | PLC | 粉料仓旋转加料器18-PF-3501X电机驱动命令 | 1830-PS07-351 | MCC | 18-PF-3501X | PLC-AI | - | - | C01
- | 18-ST-35101 | PLC | 轴动传感器用频率转换器 | 1830-PS07-351 | Field | 18-PF-3501X | PLC-AI | - | 同时进SIS | C01
- | 18-SOV-35101 | PLC | 粉料仓旋转加料器18-PF-3501X轴封气电磁阀 | 1830-PS07-351 | Field | 18-PF-3501X | PLC-DO | - | - | C01
- | 18-YL-36113R | PLC | 添加剂系统已准备就绪 | 1830-PS07-361 | CCR | 挤出机PLC | PLC-DO | - | - | C01
- | 18-YL-36112R | PLC | 添加剂系统正常运行状态 | 1830-PS07-361 | CCR | 挤出机PLC | PLC-DO | - | - | C01
- | 18-FI-36111A | PLC | 主粉料计量秤18-PF-3601实际流量值 | 1830-PS07-361 | CCR | 挤出机PLC | PLC-AO | - | - | C01
- | 18-HS-36114S | PLC | 挤压机系统启动添加剂系统 | 1830-PS07-361 | CCR | 挤出机PLC | PLC-DI | - | - | C01
- | 18-HS-36115P | PLC | 挤压机系统停止添加剂系统 | 1830-PS07-361 | CCR | 挤出机PLC | PLC-DI | - | - | C01
- | 18-YL-36116R | PLC | 挤压机电机的运行状态 | 1830-PS07-361 | CCR | 挤出机PLC | PLC-DI | - | - | C01
- | 18-FI-36117 | PLC | 挤压机流量设定值 | 1830-PS07-361 | CCR | 挤出机PLC | PLC-AI | - | - | C01
- | 18-XZH-35101 | PLC | 气动滑板阀18-XV-35101开状态反馈 | 1830-PS07-351 | CCR | 风送系统DCS | PLC-DI | - | - | C01
- | 18-XZL-35101 | PLC | 气动滑板阀18-XV-35101关状态反馈 | 1830-PS07-351 | CCR | 风送系统DCS | PLC-DI | - | - | C01
- | 18--XZAB-35102 | PLC | 气动换向阀18-XV-35102直通状态反馈 | 1830-PS07-351 | CCR | 风送系统DCS | PLC-DI | - | - | C01
- | 18--XZAC-35102 | PLC | 气动换向阀18-XV-35102旁通状态反馈 | 1830-PS07-351 | CCR | 风送系统DCS | PLC-DI | - | - | C01
- | 18-YL-35101R | PLC | 粉料仓旋转加料器18-PF-3501X电机运行状态 | 1830-PS07-351 | CCR | 风送系统DCS | PLC-DO | - | - | C01
- | 18-FI-36101C | PLC | 主粉料计量秤18-PF-3601实际流量值 | 1830-PS07-361 | CCR | 风送系统DCS | PLC-AO | - | - | C01
风送系统-粉料
- | 18-HS-35103 | DCS | 排气过滤器18-FL-3501X反吹启/停控制 | 1830-PS07-351 | Field | 反吹时序控制箱 | DCS-DO | - | - | C01
- | 18-YL-35103RN | DCS | 排气过滤器18-FL-3501X反吹运行状态 | 1830-PS07-351 | Field | 反吹时序控制箱 | DCS-DI | - | - | C01
- | 18-LHS-35103REM | DCS | 排气过滤器18-FL-3501X反吹远程状态 | 1830-PS07-351 | Field | 反吹时序控制箱 | DCS-DI | - | - | C01
- | 18-PDI-35102 | DCS | 排气过滤器18-FL-3501X差压显 | 1830-PS07-351 | Field | 18-PDT-35102 | DCS-AI | - | - | C01
- | 18-XZH-35103 | DCS | 手动蝶阀18-BV-35103开状态 | 1830-PS07-351 | Field | 18-BV-35103 | DCS-DI | - | - | C01
- | 18-XZL-35103 | DCS | 手动蝶阀18-BV-35103关状态 | 1830-PS07-351 | Field | 18-BV-35103 | DCS-DI | - | - | C01
- | 18-PI-35101 | DCS | 粉料料仓18-VS-3501X顶部压力显 | 1830-PS07-351 | Field | 18-PT-35101 | DCS-AI | - | - | C01
- | 18-LAHH-35102 | DCS | 粉料料仓18-VS-3501X高高料位报警 | 1830-PS07-351 | Field | 18-LS-35102 | DCS-DI | - | - | C01
- | 18-WI-35101 | DCS | 粉料料仓18-VS-3501X物料重量显示 | 1830-PS07-351 | Field | 18-WT-35101 | DCS-AI | - | - | C01
- | 18-LAHH-35103 | DCS | 粉料料仓18-VS-3501X低低料位报警 | 1830-PS07-351 | Field | 18-LS-35103 | DCS-DI | - | - | C01
- | 18-XS-35104 | DCS | 控制角座阀18-XV-35104的开/关信号 | 1830-PS07-351 | Field | 18-XV-35104 | DCS-DO | - | - | C01
- | 18-XS-35101 | DCS | 控制气动滑板阀18-XV-35101开/关信号 | 1830-PS07-351 | Field | 18-XV-35101 | DCS-DO | - | - | C01
- | 18-XZH-35101 | DCS | 气动滑板阀18-XV-35101开状态 | 1830-PS07-351 | Field | 18-XV-35101 | DCS-DI | - | - | C01
- | 18-XZL-35101 | DCS | 气动滑板阀18-XV-35101关状态 | 1830-PS07-351 | Field | 18-XV-35101 | DCS-DI | - | - | C01
- | 18-XS-35102 | DCS | 控制气动滑板阀18-XV-35102开/关信号 | 1830-PS07-351 | Field | 18-XV-35102 | DCS-DO | - | - | C01
- | 18-XZH-35102 | DCS | 气动滑板阀18-XV-35102开状态 | 1830-PS07-351 | Field | 18-XV-35102 | DCS-DI | - | - | C01
- | 18-XZL-35102 | DCS | 气动滑板阀18-XV-35102关状态 | 1830-PS07-351 | Field | 18-XV-35102 | DCS-DI | - | - | C01
- | 18-HS-35102P | DCS | 粉料循环旋转阀18-PF-3502X的停止控制 | 1830-PS07-351 | MCC | 18-PF-3502X | DCS-DO | - | - | C01 | 18-HS-35102SP | BLOOM修改位号
- | 18-HS-35102S | DCS | 粉料循环旋转阀18-PF-3502X的启动控制 | 1830-PS07-351 | MCC | 18-PF-3502X | DCS-DO | - | - | C01 | 18-HS-35102ST | BLOOM修改位号
- | 18-YL-35102R | DCS | 粉料循环旋转阀18-PF-3502X的运行状态 | 1830-PS07-351 | MCC | 18-PF-3502X | DCS-DI | - | - | C01 | 18-YL-35102RN | BLOOM修改位号
- | 18-YL-35102F | DCS | 粉料循环旋转阀18-PF-3502X的故障状态 | 1830-PS07-351 | MCC | 18-PF-3502X | DCS-DI | - | - | C01 | 18-YL-35102FA | BLOOM修改位号
- | 18-YL-35102L | DCS | 粉料循环旋转阀18-PF-3502X的远程状态 | 1830-PS07-351 | MCC | 18-PF-3502X | DCS-DI | - | - | C01 | 18-YL-35102REM | BLOOM修改位号
- | 18-SI-35102 | DCS | 粉料循环旋转阀18-PF-3502X的速度显示 | 1830-PS07-351 | MCC | 18-PF-3502X | DCS-AI | - | 删除 | C01 | 18-SI-35102 | BLOOM修改位号
- | 18-PI-35108 | DCS | UP-3501系统循环线输送压力显示 | 1830-PS07-351 | Field | 18-PT-35108 | DCS-AI | - | - | C01
- | 18-XS-35107 | DCS | 控制气动蝶阀18-XV-35107开/关信号 | 1830-PS07-351 | Field | 18-XV-35107 | DCS-DO | - | - | C01
- | 18-XZH-35107 | DCS | 气动蝶阀18-XV-35107开状态 | 1830-PS07-351 | Field | 18-XV-35107 | DCS-DI | - | - | C01
- | 18-XZL-35107 | DCS | 气动蝶阀18-XV-35107关状态 | 1830-PS07-351 | Field | 18-XV-35107 | DCS-DI | - | - | C01
- | 18-HS-35101P | DCS | 粉料仓旋转阀18-PF-3501X的停止控制 | 1830-PS07-351 | MCC | 18-PF-3501X | DCS-DO | - | - | C01 | 18-HS-35101SP | BLOOM修改位号
- | 18-HSF-35101S | DCS | 粉料仓旋转阀18-PF-3501X的正转启动控制 | 1830-PS07-351 | MCC | 18-PF-3501X | DCS-DO | - | - | C01 | 18-HS-35101FS | BLOOM修改位号
- | 18-HSR-35101S | DCS | 粉料仓旋转阀18-PF-3501X的反转启动控制 | 1830-PS07-351 | MCC | 18-PF-3501X | DCS-DO | - | - | C01 | 18-HS-35101RS | BLOOM修改位号
- | 18-YLF-35101R | DCS | 粉料仓旋转阀18-PF-3501X的正转运行状态 | 1830-PS07-351 | MCC | 18-PF-3501X | DCS-DI | - | - | C01 | 18-YL-35101RNF | BLOOM修改位号
- | 18-YLR-35101R | DCS | 粉料仓旋转阀18-PF-3501X的反转运行状态 | 1830-PS07-351 | MCC | 18-PF-3501X | DCS-DI | - | - | C01 | 18-YL-35101RNR | BLOOM修改位号
- | 18-YL-35101F | DCS | 粉料仓旋转阀18-PF-3501X的故障状态 | 1830-PS07-351 | MCC | 18-PF-3501X | DCS-DI | - | - | C01 | 18-YL-35101FA | BLOOM修改位号
- | 18-YL-35101L | DCS | 粉料仓旋转阀18-PF-3501X的远程状态 | 1830-PS07-351 | MCC | 18-PF-3501X | DCS-DI | - | - | C01 | 18-YL-35101REM | BLOOM修改位号
- | 18-SC-35101 | DCS | 粉料仓旋转阀18-PF-3501X的速度控制 | 1830-PS07-351 | MCC | 18-PF-3501X | DCS-AO | - | - | C01 | 18-SC-36101 | BLOOM修改位号
- | 18-SI-35101 | DCS | 粉料仓旋转阀18-PF-3501X的速度显示 | 1830-PS07-351 | MCC | 18-PF-3501X | DCS-AI | - | - | C01 | 18-SI-35101 | BLOOM修改位号
- | 18-II-35101 | DCS | 粉料仓旋转阀18-PF-3501X的电流显示 | 1830-PS07-351 | MCC | 18-PF-3501X | DCS-AI | - | - | C01 | 新增 按照电气 | BLOOM修改位号
- | 18-YL-35111R | DCS | 粉料仓旋转阀18-PF-3501X的风扇运行状态 | 1830-PS07-351 | MCC | 18-PF-3501XF | DCS-DI | - | - | C01 | 新增 按照电气 | BLOOM修改位号
- | 18-PI-35205 | DCS | 输送氮气风机入口压力显示 | 1830-PS07-352 | Field | 18-PT-35205 | DCS-AI | - | - | C01
- | 18-PY-35201 | DCS | 输送氮气风机入口排气调节阀定位器 | 1830-PS07-352 | Field | 18-PV-35201 | DCS-AO | - | - | C01
- | 18-PY-35205 | DCS | 输送氮气风机入口补气调节阀定位器 | 1830-PS07-352 | Field | 18-PV-35205 | DCS-AO | - | - | C01
- | 18-FI-35201 | DCS | 输送氮气风机入口补气流量显示 | 1830-PS07-352 | Field | 18-FT-35201 | DCS-AO | - | - | C01
- | 18-AI-35201 | DCS | 输送氮气风机入口烃含量显示 | 1830-PS07-352 | Field | 18-AT-35201 | DCS-AI | - | - | C01
- | 18-AI-35202 | DCS | 输送氮气风机入口氧含量显示 | 1830-PS07-352 | Field | 18-AT-35202 | DCS-AI | - | - | C01
- | 18-XS-35201 | DCS | 控制气动蝶阀18-XV-35201开/关信号 | 1830-PS07-352 | Field | 18-XV-35201 | DCS-DO | - | - | C01
- | 18-XZH-35201 | DCS | 气动蝶阀18-XV-35201开状态 | 1830-PS07-352 | Field | 18-XV-35201 | DCS-DI | - | - | C01
- | 18-XZL-35201 | DCS | 气动蝶阀18-XV-35201关状态 | 1830-PS07-352 | Field | 18-XV-35201 | DCS-DI | - | - | C01
- | 18-PI-35201A | DCS | 风机18-PB-3501AX入口压力显示 | 1830-PS07-352 | Field | 18-PT-35201A | DCS-AI | - | - | C01
- | 18-PI-35201B | DCS | 风机18-PB-3501AX入口压力显示 | 1830-PS07-352 | Field | 18-PT-35201B | DCS-AI | - | - | C01
- | 18-YL-35201L | DCS | 输送氮气风机18-PB-3501AX主电机远程状态 | 1830-PS07-352 | MCC | 18-PB-3501AX | DCS-DI | - | - | C01 | 18-LHS-35201REM | BLOOM修改位号
- | 18-HS-35201P | DCS | 输送氮气风机18-PB-3501AX主电机停止控制 | 1830-PS07-352 | MCC | 18-PB-3501AX | DCS-DO | - | - | C01 | 18-HS-35201SP | BLOOM修改位号
- | 18-HS-35201S | DCS | 输送氮气风机18-PB-3501AX主电机启动控制 | 1830-PS07-352 | MCC | 18-PB-3501AX | DCS-DO | - | - | C01 | 18-HS-35201ST | BLOOM修改位号
- | 18-HS-35201L | DCS | 输送氮气风机18-PB-3501AX主电机允许启动 | 1830-PS07-352 | MCC | 18-PB-3501AX | DCS-DO | - | - | C01 | 18-HS-35201AL | BLOOM修改位号
- | 18-YL-35201R | DCS | 输送氮气风机18-PB-3501AX主电机运行状态 | 1830-PS07-352 | MCC | 18-PB-3501AX | DCS-DI | - | - | C01 | 18-YL-35201RN | BLOOM修改位号
- | 18-YL-35201F | DCS | 输送氮气风机18-PB-3501AX主电机故障状态 | 1830-PS07-352 | MCC | 18-PB-3501AX | DCS-DI | - | - | C01 | 18-YL-35201FA | BLOOM修改位号
- | 18-II-35201 | DCS | 输送氮气风机18-PB-3501AX主电机电流显示 | 1830-PS07-352 | MCC | 18-PB-3501AX | DCS-AI | - | - | C01 | 18-II-35201 | BLOOM修改位号
- | 18-TI-35204A | DCS | 输送氮气风机18-PB-3501AX主电机定子温度显示 | 1830-PS07-352 | Field | 18-TT-35204A | DCS-AI | - | - | C01
- | 18-TI-35204B | DCS | 输送氮气风机18-PB-3501AX主电机定子温度显示 | 1830-PS07-352 | Field | 18-TT-35204B | DCS-AI | - | - | C01
- | 18-TI-35204C | DCS | 输送氮气风机18-PB-3501AX主电机定子温度显示 | 1830-PS07-352 | Field | 18-TT-35204C | DCS-AI | - | - | C01
- | 18-TI-35204D | DCS | 输送氮气风机18-PC-3501AX主电机轴承温度显示 | 1830-PS07-352 | Field | 18-TT-35204D | DCS-AI | - | - | C01
- | 18-TI-35204E | DCS | 输送氮气风机18-PC-3501AX主电机轴承温度显示 | 1830-PS07-352 | Field | 18-TT-35204E | DCS-AI | - | - | C01
- | 18-PSAL-35203 | DCS | 输送氮气风机18-PB-3501AX入口压力低报警 | 1830-PS07-352 | Field | 18-PB-3501AX | DCS-DI | - | - | C01
- | 18-TSAH-35202 | DCS | 输送氮气风机18-PB-3501AX出口温度高报警 | 1830-PS07-352 | Field | 18-PB-3501AX | DCS-DI | - | - | C01
- | 18-PSAH-35202 | DCS | 输送氮气风机18-PB-3501AX出口压力高报警 | 1830-PS07-352 | Field | 18-PB-3501AX | DCS-DI | - | - | C01
- | 18-XS-35202 | DCS | 控制气动蝶阀18-XV-35202开/关信号 | 1830-PS07-352 | Field | 18-XV-35202 | DCS-DO | - | - | C01
- | 18-XZH-35202 | DCS | 气动蝶阀18-XV-35202开状态 | 1830-PS07-352 | Field | 18-XV-35202 | DCS-DI | - | - | C01
- | 18-XZL-35202 | DCS | 气动蝶阀18-XV-35202关状态 | 1830-PS07-352 | Field | 18-XV-35202 | DCS-DI | - | - | C01
- | 18-XS-35203 | DCS | 控制气动蝶阀18-XV-35203开/关信号 | 1830-PS07-352 | Field | 18-XV-35203 | DCS-DO | - | - | C01
- | 18-XZH-35203 | DCS | 气动蝶阀18-XV-35203开状态 | 1830-PS07-352 | Field | 18-XV-35203 | DCS-DI | - | - | C01
- | 18-XZL-35203 | DCS | 气动蝶阀18-XV-35203关状态 | 1830-PS07-352 | Field | 18-XV-35203 | DCS-DI | - | - | C01
- | 18-PI-35211A | DCS | 风机18-PB-3501BX入口压力显示 | 1830-PS07-352 | Field | 18-PT-35211A | DCS-AI | - | - | C01
- | 18-PI-35211B | DCS | 风机18-PB-3501BX入口压力显示 | 1830-PS07-352 | Field | 18-PT-35211B | DCS-AI | - | - | C01
- | 18-YL-35202L | DCS | 输送氮气风机18-PB-3501BX主电机远程状态 | 1830-PS07-352 | MCC | 18-PB-3501BX | DCS-DI | - | - | C01 | 18-LHS-35211REM | BLOOM修改位号
- | 18-HS-35202P | DCS | 输送氮气风机18-PB-3501BX主电机停止控制 | 1830-PS07-352 | MCC | 18-PB-3501BX | DCS-DO | - | - | C01 | 18-HS-35211SP | BLOOM修改位号
- | 18-HS-35202S | DCS | 输送氮气风机18-PB-3501BX主电机启动控制 | 1830-PS07-352 | MCC | 18-PB-3501BX | DCS-DO | - | - | C01 | 18-HS-35211ST | BLOOM修改位号
- | 18-HS-35202L | DCS | 输送氮气风机18-PB-3501BX主电机允许启动 | 1830-PS07-352 | MCC | 18-PB-3501BX | DCS-DO | - | - | C01 | 18-HS-35211AL | BLOOM修改位号
- | 18-YL-35202R | DCS | 输送氮气风机18-PB-3501BX主电机运行状态 | 1830-PS07-352 | MCC | 18-PB-3501BX | DCS-DI | - | - | C01 | 18-YL-35211RN | BLOOM修改位号
- | 18-YL-35202F | DCS | 输送氮气风机18-PB-3501BX主电机故障状态 | 1830-PS07-352 | MCC | 18-PB-3501BX | DCS-DI | - | - | C01 | 18-YL-35211FA | BLOOM修改位号
- | 18-II-35202 | DCS | 输送氮气风机18-PB-3501BX主电机电流显示 | 1830-PS07-352 | MCC | 18-PB-3501BX | DCS-AI | - | - | C01 | 18-II-35211 | BLOOM修改位号
- | 18-TI-35214A | DCS | 输送氮气风机18-PB-3501BX主电机定子温度显示 | 1830-PS07-352 | Field | 18-TT-35214A | DCS-AI | - | - | C01
- | 18-TI-35214B | DCS | 输送氮气风机18-PB-3501BX主电机定子温度显示 | 1830-PS07-352 | Field | 18-TT-35214B | DCS-AI | - | - | C01
- | 18-TI-35214C | DCS | 输送氮气风机18-PB-3501BX主电机定子温度显示 | 1830-PS07-352 | Field | 18-TT-35214C | DCS-AI | - | - | C01
- | 18-TI-35214D | DCS | 输送氮气风机18-PC-3501BX主电机轴承温度显示 | 1830-PS07-352 | Field | 18-TT-35214D | DCS-AI | - | - | C01
- | 18-TI-35214E | DCS | 输送氮气风机18-PC-3501BX主电机轴承温度显示 | 1830-PS07-352 | Field | 18-TT-35214E | DCS-AI | - | - | C01
- | 18-PSAL-35213 | DCS | 输送氮气风机18-PC-3501BX入口压力低报警 | 1830-PS07-352 | Field | 18-PB-3501BX | DCS-DI | - | - | C01
- | 18-TSAH-35212 | DCS | 输送氮气风机18-PC-3501BX出口温度高报警 | 1830-PS07-352 | Field | 18-PB-3501BX | DCS-DI | - | - | C01
- | 18-PSAH-35212 | DCS | 输送氮气风机18-PC-3501BX出口压力高报警 | 1830-PS07-352 | Field | 18-PB-3501BX | DCS-DI | - | - | C01
- | 18-XS-35204 | DCS | 控制气动蝶阀18-XV-35204开/关信号 | 1830-PS07-352 | Field | 18-XV-35204 | DCS-DO | - | - | C01
- | 18-XZH-35204 | DCS | 气动蝶阀18-XV-35204开状态 | 1830-PS07-352 | Field | 18-XV-35204 | DCS-DI | - | - | C01
- | 18-XZL-35204 | DCS | 气动蝶阀18-XV-35204关状态 | 1830-PS07-352 | Field | 18-XV-35204 | DCS-DI | - | - | C01
- | 18-TI-35201 | DCS | 输送氮气风机出口温度显示 | 1830-PS07-352 | Field | 18-TT-35201 | DCS-AI
- | 18-XS-35206 | DCS | 控制气动蝶阀18-XV-35206开/关信号 | 1830-PS07-352 | Field | 18-XV-35206 | DCS-DO | - | - | C01
- | 18-XZH-35206 | DCS | 气动蝶阀18-XV-35206开状态 | 1830-PS07-352 | Field | 18-XV-35206 | DCS-DI | - | - | C01
- | 18-XZL-35206 | DCS | 气动蝶阀18-XV-35206关状态 | 1830-PS07-352 | Field | 18-XV-35206 | DCS-DI | - | - | C01
- | 18-PI-35204 | DCS | 输送氮气出口冷却器EM-3502X出口压力显示 | 1830-PS07-352 | Field | 18-PT-35204 | DCS-AI
挤出机（日钢）
- | 18-TIA-36311A~F | PLC | MAIN DRIVE MOTOR WINDING TEMP. | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36311A~F | Temperature Transmitter | MAIN DRIVE MOTOR WINDING TEMP. | 1830-PS07-363 | Field | 18-3601-PJB-1001 | PLC-AIx6 | - | Pt100/No.3 PLC | C01
- | 18-TIA-36312AB | PLC | MAIN DRIVE MOTOR BEARING TEMP.（NDE） | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36312AB | Temperature Transmitter | MAIN DRIVE MOTOR BEARING TEMP.（NDE） | 1830-PS07-363 | Field | 18-3601-PJB-1002 | PLC-AIx2 | - | Pt100/No.3 PLC | C01
- | 18-TIA-36313AB | PLC | MAIN DRIVE MOTOR BEARING TEMP.（DE） | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36313AB | Temperature Transmitter | MAIN DRIVE MOTOR BEARING TEMP.（DE） | 1830-PS07-363 | Field | 18-3601-PJB-1002 | PLC-AIx2 | - | Pt100/No.3 PLC | C01
- | 18-VIA-36312AB | PLC | MAIN DRIVE MOTOR BEARING VIBRATION（NDE） | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-VE-36312AB | Vibration Transmitter | MAIN DRIVE MOTOR BEARING VIBRATION（NDE） | 1830-PS07-363 | Field | 18-3601-PJB-1004 | PLC-AIx2 | - | No.3 PLC | C01
- | 18-VIA-36313AB | PLC | MAIN DRIVE MOTOR BEARING VIBRATION（DE） | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-VE-36313AB | Vibration Transmitter | MAIN DRIVE MOTOR BEARING VIBRATION（DE） | 1830-PS07-363 | Field | 18-3601-PJB-1004 | PLC-AIx2 | - | No.3 PLC | C01
- | 18-LS-36314AB | PLC | MAIN DRIVE MOTOR COOLER WATER LEVEL | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-LS-36314AB | LEAKAGE DETECTOR | MAIN DRIVE MOTOR COOLER WATER LEVEL | 1830-PS07-363 | Field | 18-3601-PJB-1005 | PLC-DIx2 | - | SPDT/No.1 PLC | C01
- | 18-FIA-36312 | PLC | - | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-FT-36312 | Flow Transmitter | - | 1830-PS07-363 | In-Line | - | PLC-AI | - | No.3 PLC | C01
- | 18-FIA-36313 | PLC | - | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-FT-36313 | Flow Transmitter | - | 1830-PS07-363 | In-Line | - | PLC-AI | - | No.3 PLC | C01
- | 18-FIA-36314 | PLC | MAIN DRIVE MOTOR CWR PIPING FLOW | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-FT-36314 | Flow Transmitter | MAIN DRIVE MOTOR CWR PIPING FLOW | 1830-PS07-363 | In-Line | 100-CWR-36301-CA2W-N | PLC-AI | - | No.3 PLC | C01
- | 18-PIA-36323 | PLC | JACK-UP OIL UNIT PRESSURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-PT-36323 | Pressure Transmitter | JACK-UP OIL UNIT PRESSURE | 1830-PS07-363 | Field | 18-3601-PJB-1003 | PLC-AI | - | No.3 PLC | C01
- | 18-PIA-36324 | PLC | JACK-UP OIL UNIT PRESSURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-PT-36324 | Pressure Transmitter | JACK-UP OIL UNIT PRESSURE | 1830-PS07-363 | Field | 18-3601-PJB-1003 | PLC-AI | - | No.3 PLC | C01
- | 18-PDIA-36333 | PLC | MAIN DRIVE MOTOR LUBE OIL FILTER PRESSURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-PDT-36333 | DP Transmitter | MAIN DRIVE MOTOR LUBE OIL FILTER PRESSURE | 1830-PS07-363 | Field | 18-3601-PJB-1006 | PLC-AI | - | No.3 PLC | C01
- | 18-PIA-36334A | PLC | MAIN DRIVE MOTOR LUBE OIL PRESSURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-PT-36334A | Pressure Transmitter | MAIN DRIVE MOTOR LUBE OIL PRESSURE | 1830-PS07-363 | Field | 18-3601-PJB-1006 | PLC-AI | - | No.3 PLC | C01
- | 18-PIA-36334B | PLC | MAIN DRIVE MOTOR LUBE OIL PRESSURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-PT-36334B | Pressure Transmitter | MAIN DRIVE MOTOR LUBE OIL PRESSURE | 1830-PS07-363 | Field | 18-3601-PJB-1006 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-36332 | PLC | MAIN DRIVE MOTOR LUBE OIL TEMPERATURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36332 | Temperature Transmitter | MAIN DRIVE MOTOR LUBE OIL TEMPERATURE | 1830-PS07-363 | Field | 18-3601-PJB-1006 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-36333 | PLC | MAIN DRIVE MOTOR LUBE OIL TEMPERATURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36333 | Temperature Transmitter | MAIN DRIVE MOTOR LUBE OIL TEMPERATURE | 1830-PS07-363 | Field | 18-3601-PJB-1006 | PLC-AI | - | No.3 PLC | C01
- | 18-TS-36334 | PLC | MAIN DRIVE MOTOR LUBE OIL TEMPERATURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TS-36334 | Temperature SWITCH | MAIN DRIVE MOTOR LUBE OIL TEMPERATURE | 1830-PS07-363 | Equip. | 18-VK-3601X | PLC-DI | - | No.1 PLC | C01
- | 18-LIA-36332 | PLC | MAIN DRIVE MOTOR LUBE OIL TANK LEVEL | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-LT-36332 | DP Transmitter | MAIN DRIVE MOTOR LUBE OIL TANK LEVEL | 1830-PS07-363 | Equip. | 18-3601-PJB-1006 | PLC-AI | - | No.3 PLC | C01
- | 18-SIA-36350A | PLC | MIXER TORQUE COUPLING SLIP DETECTOR(MOTOR SIDE) | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-SE-36350A | PROXIMITY SWITCH | MIXER TORQUE COUPLING SLIP DETECTOR(MOTOR SIDE) | 1830-PS07-363 | Field | 18-3601-PJB-1007 | PLC-DI | - | No.3 PLC | C01
- | 18-SIA-36350B | PLC | MIXER TORQUE COUPLING SLIP DETECTOR(G/R SIDE) | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-SE-36350B | PROXIMITY SWITCH | MIXER TORQUE COUPLING SLIP DETECTOR(G/R SIDE) | 1830-PS07-363 | Field | 18-3601-PJB-1007 | PLC-DI | - | No.3 PLC | C01
- | 18-ZSH-36341 | PROXIMITY SWITCH | DISCHARGE UNIT CLUTCH "ON" | 1830-PS07-363 | Field | 18-3601-PJB-1011 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSL-36341 | PROXIMITY SWITCH | DISCHARGE UNIT CLUTCH "OFF" | 1830-PS07-363 | Field | 18-3601-PJB-1011 | PLC-DI | - | No.1 PLC | C01
- | 18-HY-36342 | Solenoid Valve | DISCHARGE UNIT CLUTCH "ON"/"OFF" | 1830-PS07-363 | Field | 18-3601-PJB-1012 | PLC-DOx2 | - | No.2 PLC | C01
- | 18-HY-36343 | Solenoid Valve | DISCHARGE UNIT AIR MOTOR "ON" | 1830-PS07-363 | Field | 18-3601-PJB-1012 | PLC-DO | - | No.2 PLC | C01
- | 18-TIA-36341A~C | PLC | PMM-3603X WINDING TEMP. | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36341A~C | Temperature Transmitter | PMM-3603X WINDING TEMP. | 1830-PS07-363 | Field | 18-3601-PJB-1010 | PLC-AIx3 | - | Pt100/No.3 PLC | C01
- | 18-TIA-36342 | PLC | PMM-3603X BEARING TEMP.（NDE） | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36342 | Temperature Transmitter | PMM-3603X BEARING TEMP.（NDE） | 1830-PS07-363 | Field | 18-3601-PJB-1010 | PLC-AI | - | Pt100/No.3 PLC | C01
- | 18-TIA-36343 | PLC | PMM-3603X BEARING TEMP.（DE） | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36343 | Temperature Transmitter | PMM-3603X BEARING TEMP.（DE） | 1830-PS07-363 | Field | 18-3601-PJB-1010 | PLC-AI | - | Pt100/No.3 PLC | C01
- | 18-ZIA-36352AB | PLC | MIXER G/R GEAR POSITION "HIGH SPEED" | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-ZE-36352AB | PROXIMITY SENSOR | MIXER G/R GEAR POSITION "LOW SPEED" | 1830-PS07-363 | Field | 18-3601-PJB-1013 | PLC-AIx2 | - | No.3 PLC | C01
- | 18-ZSH-36351 | PROXIMITY SWITCH | CLUTCH POSITION "HIGH SPEED" | 1830-PS07-363 | Field | 18-3601-PJB-1015 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSL-36351 | PROXIMITY SWITCH | CLUTCH POSITION "LOW SPEED" | 1830-PS07-363 | Field | 18-3601-PJB-1015 | PLC-DI | - | No.1 PLC | C01
- | 18-TIA-36351AB | PLC | MIXER G/R BEARING TEMP. | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36351AB | Temperature Transmitter | MIXER G/R BEARING TEMP. | 1830-PS07-363 | Field | 18-3601-PJB-1013 | PLC-AIx2 | - | Pt100/No.3 PLC | C01
- | 18-TIA-36352AB | PLC | MIXER G/R BEARING TEMP. | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36352AB | Temperature Transmitter | MIXER G/R BEARING TEMP. | 1830-PS07-363 | Field | 18-3601-PJB-1013 | PLC-AIx2 | - | Pt100/No.3 PLC | C01
- | 18-TIA-36353 | PLC | MIXER G/R OIL BATH TEMP. | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36353 | Temperature Transmitter | MIXER G/R OIL BATH TEMP. | 1830-PS07-363 | Field | 18-3601-PJB-1013 | PLC-AI | - | Pt100/No.3 PLC | C01
- | 18-VIA-36351A~C | PLC | MIXER G/R VIBRATION | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-VE-36351A~C | VIBRATION SENSOR | MIXER G/R VIBRATION | 1830-PS07-363 | Field | 18-3601-PJB-1014 | PLC-AIx3 | - | No.3 PLC | C01
- | 18-TSH-36354A | THERMOSTAT | MIXER G/R TEMP. | 1830-PS07-363 | Field | - | PLC-DI | - | No.1 PLC | C01
- | 18-TSH-36354B | THERMOSTAT | MIXER G/R TEMP. | 1830-PS07-363 | Field | - | PLC-DI | - | No.1 PLC | C01
- | 18-PDIA-36363 | PLC | MIXER G/R LUBE OIL FILTER PRESSURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-PDT-36363 | DP Transmitter | MIXER G/R LUBE OIL FILTER PRESSURE | 1830-PS07-363 | Field | 18-3601-PJB-1016 | PLC-AI | - | No.3 PLC | C01
- | 18-PIA-36364A | PLC | MIXER G/R MOTOR LUBE OIL PRESSURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-PT-36364A | Pressure Transmitter | MIXER G/R MOTOR LUBE OIL PRESSURE | 1830-PS07-363 | Field | 18-3601-PJB-1016 | PLC-AI | - | No.3 PLC | C01
- | 18-PIA-36364B | PLC | MIXER G/R MOTOR LUBE OIL PRESSURE | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-PT-36364B | Pressure Transmitter | MIXER G/R MOTOR LUBE OIL PRESSURE | 1830-PS07-363 | Field | 18-3601-PJB-1016 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-36362 | PLC | MIXER G/R MOTOR LUBE OIL TEMP. | 1830-PS07-363 | CCR | - | - | - | - | C01
- | 18-TT-36362 | Temperature Transmitter | MIXER G/R MOTOR LUBE OIL TEMP. | 1830-PS07-363 | Field | 18-3601-PJB-1016 | PLC-AI | - | No.3 PLC | C01
- | 18-PIA-36401 | PLC | ABC SEAL PRESSURE | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-PT-36401 | Pressure Transmitter | ABC SEAL PRESSURE | 1830-PS07-364 | Field | 18-PJ-3601X | PLC-AI | - | No.3 PLC | C01
- | 18-FIA-36403 | PLC | - | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-FT-36403 | Pressure Transmitter | - | 1830-PS07-364 | Field | - | PLC-DI | - | No.1 PLC | C01
- | 18-LS-36404 | PLC | FEED HOPPER LEVEL | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-LS-36404 | LEVEL SWITCH | FEED HOPPER LEVEL | 1830-PS07-364 | Equip. | 18-VH-3601X | PLC-DI | - | No.1 PLC | C01
- | 18-PDIA-36407 | PLC | FEED HOPPER VENT FILTER PRESSURE | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-PDT-36407 | DP Transmitter | FEED HOPPER VENT FILTER PRESSURE | 1830-PS07-364 | Field | 18-FL-3601X | PLC-AI | - | No.3 PLC | C01
- | 18-ZIA-36432 | PLC | SLOT DISK POSITION | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-ZE-36432 | LINEAR SCALE | SLOT DISK POSITION | 1830-PS07-364 | Field | 18-3601-PJB-1017 | PLC-AI | - | No.3 PLC/四线制24V DC 电源 | C01
- | 18-ZSH-36431 | PROXIMITY SWITCH | SLOT DISK “OPEN” | 1830-PS07-364 | Field | 18-3601-PJB-1018 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSL-36431 | PROXIMITY SWITCH | SLOT DISK “CLOSE” | 1830-PS07-364 | Field | 18-3601-PJB-1018 | PLC-DI | - | No.1 PLC | C01
- | 18-TIA-36420 | PLC | SLOT DISK TEMP. | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-TT-36420 | Temperature Transmitter | SLOT DISK TEMP. | 1830-PS07-364 | Field | 18-3601-PJB-1019 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-36430 | PLC | SLOT DISK HEATER TEMP. | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-TT-36430 | Temperature Transmitter | SLOT DISK HEATER TEMP. | 1830-PS07-364 | Field | 18-3601-PJB-1019 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-36412~15 | PLC | CYLINDER TEMP. | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-TT-36412~15 | Temperature Transmitter | CYLINDER TEMP. | 1830-PS07-364 | Field | 18-3601-PJB-1019 | PLC-AIx4 | - | No.3 PLC | C01
- | 18-TIA-36422~25 | PLC | CYLINDER HEATER TEMP. | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-TT-36422~25 | Temperature Transmitter | CYLINDER HEATER TEMP. | 1830-PS07-364 | Field | 18-3601-PJB-1019 | PLC-AIx4 | - | No.3 PLC | C01
- | 18-TIA-36416~19 | PLC | CYLINDER TEMP. | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-TT-36416~19 | Temperature Transmitter | CYLINDER TEMP. | 1830-PS07-364 | Field | 18-3601-PJB-1020 | PLC-AIx4 | - | No.3 PLC | C01
- | 18-TIA-36426~29 | PLC | CYLINDER HEATER TEMP. | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-TT-36426~29 | Temperature Transmitter | CYLINDER HEATER TEMP. | 1830-PS07-364 | Field | 18-3601-PJB-1020 | PLC-AIx4 | - | No.3 PLC | C01
- | 18-TY-36412~19 | Solenoid Valve | CYLINDER COOLING | 1830-PS07-364 | Field | 18-3601-PJB-1021 | PLC-DOx8 | - | No.2 PLC | C01
- | 18-TIA-36441 | PLC | VENT HOUSING TEMP. | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-TT-36441 | Temperature Transmitter | VENT HOUSING TEMP. | 1830-PS07-364 | Field | 18-3601-PJB-1020 | PLC-AI | - | No.3 PLC | C01
- | 18-PIA-36417 | PLC | CYLINDER POLY. PRESS. | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-PT-36417 | Pressure Transmitter | CYLINDER POLY. PRESS. | 1830-PS07-364 | Field | 18-3601-PJB-1020 | PLC-AI | - | No.3 PLC | C01
- | 36417？ | PLC | CCW LINE TEMP. | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-TT-36462 | Temperature Transmitter | CCW LINE TEMP. | 1830-PS07-364 | Field | 18-3601-PJB-1022 | PLC-AI | - | No.3 PLC | C01
- | 18-TV-36462 | CONTROL VALVE | CCW LINE TEMP. CONTROL VALVE | 1830-PS07-364 | Field | 18-3601-PJB-1022 | PLC-AI | - | No.3 PLC | C01
- | 18-LIA-36464 | PLC | CCW TANK LEVEL | 1830-PS07-364 | CCR | - | - | - | - | C01
- | 18-LT-36464 | DIFF. PRESS.TRANSMITTER | CCW TANK LEVEL | 1830-PS07-364 | Field | 18-3601-PJB-1022 | PLC-AI | - | No.3 PLC | C01
- | 18-LY-36464 | Solenoid Valve | - | 1830-PS07-364 | Field | - | PLC-AI | - | No.2 PLC | C01
- | 18-HY-36408 | Solenoid Valve | FEED VENT FILTER | 1830-PS07-364 | Field | - | PLC-DO | - | No.2 PLC | C01
- | 18-ZSH-36501 | PROXIMITY SWITCH | CLUTCH POSITION "HIGH SPEED" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSL-36501 | PROXIMITY SWITCH | CLUTCH POSITION "LOW SPEED" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-HY-36501A | Solenoid Valve | D/V CUTTING DEVICE "FORWARD" | 1830-PS07-365 | Field | 18-3601-PJB-1025 | PLC-DO | - | No.2 PLC | C01
- | 18-HY-36501B | Solenoid Valve | D/V CUTTING DEVICE "BACKWARD" | 1830-PS07-365 | Field | 18-3601-PJB-1025 | PLC-DO | - | No.2 PLC | C01
- | 18-PIA-36501AB | PLC | S/C INLET POLY. PRESS. | 1830-PS07-365 | CCR | - | - | - | - | C01
- | 18-PT-36501AB | Pressure Transmitter | S/C INLET POLY. PRESS. | 1830-PS07-365 | Field | 18-3601-PJB-1023 | PLC-AIx2 | - | No.3 PLC | C01
- | 18-TIA-36501 | PLC | S/C INLET POLY. TEMP. | 1830-PS07-365 | CCR | - | - | - | - | C01
- | 18-TT-36501 | Temperature Transmitter | S/C INLET POLY. TEMP. | 1830-PS07-365 | Field | 18-3601-PJB-1023 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-36502 | PLC | S/C BODY TEMP. | 1830-PS07-365 | CCR | - | - | - | - | C01
- | 18-TT-36502 | Temperature Transmitter | S/C BODY TEMP. | 1830-PS07-365 | Field | 18-3601-PJB-1023 | PLC-AI | - | No.3 PLC | C01
- | 18-ZSL-36502 | PROXIMITY SWITCH | UPPER SCREEN CHANGER "CHANGE" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSM-36502 | PROXIMITY SWITCH | UPPER SCREEN CHANGER "AIR PURGE" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSN-36502 | PROXIMITY SWITCH | UPPER SCREEN CHANGER "AIR PURGE" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-ZST-36502 | PROXIMITY SWITCH | UPPER SCREEN CHANGER "THROUGH" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSL-36503 | PROXIMITY SWITCH | UPPER SCREEN CHANGER "CHANGE" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSM-36503 | PROXIMITY SWITCH | UPPER SCREEN CHANGER "AIR PURGE" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSN-36503 | PROXIMITY SWITCH | UPPER SCREEN CHANGER "AIR PURGE" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-ZST-36503 | PROXIMITY SWITCH | UPPER SCREEN CHANGER "THROUGH" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSH-36504 | PROXIMITY SWITCH | SCREEN CHANGER SAFETY COVER "OPEN" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-PIA-36515 | PLC | HYDRAULIC OIL UNIT PRESS. | 1830-PS07-365 | CCR | - | - | - | - | C01
- | 18-PT-36515 | Pressure Transmitter | HYDRAULIC OIL UNIT PRESS. | 1830-PS07-365 | Equip. | 18-PP-3605X | PLC-AI | - | No.3 PLC | C01
- | 18-HY-36511 | Solenoid Valve | DIVERTER VALVE "THROUGH" OR "DIVERT" | 1830-PS07-365 | Field | 18-3601-PJB-1026 | PLC-DOx2 | - | No.2 PLC | C01
- | 18-HY-36512 | Solenoid Valve | UPPER SCREEN "THROUGH" OR "CHANGE" | 1830-PS07-365 | Field | 18-3601-PJB-1026 | PLC-DOx2 | - | No.2 PLC | C01
- | 18-HY-36513 | Solenoid Valve | LOWER SCREEN "THROUGH" OR "CHANGE" | 1830-PS07-365 | Field | 18-3601-PJB-1026 | PLC-DOx2 | - | No.2 PLC | C01
- | 18-HY-36514 | Solenoid Valve | START COMPENSATION "S/C" OR "D/V" | 1830-PS07-365 | Field | 18-3601-PJB-1026 | PLC-DOx2 | - | No.2 PLC | C01
- | 18-PIA-36504AB | PLC | DIE HOLDER POLY. PRESS. | 1830-PS07-365 | CCR | - | - | - | - | C01
- | 18-PT-36504AB | Pressure Transmitter | DIE HOLDER POLY. PRESS. | 1830-PS07-365 | Field | 18-3601-PJB-1023 | PLC-AIx2 | - | No.3 PLC | C01
- | 18-TI-36504 | PLC | DIE HOLDER POLY. TEMP. | 1830-PS07-365 | CCR | - | - | - | - | C01
- | 18-TT-36504 | Temperature Transmitter | DIE HOLDER POLY. TEMP. | 1830-PS07-365 | Field | 18-3601-PJB-1023 | PLC-AI | - | No.3 PLC | C01
- | 18-TI-36506 | PLC | DIE TEMP. | 1830-PS07-365 | CCR | - | - | - | - | C01
- | 18-TT-36506 | Temperature Transmitter | DIE TEMP. | 1830-PS07-365 | Field | 18-3601-PJB-1023 | PLC-AI | - | No.3 PLC | C01
- | 18-ZSH-36507 | PROXIMITY SWITCH | PELLETIZER LOCK-RING "UNLOCK" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSH-36508 | PROXIMITY SWITCH | SPLASH COVER "OPEN" | 1830-PS07-365 | Field | 18-3601-PJB-1024 | PLC-DI | - | No.1 PLC | C01
- | 18-HY-36507 | Solenoid Valve | PELLETIZER LOCK-RING "UNLOCK" OR "LOCK" | 1830-PS07-365 | Field | 18-3601-PJB-1025 | PLC-DOx2 | - | No.2 PLC | C01
- | 18-ZSH-36611 | PROXIMITY SWITCH | PELLETIZER UNIT "REMOVE" | 1830-PS07-366 | Field | 18-3601-PJB-1033 | PLC-DI | - | No.1 PLC | C01
- | 18-ZIA-36612 | PLC | PELLETIZER BLADE POSITION | 1830-PS07-366 | CCR | - | - | - | - | C01
- | 18-ZE-36612 | PROXIMITY SENSOR | PELLETIZER BLADE POSITION | 1830-PS07-366 | Field | 18-3601-PJB-1031 | PLC-AI | - | No.3 PLC | C01
- | 18-PCV-36623 | I/P TRANSDUCER | PELLETIZER SHAFT FORWARD PRESS. CONTROL | 1830-PS07-366 | Field | 18-3601-PJB-1031 | PLC-AI | - | No.3 PLC | C01
- | 18-HY-36621 | Solenoid Valve | PELLETIZER SHAFT FORWARD PRESS. "ON" OR "OFF" | 1830-PS07-366 | Field | 18-3601-PJB-1035 | PLC-DOx2 | - | No.2 PLC | C01
- | 18-PCV-36624 | I/P TRANSDUCER | PELLETIZER SHAFT BALANCE PRESS. CONTROL | 1830-PS07-366 | Field | 18-3601-PJB-1031 | PLC-AI | - | No.3 PLC | C01
- | 18-HY-36622 | Solenoid Valve | PELLETIZER SHAFT BALANCE PRESS. "ON" OR "OFF" | 1830-PS07-366 | Field | 18-3601-PJB-1035 | PLC-DOx2 | - | No.2 PLC | C01
- | 18-PIA-36617AB | PLC | PELLETIZER UNIT CLAMP HYD. OIL PRESS. | 1830-PS07-366 | CCR | - | - | - | - | C01
- | 18-PT-36617AB | Pressure Transmitter | PELLETIZER UNIT CLAMP HYD. OIL PRESS. | 1830-PS07-366 | Field | 18-3601-PJB-1031 | PLC-AIx2 | - | No.3 PLC | C01
- | 18-HY-36617 | Solenoid Valve | PELLETIZER UNIT CLAMP "UNLOCK" | 1830-PS07-366 | Field | 18-3601-PJB-1035 | PLC-DO | - | No.2 PLC | C01
- | 18-HY-36618 | Solenoid Valve | PELLETIZER UNIT SAFETY LOCK "UNLOCK" | 1830-PS07-366 | Field | 18-3601-PJB-1035 | PLC-DO | - | No.2 PLC | C01
- | 18-PIA-36613AB | PLC | PELLETIZER UNIT CLAMBER INLET WATER PRESS. | 1830-PS07-366 | CCR | - | - | - | - | C01
- | 18-PT-36613AB | Pressure Transmitter | PELLETIZER UNIT CLAMBER INLET WATER PRESS. | 1830-PS07-366 | Field | 18-3601-PJB-1031 | PLC-AIx2 | - | No.3 PLC | C01
- | 18-TIA-36613 | PLC | PELLETIZER UNIT CLAMBER OUTLET WATER TEMP. | 1830-PS07-366 | CCR | - | - | - | - | C01
- | 18-TT-36613 | Temperature Transmitter | PELLETIZER UNIT CLAMBER OUTLET WATER TEMP. | 1830-PS07-366 | Field | 18-3601-PJB-1031 | PLC-AI | - | No.3 PLC | C01
- | 18-LSL-36614 | LEVEL SWITCH | PELLETIZER CLAMBER LEVEL "LOW" | 1830-PS07-366 | Field | 18-3601-PJB-1033 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSH-36615 | PROXIMITY SWITCH | PELLETIZER CLAMBER DRAIN VALVE "OPEN" | 1830-PS07-366 | Field | 18-3601-PJB-1033 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSL-36615 | PROXIMITY SWITCH | PELLETIZER CLAMBER DRAIN VALVE "CLOSE" | 1830-PS07-366 | Field | 18-3601-PJB-1033 | PLC-DI | - | No.1 PLC | C01
- | 18-HY-36615 | Solenoid Valve | PELLETIZER CLAMBER DRAIN VALVE "OPEN" OR "CLOSE" | 1830-PS07-366 | Field | 18-3601-PJB-1035 | PLC-DOx2 | - | No.2 PLC | C01
- | 18-ZSL-36616 | PROXIMITY SWITCH | PELLETIZER CLAMBER MANUAL VALVE "CLOSE" | 1830-PS07-366 | Field | 18-3601-PJB-1033 | PLC-DI | - | No.1 PLC | C01
- | 18-LP-36618 | - | - | 1830-PS07-366 | Field | 18-3601-PJB-1036 | PLC-DO | - | No.2 PLC | C01
- | 18-HY-36633 | Solenoid Valve | PELLETIZER CARRIAGE MOVEMENT "HIGH SPEED FORWARD" | 1830-PS07-366 | Field | 18-3601-PJB-1035 | PLC-DO | - | No.2 PLC | C01
- | 18-HY-36634 | Solenoid Valve | PELLETIZER CARRIAGE MOVEMENT "HIGH SPEED BACKWARD" | 1830-PS07-366 | Field | 18-3601-PJB-1035 | PLC-DO | - | No.2 PLC | C01
- | 18-HY-36635 | Solenoid Valve | PELLETIZER CARRIAGE AIR MOTOR CLUTCH "ON" | 1830-PS07-366 | Field | 18-3601-PJB-1035 | PLC-DO | - | No.2 PLC | C01
- | 18-TIA-36641A | PLC | PELLETIZER MOTOR WINDING TEMP. | 1830-PS07-366 | CCR | - | - | - | - | C01
- | 18-TT-36641A | Temperature Transmitter | PELLETIZER MOTOR WINDING TEMP. | 1830-PS07-366 | Field | 18-3601-PJB-1032 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-36641B | PLC | PELLETIZER MOTOR WINDING TEMP. | 1830-PS07-366 | CCR | - | - | - | - | C01
- | 18-TT-36641B | Temperature Transmitter | PELLETIZER MOTOR WINDING TEMP. | 1830-PS07-366 | Field | 18-3601-PJB-1032 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-36641C | PLC | PELLETIZER MOTOR WINDING TEMP. | 1830-PS07-366 | CCR | - | - | - | - | C01
- | 18-TT-36641C | Temperature Transmitter | PELLETIZER MOTOR WINDING TEMP. | 1830-PS07-366 | Field | 18-3601-PJB-1032 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-36642 | PLC | PELLETIZER MOTOR BEARING TEMP.(NDE) | 1830-PS07-366 | CCR | - | - | - | - | C01
- | 18-TT-36642 | Temperature Transmitter | PELLETIZER MOTOR BEARING TEMP.(NDE) | 1830-PS07-366 | Field | 18-3601-PJB-1032 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-36643 | PLC | PELLETIZER MOTOR BEARING TEMP.(DE) | 1830-PS07-366 | CCR | - | - | - | - | C01
- | 18-TT-36643 | Temperature Transmitter | PELLETIZER MOTOR BEARING TEMP.(DE) | 1830-PS07-366 | Field | 18-3601-PJB-1032 | PLC-AI | - | No.3 PLC | C01
- | 18-ZSH-37211 | PROXIMITY SWITCH | PCW 3WAY VALVE | 1830-PS07-372 | Field | 18-SP-3701X | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-ZSL-37211 | PROXIMITY SWITCH | PCW 3WAY VALVE | 1830-PS07-372 | Field | 18-SP-3701X | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-HY-37211 | Solenoid Valve | PCW 3WAY VALVE | 1830-PS07-372 | Field | 18-SP-3701X | PLC-DO | - | No.2 PLC/隔爆 | C01
- | 18-TIC-37201 | PLC | TRANSPORT WATER SYSTEM | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37201 | Temperature Transmitter | TRANSPORT WATER SYSTEM | 1830-PS07-372 | On-line | 18-300-PCW-37209-A21B-N | PLC-AI | - | No.3 PLC | C01
- | 18-TCV-37201 | CONTROL VALVE | TRANSPORT WATER SYSTEM | 1830-PS07-372 | In-line | 18-350-CWR-37101A-CA2W-N | PLC-AI | - | No.3 PLC | C01
- | 18-FIA-37201AB | PLC | TRANSPORT WATER SYSTEM | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-FT-37201AB | DIFF. PRESS.TRANSMITTER | TRANSPORT WATER SYSTEM | 1830-PS07-372 | Off-line | 18-300-PCW-37209-A21B-N | PLC-AIx2 | - | No.3 PLC | C01
- | 18-LIA-37204 | PLC | TRANSPORT WATER TANK | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-LT-37204 | DIFF. PRESS.TRANSMITTER | TRANSPORT WATER TANK | 1830-PS07-372 | Equip. | 18-VE-3701X | PLC-AI | - | No.3 PLC | C01
- | 18-LY-37204 | Solenoid Valve | TRANSPORT WATER TANK | 1830-PS07-372 | Field | 18-LV-37204 | PLC-DO | - | No.2 PLC | C01
- | 18-TIA-37211A | PLC | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37211A | Temperature Transmitter | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | Field | 18-3601-PJB-1042 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-37211B | PLC | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37211B | Temperature Transmitter | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | Field | 18-3601-PJB-1042 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-37211C | PLC | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37211C | Temperature Transmitter | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | Field | 18-3601-PJB-1042 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-37212 | PLC | PCW MOTOR BEARING NDE TEMP. | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37212 | Temperature Transmitter | PCW MOTOR BEARING NDE TEMP. | 1830-PS07-372 | Field | 18-3601-PJB-1042 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-37213 | PLC | PCW MOTOR BEARING DE TEMP. | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37213 | Temperature Transmitter | PCW MOTOR BEARING DE TEMP. | 1830-PS07-372 | Field | 18-3601-PJB-1042 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-37221A | PLC | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37221A | Temperature Transmitter | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | Field | 18-3601-PJB-1045 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-37221B | PLC | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37221B | Temperature Transmitter | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | Field | 18-3601-PJB-1045 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-37221C | PLC | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37221C | Temperature Transmitter | PCW MOTOR WINDING TEMP. | 1830-PS07-372 | Field | 18-3601-PJB-1045 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-37222 | PLC | PCW MOTOR BEARING NDE TEMP. | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37222 | Temperature Transmitter | PCW MOTOR BEARING NDE TEMP. | 1830-PS07-372 | Field | 18-3601-PJB-1045 | PLC-AI | - | No.3 PLC | C01
- | 18-TIA-37223 | PLC | PCW MOTOR BEARING DE TEMP. | 1830-PS07-372 | CCR | - | - | - | - | C01
- | 18-TT-37223 | Temperature Transmitter | PCW MOTOR BEARING DE TEMP. | 1830-PS07-372 | Field | 18-3601-PJB-1045 | PLC-AI | - | No.3 PLC | C01
- | 18-ZSH-37301 | PROXIMITY SWITCH | PCW 3WAY VALVE | 1830-PS07-373 | Field | 18-SP-3702X | PLC-DI | - | No.2 PLC/本安 | C01
- | 18-ZSL-37301 | PROXIMITY SWITCH | PCW 3WAY VALVE | 1830-PS07-373 | Field | 18-SP-3702X | PLC-DI | - | No.2 PLC/本安 | C01
- | 18-HY-37301 | Solenoid Valve | PCW 3WAY VALVE | 1830-PS07-373 | Field | 18-SP-3702X | PLC-DOx2 | - | No.3 PLC/隔爆 | C01
- | 18-ZSH-37311 | PROXIMITY SWITCH | PRESEPARATION SIEVE GATE "OPEN" | 1830-PS07-373 | Field | 18-3601-PJB-3037 | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-ZSL-37311 | PROXIMITY SWITCH | PRESEPARATION SIEVE GATE "CLOSE" | 1830-PS07-373 | Field | 18-3601-PJB-3037 | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-HY-37311 | Solenoid Valve | PRESEPARATION SIEVE GAT | 1830-PS07-373 | Field | - | PLC-DOx2 | - | No.2 PLC/隔爆 | C01
- | 18-LSH-37313 | Solenoid Valve | PRESEPARATION SIEVE LEVEL"HIGH" | 1830-PS07-373 | Field | 18-3601-PJB-3037 | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-LP-37371 | - | - | 1830-PS07-373 | Field | 18-3601-PJB-1039 | PLC-DO | - | No.2 PLC | C01
- | 18-SE-37321A | PROXIMITY SWITCH | PELLET ROTARY DRYER SPEED | 1830-PS07-373 | Field | 18-3601-PJB-3038 | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-SE-37321B | PROXIMITY SWITCH | PELLET ROTARY DRYER SPEED | 1830-PS07-373 | Field | 18-3601-PJB-3038 | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-ZSH-37351 | PROXIMITY SWITCH | PELLET DIVERTER VALVE | 1830-PS07-373 | Field | 18-SP-3703X | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-ZSL-37351 | PROXIMITY SWITCH | PELLET DIVERTER VALVE | 1830-PS07-373 | Field | 18-SP-3703X | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-HY-37351 | Solenoid Valve | PELLET DIVERTER VALVE | 1830-PS07-373 | Field | 18-SP-3703X | PLC-DOx2 | - | No.2 PLC/隔爆 | C01
- | 18-ZSH-37361 | PROXIMITY SWITCH | PELLET DIVERTER VALVE | 1830-PS07-373 | Field | 18-SP-3704X | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-ZSL-37361 | PROXIMITY SWITCH | PELLET DIVERTER VALVE | 1830-PS07-373 | Field | 18-SP-3704X | PLC-DI | - | No.1 PLC/本安 | C01
- | 18-HY-37361 | Solenoid Valve | PELLET DIVERTER VALVE | 1830-PS07-373 | Field | 18-SP-3704X | PLC-DOx2 | - | No.2 PLC/隔爆 | C01
- | 18-HS-36507 | - | PELLETIZER UNIT LOCK RING "UNLOCK" OR "LOCK" | 1830-PS07-365 | Field | 18-3601-PJB-1034 | PLC-DIx2 | - | No.1 PLC | C01
- | 18-HS-36617 | - | PELLETIZER UNIT CLAMP "UNLOCK" OR "LOCK" | 1830-PS07-366 | Field | 18-3601-PJB-1034 | PLC-DIx2 | - | No.1 PLC | C01
- | 18-HS-36618 | - | PELLETIZER UNIT CLAMP SAFETY LOCK "UNLOCK" OR "LOCK" | 1830-PS07-366 | Field | 18-3601-PJB-1034 | PLC-DIx2 | - | No.1 PLC | C01
- | 18-HS-36632 | - | PELLETIZER CARIAGE MOVEMENT "LOW" OR "HIGH" | 1830-PS07-366 | Field | 18-3601-PJB-1034 | PLC-DIx2 | - | No.1 PLC | C01
- | 18-HS-36631 | - | PELLETIZER CARIAGE MOVEMENT "FORWARD" OR "BACKWARD" | 1830-PS07-366 | Field | 18-3601-PJB-1034 | PLC-DIx2 | - | No.1 PLC | C01
- | 18-HS-36619 | - | SCOPLAMP “ON” | 1830-PS07-366 | Field | 18-3601-PJB-1034 | PLC-DI | - | No.1 PLC | C01
- | 18-ZSH-36702 | PROXIMITY SWITCH | INLET HOT OIL PUMP SUCTION VALVE "OPEN" (DIE) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-ZSH-36701A | PROXIMITY SWITCH | No.1 HOT OIL PUMP SUCTION VALVE "OPEN" (DIE) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-ZSH-36701B | PROXIMITY SWITCH | No.2 HOT OIL PUMP SUCTION VALVE "OPEN" (DIE) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-TIA-36705A | PLC | SAFETY TEMP. LIMITER (DIE) | 1830-PS07-367 | CCR | - | - | - | - | C01
- | 18-TE-36705A | Pt100 | SAFETY TEMP. LIMITER (DIE) | 1830-PS07-367 | Field | 18-3601-PJB-1051 | MCC-Pt100 | - | hold/本安 | C01
- | 18-TIA-36705B | PLC | SAFETY TEMP. LIMITER (DIE) | 1830-PS07-367 | CCR | - | - | - | - | C01
- | 18-TE-36705B | Pt100 | SAFETY TEMP. LIMITER (DIE) | 1830-PS07-367 | Field | 18-3601-PJB-1051 | MCC-Pt100 | - | hold/本安 | C01
- | 18-TIA-36726 | PLC | SAFETY TEMP. LIMITER (TANK) | 1830-PS07-367 | CCR | - | - | - | - | C01
- | 18-TE-36726 | Pt100 | SAFETY TEMP. LIMITER (TANK) | 1830-PS07-367 | Field | 18-3601-PJB-1051 | MCC-Pt100 | - | hold/- | C01
- | 18-FSL-36705A | ORIFICE &DIFF. PRESS. SWITCH | HOT OIL FLOW "LOW" (DIE) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-FSLL-36705A | ORIFICE &DIFF. PRESS. SWITCH | HOT OIL FLOW "L.LOW" (DIE) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-FSL-36705B | ORIFICE &DIFF. PRESS. SWITCH | HOT OIL FLOW "LOW" (DIE) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-FSLL-36705B | ORIFICE &DIFF. PRESS. SWITCH | HOT OIL FLOW "L.LOW" (DIE) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-FIA-36703 | PLC | HOT OIL FLOW (DIE) | 1830-PS07-367 | CCR | - | - | - | - | C01
- | 18-FT-36703 | ORIFICE &DIFF. PRESS. TRANSMITTER | HOT OIL FLOW (DIE) | 1830-PS07-367 | Off-Line | 18-3601-PJB-1052 | MCC-AI | - | hold/本安 | C01
- | 18-TIA-36703 | PLC | - | 1830-PS07-367 | CCR | - | - | - | - | C01
- | 18-TT-36703 | Temperature Transmitter | - | 1830-PS07-367 | On-Line | 18-100-HO-36702-3P2-H | PLC-AI | - | hold/隔爆 | C01
- | 18-ZSH-36712 | PROXIMITY SWITCH | INLET HOT OIL PUMP SUCTION VALVE "OPEN" (OTHERS) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-ZSH-36711A | PROXIMITY SWITCH | No.1 HOT OIL PUMP SUCTION VALVE "OPEN" (OTHERS) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-ZSH-36711B | PROXIMITY SWITCH | No.2 HOT OIL PUMP SUCTION VALVE "OPEN" (OTHERS) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-TIA-36715 | PLC | SAFETY TEMP. LIMITER (OTHERS) | 1830-PS07-367 | CCR | - | - | - | - | C01
- | 18-TE-36715 | Pt100 | SAFETY TEMP. LIMITER (OTHERS) | 1830-PS07-367 | Field | 18-3601-PJB-1051 | MCC-Pt100 | - | hold/本安 | C01
- | 18-FSL-36715 | ORIFICE &DIFF. PRESS. SWITCH | HOT OIL FLOW "LOW" (OTHERS) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-FSLL-36715 | ORIFICE &DIFF. PRESS. SWITCH | HOT OIL FLOW "L.LOW" (OTHERS) | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-FIA-36713 | PLC | HOT OIL FLOW (OTHERS) | 1830-PS07-367 | CCR | - | - | - | - | C01
- | 18-FT-36713 | ORIFICE &DIFF. PRESS. TRANSMITTER | HOT OIL FLOW (OTHERS) | 1830-PS07-367 | Off-Line | 18-3601-PJB-1052 | MCC-AI | - | hold/本安 | C01
- | 18-TIA-36713 | PLC | HOT OIL TEMP. (OTHERS) | 1830-PS07-367 | CCR | - | - | - | - | C01
- | 18-TT-36713 | Temperature Transmitter | HOT OIL TEMP. (OTHERS) | 1830-PS07-367 | On-Line | 18-3601-PJB-1052 | MCC-AI | - | hold/本安 | C01
- | 18-PIA-36721 | PLC | HOT OIL TANK N2 PRESS. | 1830-PS07-367 | CCR | - | - | - | - | C01
- | 18-PT-36721 | PRESS. TRANSMITTER | HOT OIL TANK N2 PRESS. | 1830-PS07-367 | Off-Line | 18-3601-PJB-1052 | MCC-AI | - | hold/本安 | C01
- | 18-PSH-36722 | PRESS. SWTICH | HOT OIL TANK N2 PRESS. "HIGH" | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-LSL-36722 | PRESS. SWTICH | HOT OIL TANK LEVEL "LOW" | 1830-PS07-367 | Field | 18-3601-PJB-1053 | MCC-DI | - | hold/本安 | C01
- | 18-HS-36301 | PLC | MAIN DRIVE MOTOR "START" | 1830-PS07-363 | Field | MAIN DRIVE MOTOR H.V. PANEL | PLC-DO | - | No.2 PLC | C01
- | 18-HS-36302 | PLC | MAIN DRIVE MOTOR "STOP" | 1830-PS07-363 | Field | MAIN DRIVE MOTOR H.V. PANEL | PLC-DO | - | No.2 PLC | C01
- | 18-EA-36303 | PLC | MAIN DRIVE MOTOR HV PANEL "ELECTRICAL FAULT" | 1830-PS07-363 | Field | MAIN DRIVE MOTOR H.V. PANEL | PLC-DI | - | No.1 PLC | C01
- | 18-EL-36301 | PLC | MAIN DRIVE MOTOR "RUN" | 1830-PS07-363 | Field | MAIN DRIVE MOTOR H.V. PANEL | PLC-DI | - | No.1 PLC | C01
- | 18-II-36301 | PLC | MAIN DRIVE MOTOR CURRENT | 1830-PS07-363 | Field | MAIN DRIVE MOTOR H.V. PANEL | PLC-AI | - | No.3 PLC | C01
- | 18-HS-36601 | PLC | PELLETIZER MOTOR "START" | 1830-PS07-366 | Field | PELLETIZER MOTOR VSD PANEL | PLC-DO | - | No.2 PLC | C01
- | 18-HS-36602 | PLC | PELLETIZER MOTOR "STOP" | 1830-PS07-366 | Field | PELLETIZER MOTOR VSD PANEL | PLC-DO | - | No.2 PLC | C01
- | 18-EA-36603 | PLC | PELLETIZER MOTOR VSD PANEL "ELECTRICAL FAULT" | 1830-PS07-366 | Field | PELLETIZER MOTOR VSD PANEL | PLC-DI | - | No.1 PLC | C01
- | 18-EL-36601 | PLC | PELLETIZER MOTOR "RUN" | 1830-PS07-366 | Field | PELLETIZER MOTOR VSD PANEL | PLC-DI | - | No.1 PLC | C01
- | 18-EL-36603 | PLC | PELLETIZER MOTOR VSD "READY" | 1830-PS07-366 | Field | PELLETIZER MOTOR VSD PANEL | PLC-DI | - | No.1 PLC | C01
- | 18-II-36601 | PLC | PELLETIZER MOTOR CURRENT | 1830-PS07-366 | Field | PELLETIZER MOTOR VSD PANEL | PLC-AI | - | No.3 PLC | C01
- | 18-SI-36602 | PLC | PELLETIZER MOTOR SPEED | 1830-PS07-366 | Field | PELLETIZER MOTOR VSD PANEL | PLC-AI | - | No.3 PLC | C01
- | 18-SIC-36603 | PLC | PELLETIZER MOTOR SPEED CONTROL | 1830-PS07-366 | Field | PELLETIZER MOTOR VSD PANEL | PLC-AI | - | No.3 PLC | C01
[6 empty] | Type of IO | DCS
Total DCS-AI
Total DCS-AO
Total DCS-DI
Total DCS-DO
Total SIS-AI
Total SIS-DI
Total SIS-DO
[6 empty] | Total Modbus RTU 485 | 5
Total DCS-Pt100