## DCS_IO_DB_FCS0704
AREA | PID_SHT | PID_TAG | COMMENT(Chinese) | COMMENT | FCS_COMP_NAME | FCS | NODE | SLOT | TERMINAL | MODULE | SIGNAL | DUPLEX | DIOTAG | LOOP | DCS_TAG | TYPNO | DRAWNO | TGCOMM | ENG_LO | ENG_HI | ENG_UNITS | IOADDR_SYSTAG | IO_TYPE | Wire_Type | MRP_COMP_Name | BoardModel | Board_No | Board_TB_No | Board_TB_No | Board_TB_No | TBNo. | TB A or (+) | TB B or (-) | TB C | Remarks | Source | Type | I/O | HHH | HH | H | L | LL | LLL | LOG | SOE | DCS Subfunction | Power Supply | Excitation Voltage | Drawing No. | Chinese Remark | English Remark
区域 |  | 测点编号 | 测点中文名称 | 测点英文名称 | 控制柜机柜名 | 控制器编号 | 节点编号 | 插槽编号 | 通道编号 | 卡见类型 | 信号类型 | 冗余 | 通道编号 | 回路 | DCS测点编号 | 类型 | DR图号 | 注释 | 下限 | 上限 | 单位 | 系统地址 | IO类型 | 线制 | 接线柜柜号 | 端子板类型 | 端子板编号 | 端子编号 | 端子编号 | 端子编号 | 端子编号 | 端子A编号 | 端子B编号 | 端子C编号 | 备注 | 信号来源 | 信号制 | 信号类别 | 报警 | [5 empty] | 记录 |  | DCS 子功能 | 供电方 | 励磁电压 | 图号 | 中文备注 | 英文备注
|  | 70LBA10CP101 | 主蒸汽压力1（电动阀前） | Main steam pressure 1（before MOV） | 70CRB01 | FCS0704 | 1 | 1 | 1 | AAI143-H | 4~20mA | N | %Z011101 | [5 empty] | 0 | 16 | Mpa | %Z011101 | AI |  | 70CRB03 | [5 empty] | TBB01 | 1 | 2 |  |  | 70LBA10CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-001
|  | 70LBA10CT103 | 主蒸汽电动阀前疏水阀后温度 | Temperature after turbine main steam MOV front drain valve | 70CRB01 | FCS0704 | 1 | 1 | 2 | AAI143-H | 4~20mA | N | %Z011102 | [5 empty] | 0 | 600 | ℃ | %Z011102 | AI |  | 70CRB03 | [5 empty] | TBB01 | 3 | 4 |  |  | 70LBA10CT103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-001
|  | 70LBA10CF101 | 主蒸汽流量1 | Main steam flow 1 | 70CRB01 | FCS0704 | 1 | 1 | 3 | AAI143-H | 4~20mA | N | %Z011103 | [5 empty] | 0 | 450 | t/h | %Z011103 | AI |  | 70CRB03 | [5 empty] | TBB01 | 5 | 6 |  |  | 70LBA10CF101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-001
|  | 70LBA10CF103 | 主蒸汽流量3 | Main steam flow 3 | 70CRB01 | FCS0704 | 1 | 1 | 4 | AAI143-H | 4~20mA | N | %Z011104 | [5 empty] | 0 | 450 | t/h | %Z011104 | AI |  | 70CRB03 | [5 empty] | TBB01 | 7 | 8 |  |  | 70LBA10CF103 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-001
|  | 70LBR20CT106 | 主蒸汽减温减压(B)后蒸汽温度 | Steam temperature after main steam temperature and pressure reduction(B) | 70CRB01 | FCS0704 | 1 | 1 | 5 | AAI143-H | 4~20mA | N | %Z011105 | [5 empty] | 0 | 300 | ℃ | %Z011105 | AI |  | 70CRB03 | [5 empty] | TBB01 | 9 | 10 |  |  | 70LBR20CT106 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-002
|  | 70LBQ20CP105 | 主蒸汽减温减压(A)后蒸汽压力 | Steam pressure after main steam temperature and pressure reduction(A) | 70CRB01 | FCS0704 | 1 | 1 | 6 | AAI143-H | 4~20mA | N | %Z011106 | [5 empty] | 0 | 2 | MPa | %Z011106 | AI |  | 70CRB03 | [5 empty] | TBB01 | 11 | 12 |  |  | 70LBQ20CP105 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-005
|  | 70LBQ20CT112 | 主蒸汽中压旁路管道电动阀后疏水温度 | Drain temperature after main steam MP bypass pipe MOV | 70CRB01 | FCS0704 | 1 | 1 | 7 | AAI143-H | 4~20mA | N | %Z011107 | [5 empty] | 0 | 300 | ℃ | %Z011107 | AI |  | 70CRB03 | [5 empty] | TBB01 | 13 | 142 |  |  | 70LBQ20CT112 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70MKA75CE101A | 发电机漏液检测1 | Generator leakage detection 1 | 70CRB01 | FCS0704 | 1 | 1 | 8 | AAI143-H | 4~20mA | N | %Z011108 | [5 empty] | 0 | 500 | MΩ | %Z011108 | AI |  | 70CRB03 | [5 empty] | TBB01 | 15 | 16 |  |  | 70MKA20GH001 | 4～20mA | AI | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA75CE101C | 发电机漏液检测3 | Generator leakage detection 3 | 70CRB01 | FCS0704 | 1 | 1 | 9 | AAI143-H | 4~20mA | N | %Z011109 | [5 empty] | 0 | 500 | MΩ | %Z011109 | AI |  | 70CRB03 | [5 empty] | TBB01 | 17 | 18 |  |  | 70MKA20GH001 | 4～20mA | AI | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70LBA10CT104 | 汽机(左)进汽管道疏水阀后温度 | Temperature after turbine(left) main steam inlet pipe drain valve | 70CRB01 | FCS0704 | 1 | 1 | 10 | AAI143-H | 4~20mA | N | %Z011110 | [5 empty] | 0 | 600 | ℃ | %Z011110 | AI |  | 70CRB03 | [5 empty] | TBB01 | 19 | 20 |  |  | 70LBA10CT104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-001
|  | 70LBA20CT101 | 减温减压器A前疏水阀后温度 | Temperature after desuperheater A front drain valve | 70CRB01 | FCS0704 | 1 | 1 | 11 | AAI143-H | 4~20mA | N | %Z011111 | [5 empty] | 0 | 600 | ℃ | %Z011111 | AI |  | 70CRB03 | [5 empty] | TBB01 | 21 | 22 |  |  | 70LBA20CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-001
|  | 70MAA50CP111 | #2级调整抽汽压力#5 | #2 regulated extraction steam pressure #5 | 70CRB01 | FCS0704 | 1 | 1 | 12 | AAI143-H | 4~20mA | N | %Z011112 | [5 empty] | 0 | 1.6 | MPa | %Z011112 | AI |  | 70CRB03 | [5 empty] | TBB01 | 23 | 24 |  |  | 70MAA50CP111 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70MAA50CT127 | #2级调整抽汽温度#3 | #2 regulated extraction steam temperature #3 | 70CRB01 | FCS0704 | 1 | 1 | 13 | AAI143-H | 4~20mA | N | %Z011113 | [5 empty] | 0 | 300 | ℃ | %Z011113 | AI |  | 70CRB03 | [5 empty] | TBB01 | 25 | 26 |  |  | 70MAA50CT127 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
[5 empty] | 70CRB01 | FCS0704 | 1 | 1 | 14 | AAI143-H | 4~20mA | N | %Z011114 | [8 empty] | %Z011114 | AI |  | 70CRB03 | [5 empty] | TBB01 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 1 | 1 | 15 | AAI143-H | 4~20mA | N | %Z011115 | [8 empty] | %Z011115 | AI |  | 70CRB03 | [5 empty] | TBB01 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 1 | 1 | 16 | AAI143-H | 4~20mA | N | %Z011116 | [8 empty] | %Z011116 | AI |  | 70CRB03 | [5 empty] | TBB01 | 31 | 32
|  | 70LBA10CP102 | 主蒸汽压力2（电动阀前） | Main steam pressure 2（before MOV） | 70CRB01 | FCS0704 | 1 | 2 | 1 | AAI143-H | 4~20mA | N | %Z012101 | [5 empty] | 0 | 16 | Mpa | %Z012101 | AI |  | 70CRB03 | [5 empty] | TBB02 | 1 | 2 |  |  | 70LBA10CP102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-001
|  | A0LBA10CT101 | 主蒸汽联络管疏水阀后温度 | Temperature after main steam contact pipe drain valve | 70CRB01 | FCS0704 | 1 | 2 | 2 | AAI143-H | 4~20mA | N | %Z012102 | [5 empty] | 0 | 600 | ℃ | %Z012102 | AI |  | 70CRB03 | [5 empty] | TBB02 | 3 | 4 |  |  | A0LBA10CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-001
|  | 70LBA10CF102 | 主蒸汽流量2 | Main steam flow 2 | 70CRB01 | FCS0704 | 1 | 2 | 3 | AAI143-H | 4~20mA | N | %Z012103 | [5 empty] | 0 | 450 | t/h | %Z012103 | AI |  | 70CRB03 | [5 empty] | TBB02 | 5 | 6 |  |  | 70LBA10CF102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-001
|  | 70LBR20CP102 | 主蒸汽减温减压(B)后蒸汽压力 | Steam pressure after main steam temperature and pressure reduction(B) | 70CRB01 | FCS0704 | 1 | 2 | 4 | AAI143-H | 4~20mA | N | %Z012104 | [5 empty] | 0 | 0.8 | MPa | %Z012104 | AI |  | 70CRB03 | [5 empty] | TBB02 | 7 | 8 |  |  | 70LBR20CP102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-002
|  | 70LBR20CT105 | 主蒸汽低压旁路管道电动阀后疏水温度 | Drain temperature after main steam LP bypass pipe MOV | 70CRB01 | FCS0704 | 1 | 2 | 5 | AAI143-H | 4~20mA | N | %Z012105 | [5 empty] | 0 | 300 | ℃ | %Z012105 | AI |  | 70CRB03 | [5 empty] | TBB02 | 9 | 10 |  |  | 70LBR20CT105 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBQ20CT111 | 主蒸汽减温减压(A)后蒸汽温度 | Steam temperature after main steam temperature and pressure reduction(A) | 70CRB01 | FCS0704 | 1 | 2 | 6 | AAI143-H | 4~20mA | N | %Z012106 | [5 empty] | 0 | 300 | ℃ | %Z012106 | AI |  | 70CRB03 | [5 empty] | TBB02 | 11 | 12 |  |  | 70LBQ20CT111 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-005
|  | 70MKA75CE101B | 发电机漏液检测2 | Generator leakage detection 2 | 70CRB01 | FCS0704 | 1 | 2 | 7 | AAI143-H | 4~20mA | N | %Z012107 | [5 empty] | 0 | 500 | MΩ | %Z012107 | AI |  | 70CRB03 | [5 empty] | TBB02 | 13 | 142 |  |  | 70MKA20GH001 | 4～20mA | AI | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA75CE101D | 发电机漏液检测4 | Generator leakage detection 4 | 70CRB01 | FCS0704 | 1 | 2 | 8 | AAI143-H | 4~20mA | N | %Z012108 | [5 empty] | 0 | 500 | MΩ | %Z012108 | AI |  | 70CRB03 | [5 empty] | TBB02 | 15 | 16 |  |  | 70MKA20GH001 | 4～20mA | AI | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70LBA11CP102 | 主汽门(左)前蒸汽压力2 | Steam pressure before MSV(left) | 70CRB01 | FCS0704 | 1 | 2 | 9 | AAI143-H | 4~20mA | N | %Z012109 | [5 empty] | 0 | 16 | Mpa | %Z012109 | AI |  | 70CRB03 | [5 empty] | TBB02 | 17 | 18 |  |  | 70LBA11CP102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-001
|  | 70LBA10CT105 | 汽机(右)进汽管道疏水阀后温度 | Temperature after turbine(right) main steam inlet pipe drain valve | 70CRB01 | FCS0704 | 1 | 2 | 10 | AAI143-H | 4~20mA | N | %Z012110 | [5 empty] | 0 | 600 | ℃ | %Z012110 | AI |  | 70CRB03 | [5 empty] | TBB02 | 19 | 20 |  |  | 70LBA10CT105 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-001
|  | 70LBA20CT102 | 减温减压器B前疏水阀后温度 | Temperature after desuperheater B front drain valve | 70CRB01 | FCS0704 | 1 | 2 | 11 | AAI143-H | 4~20mA | N | %Z012111 | [5 empty] | 0 | 600 | ℃ | %Z012111 | AI |  | 70CRB03 | [5 empty] | TBB02 | 21 | 22 |  |  | 70LBA20CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-001
|  | 70MAA50CP112 | #2级调整抽汽压力#6 | #2 regulated extraction steam pressure #6 | 70CRB01 | FCS0704 | 1 | 2 | 12 | AAI143-H | 4~20mA | N | %Z012112 | [5 empty] | 0 | 1.6 | MPa | %Z012112 | AI |  | 70CRB03 | [5 empty] | TBB02 | 23 | 24 |  |  | 70MAA50CP112 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70MAA50CT128 | #2级调整抽汽温度#4 | #2 regulated extraction steam temperature #4 | 70CRB01 | FCS0704 | 1 | 2 | 13 | AAI143-H | 4~20mA | N | %Z012113 | [5 empty] | 0 | 300 | ℃ | %Z012113 | AI |  | 70CRB03 | [5 empty] | TBB02 | 25 | 26 |  |  | 70MAA50CT128 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
[5 empty] | 70CRB01 | FCS0704 | 1 | 2 | 14 | AAI143-H | 4~20mA | N | %Z012114 | [8 empty] | %Z012114 | AI |  | 70CRB03 | [5 empty] | TBB02 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 1 | 2 | 15 | AAI143-H | 4~20mA | N | %Z012115 | [8 empty] | %Z012115 | AI |  | 70CRB03 | [5 empty] | TBB02 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 1 | 2 | 16 | AAI143-H | 4~20mA | N | %Z012116 | [8 empty] | %Z012116 | AI |  | 70CRB03 | [5 empty] | TBB02 | 31 | 32
|  | 70MAX01CL101 | EH油箱油位 | EH oil tank oil level | 70CRB01 | FCS0704 | 2 | 1 | 1 | AAI143-H | 4~20mA | N | %Z021101 | [5 empty] | 0 | 1 | m | %Z021101 | AI |  | 70CRB03 | [5 empty] | TBB03 | 1 | 2 |  |  | 70MAX01GC001 | 4～20mA | AI | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAX01CP101 | 1#EH油泵出口油压 | 1# EH oil pump outlet oil Pressure | 70CRB01 | FCS0704 | 2 | 1 | 2 | AAI143-H | 4~20mA | N | %Z021102 | [5 empty] | 0 | 25 | Mpa | %Z021102 | AI |  | 70CRB03 | [5 empty] | TBB03 | 3 | 4 |  |  | 70MAX01GC001 | 4～20mA | AI | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70LBQ10CP101 | 1#抽汽蒸汽压力 | 1# extraction steam pressure | 70CRB01 | FCS0704 | 2 | 1 | 3 | AAI143-H | 4~20mA | N | %Z021103 | [5 empty] | 0 | 4 | MPa | %Z021103 | AI |  | 70CRB03 | [5 empty] | TBB03 | 5 | 6 |  |  | 70LBQ10CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBQ10CT101 | 1#抽汽蒸汽温度 | 1# extraction steam temperature | 70CRB01 | FCS0704 | 2 | 1 | 4 | AAI143-H | 4~20mA | N | %Z021104 | [5 empty] | 0 | 400 | ℃ | %Z021104 | AI |  | 70CRB03 | [5 empty] | TBB03 | 7 | 8 |  |  | 70LBQ10CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBQ10CT102 | 1#抽汽逆止阀后管顶温度 | Top temperature of pipe after 1# extraction steam check valve | 70CRB01 | FCS0704 | 2 | 1 | 5 | AAI143-H | 4~20mA | N | %Z021105 | [5 empty] | 0 | 400 | ℃ | %Z021105 | AI |  | 70CRB03 | [5 empty] | TBB03 | 9 | 10 |  |  | 70LBQ10CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBR20CT101 | #2级调整抽汽逆止阀后管顶温度 | Top temperature of pipe after #2 regulated extraction steam check valve | 70CRB01 | FCS0704 | 2 | 1 | 6 | AAI143-H | 4~20mA | N | %Z021106 | [5 empty] | 0 | 300 | ℃ | %Z021106 | AI |  | 70CRB03 | [5 empty] | TBB03 | 11 | 12 |  |  | 70LBR20CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CT103 | #2级调整抽汽逆止阀后疏水温度 | Drain temperature after #2 regulated extraction steam check valve | 70CRB01 | FCS0704 | 2 | 1 | 7 | AAI143-H | 4~20mA | N | %Z021107 | [5 empty] | 0 | 300 | ℃ | %Z021107 | AI |  | 70CRB03 | [5 empty] | TBB03 | 13 | 142 |  |  | 70LBR20CT103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CT104 | #2级调整抽汽减温减压(D)后蒸汽温度 | Steam temperature after #2 regulated extraction steam temperature and pressure reduction(D) | 70CRB01 | FCS0704 | 2 | 1 | 8 | AAI143-H | 4~20mA | N | %Z021108 | [5 empty] | 0 | 300 | ℃ | %Z021108 | AI |  | 70CRB03 | [5 empty] | TBB03 | 15 | 16 |  |  | 70LBR20CT104 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-002
|  | 70MAW10CL101 | 轴封冷却器液位 | Gland steam condenser level | 70CRB01 | FCS0704 | 2 | 1 | 9 | AAI143-H | 4~20mA | N | %Z021109 | [5 empty] | 0 |  | m | %Z021109 | AI |  | 70CRB03 | [5 empty] | TBB03 | 17 | 18 |  |  | 70MAW10CL101 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-012
|  | 70GHC20CT101 | 冷渣机入口冷却水温度 | Slag cooler inlet cooling water temperature | 70CRB01 | FCS0704 | 2 | 1 | 10 | AAI143-H | 4~20mA | N | %Z021110 | [5 empty] | 0 | 100 | ℃ | %Z021110 | AI |  | 70CRB03 | [5 empty] | TBB03 | 19 | 20 |  |  | 70GHC20CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-015
|  | 70MAW10CP101 | 汽封母管供汽压力1 | Gland seal main steam pressure 1 | 70CRB01 | FCS0704 | 2 | 1 | 11 | AAI143-H | 4~20mA | N | %Z021111 | [5 empty] | -10 | 90 | mbar | %Z021111 | AI |  | 70CRB03 | [5 empty] | TBB03 | 21 | 22 |  |  | 70MAW10CP101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-016
|  | 70MAL19CT101 | 调节级前疏水阀(左)后温度 | Temperature after drain valve before djusting stage(left) | 70CRB01 | FCS0704 | 2 | 1 | 12 | AAI143-H | 4~20mA | N | %Z021112 | [5 empty] | 0 | 600 | ℃ | %Z021112 | AI |  | 70CRB03 | [5 empty] | TBB03 | 23 | 24 |  |  | 70MAL19CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-017
|  | 70MAL22CT101 | 调节级后疏水阀后温度 | Temperature after drain valve after djusting stage | 70CRB01 | FCS0704 | 2 | 1 | 13 | AAI143-H | 4~20mA | N | %Z021113 | [5 empty] | 0 | 600 | ℃ | %Z021113 | AI |  | 70CRB03 | [5 empty] | TBB03 | 25 | 26 |  |  | 70MAL22CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 2 | 1 | 14 | AAI143-H | 4~20mA | N | %Z021114 | [8 empty] | %Z021114 | AI |  | 70CRB03 | [5 empty] | TBB03 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 2 | 1 | 15 | AAI143-H | 4~20mA | N | %Z021115 | [8 empty] | %Z021115 | AI |  | 70CRB03 | [5 empty] | TBB03 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 2 | 1 | 16 | AAI143-H | 4~20mA | N | %Z021116 | [8 empty] | %Z021116 | AI |  | 70CRB03 | [5 empty] | TBB03 | 31 | 32
|  | 70LBQ10CT103 | 1#抽汽逆止阀后管底温度 | Bottom temperature of pipe after 1# extraction steam check valve | 70CRB01 | FCS0704 | 2 | 2 | 1 | AAI143-H | 4~20mA | N | %Z022101 | [5 empty] | 0 | 400 | ℃ | %Z022101 | AI |  | 70CRB03 | [5 empty] | TBB04 | 1 | 2 |  |  | 70LBQ10CT103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBQ10CT104 | 1#抽汽逆止阀后疏水温度 | Drain temperature after 1# extraction steam check valve | 70CRB01 | FCS0704 | 2 | 2 | 2 | AAI143-H | 4~20mA | N | %Z022102 | [5 empty] | 0 | 400 | ℃ | %Z022102 | AI |  | 70CRB03 | [5 empty] | TBB04 | 3 | 4 |  |  | 70LBQ10CT104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70MAL41CT101 | 1#抽汽逆止阀前疏水阀后温度 | Temperature after drain valve before 1# extraction steam check valve | 70CRB01 | FCS0704 | 2 | 2 | 3 | AAI143-H | 4~20mA | N | %Z022103 | [5 empty] | 0 | 400 | ℃ | %Z022103 | AI |  | 70CRB03 | [5 empty] | TBB04 | 5 | 6 |  |  | 70MAL41CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-017
|  | 70LBR20CT102 | #2级调整抽汽逆止阀后管底温度 | Bottom temperature of pipe after #2 regulated extraction steam check valve | 70CRB01 | FCS0704 | 2 | 2 | 4 | AAI143-H | 4~20mA | N | %Z022104 | [5 empty] | 0 | 300 | ℃ | %Z022104 | AI |  | 70CRB03 | [5 empty] | TBB04 | 7 | 8 |  |  | 70LBR20CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CP101 | #2级调整抽汽减温减压(D)后蒸汽压力 | Steam pressure after #2 regulated extraction steam temperature and pressure reduction(D) | 70CRB01 | FCS0704 | 2 | 2 | 5 | AAI143-H | 4~20mA | N | %Z022105 | [5 empty] | 0 | 0.8 | MPa | %Z022105 | AI |  | 70CRB03 | [5 empty] | TBB04 | 9 | 10 |  |  | 70LBR20CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CF101 | #2级调整抽汽减温减压(D)后蒸汽流量 | Steam flow after #2 regulated extraction steam temperature and pressure reduction(D) | 70CRB01 | FCS0704 | 2 | 2 | 6 | AAI143-H | 4~20mA | N | %Z022106 | [5 empty] | 0 | 140 | t/h | %Z022106 | AI |  | 70CRB03 | [5 empty] | TBB04 | 11 | 12 |  |  | 70LBR20CF101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-002
|  | 70LBR20CT109 | #2级调整抽汽电动阀后疏水温度 | Drain temperature after #2 regulated extraction steam MOV | 70CRB01 | FCS0704 | 2 | 2 | 7 | AAI143-H | 4~20mA | N | %Z022107 | [5 empty] | 0 | 300 | ℃ | %Z022107 | AI |  | 70CRB03 | [5 empty] | TBB04 | 13 | 142 |  |  | 70LBR20CT109 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CF102 | 低压联箱进汽母管蒸汽流量 | LP steam header inlet main pipe steam flow | 70CRB01 | FCS0704 | 2 | 2 | 8 | AAI143-H | 4~20mA | N | %Z022108 | [5 empty] | 0 | 140 | t/h | %Z022108 | AI |  | 70CRB03 | [5 empty] | TBB04 | 15 | 16 |  |  | 70LBR20CF102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CP104 | 低压联箱蒸汽压力 | LP steam header steam pressure | 70CRB01 | FCS0704 | 2 | 2 | 9 | AAI143-H | 4~20mA | N | %Z022109 | [5 empty] | 0 | 1 | MPa | %Z022109 | AI |  | 70CRB03 | [5 empty] | TBB04 | 17 | 18 |  |  | 70LBR20CP104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CF105 | 低压联箱至老厂#1机组低压蒸汽管道供热蒸汽流量 | LP steam header to existing LP steam line of #1 unit heating steam flow | 70CRB01 | FCS0704 | 2 | 2 | 10 | AAI143-H | 4~20mA | N | %Z022110 | [5 empty] | 0 | 70 | t/h | %Z022110 | AI |  | 70CRB03 | [5 empty] | TBB04 | 19 | 20 |  |  | 70LBR20CF105 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CF106 | 低压联箱至老厂#2机组低压蒸汽管道供热蒸汽流量 | LP steam header to existing LP steam line of #2 unit heating steam flow | 70CRB01 | FCS0704 | 2 | 2 | 11 | AAI143-H | 4~20mA | N | %Z022111 | [5 empty] | 0 | 70 | t/h | %Z022111 | AI |  | 70CRB03 | [5 empty] | TBB04 | 21 | 22 |  |  | 70LBR20CF106 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70GHC30CT101 | 冷渣机出口冷却水温度 | Slag cooler outlet cooling water temperature | 70CRB01 | FCS0704 | 2 | 2 | 12 | AAI143-H | 4~20mA | N | %Z022112 | [5 empty] | 0 | 100 | ℃ | %Z022112 | AI |  | 70CRB03 | [5 empty] | TBB04 | 23 | 24 |  |  | 70GHC30CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-015
|  | 70GHC30CF101 | 冷渣机出口冷却水回水流量 | Slag cooler outlet cooling water returning flow | 70CRB01 | FCS0704 | 2 | 2 | 13 | AAI143-H | 4~20mA | N | %Z022113 | [5 empty] | 0 | 150 | t/h | %Z022113 | AI |  | 70CRB03 | [5 empty] | TBB04 | 25 | 26 |  |  | 70GHC30CF101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-015
|  | 70MAW10CP102 | 汽封母管供汽压力2 | Gland seal main steam pressure 2 | 70CRB01 | FCS0704 | 2 | 2 | 14 | AAI143-H | 4~20mA | N | %Z022114 | [5 empty] | -10 | 90 | mbar | %Z022114 | AI |  | 70CRB03 | [5 empty] | TBB04 | 27 | 28 |  |  | 70MAW10CP102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-016
[5 empty] | 70CRB01 | FCS0704 | 2 | 2 | 15 | AAI143-H | 4~20mA | N | %Z022115 | [8 empty] | %Z022115 | AI |  | 70CRB03 | [5 empty] | TBB04 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 2 | 2 | 16 | AAI143-H | 4~20mA | N | %Z022116 | [8 empty] | %Z022116 | AI |  | 70CRB03 | [5 empty] | TBB04 | 31 | 32
|  | 70MAV21AP021XQ01 | 1#主油泵电流 | 1# main oil pump current | 70CRB01 | FCS0704 | 2 | 3 | 1 | AAI143-H | 4~20mA | N | %Z023101 | [7 empty] | A | %Z023101 | AI | 4W | 70CRB03 | [5 empty] | TBB05 | 2 | 1 |  |  | 70MAV21AP021 | 4～20mA | AI | [8 empty] | DAS | U |  | K0203-005
|  | 70MAX01AP001XQ01 | 1# EH油泵电流 | 1# EH oil pump current | 70CRB01 | FCS0704 | 2 | 3 | 2 | AAI143-H | 4~20mA | N | %Z023102 | [7 empty] | A | %Z023102 | AI | 4W | 70CRB03 | [5 empty] | TBB05 | 4 | 3 |  |  | 70MAX01GH001 | 4～20mA | AI | [8 empty] | DAS | U |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70CJJ01YQ04 | 负荷设定值 | Load setpoint | 70CRB01 | FCS0704 | 2 | 3 | 3 | AAI143-H | 4~20mA | N | %Z023103 | [7 empty] | MW | %Z023103 | AI | 4W | 70CRB03 | [5 empty] | TBB05 | 6 | 5 |  |  | 70CJJ01 | 4～20mA | AI | [8 empty] | MCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
|  | 70CJJ01YQ05 | 实际功率 | Actual load | 70CRB01 | FCS0704 | 2 | 3 | 4 | AAI143-H | 4~20mA | N | %Z023104 | [7 empty] | MW | %Z023104 | AI | 4W | 70CRB03 | [5 empty] | TBB05 | 8 | 7 |  |  | 70CJJ01 | 4～20mA | AI | [8 empty] | MCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
|  | 70CJJ01YQ06 | 实际转速 | Actual speed | 70CRB01 | FCS0704 | 2 | 3 | 5 | AAI143-H | 4~20mA | N | %Z023105 | [5 empty] | 0 | 3500 | rpm | %Z023105 | AI | 4W | 70CRB03 | [5 empty] | TBB05 | 10 | 9 |  |  | 70CJJ01 | 4～20mA | AI | [8 empty] | MCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
|  | 70LBR20CT107 | 低压联箱进汽母管蒸汽温度 | LP steam header inlet main pipe steam temperature | 70CRB01 | FCS0704 | 2 | 3 | 6 | AAI143-H | 4~20mA | N | %Z023106 | [5 empty] | 0 | 300 | ℃ | %Z023106 | AI |  | 70CRB03 | [5 empty] | TBB05 | 11 | 12 |  |  | 70LBR20CT107 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CP103 | 低压联箱进汽母管蒸汽压力 | LP steam header inlet main pipe steam pressure | 70CRB01 | FCS0704 | 2 | 3 | 7 | AAI143-H | 4~20mA | N | %Z023107 | [5 empty] | 0 | 0.8 | MPa | %Z023107 | AI |  | 70CRB03 | [5 empty] | TBB05 | 13 | 142 |  |  | 70LBR20CP103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CF103 | 低压联箱至老厂#6机组低压蒸汽管道供热蒸汽流量 | LP steam header to existing LP steam line of #6 unit heating steam flow | 70CRB01 | FCS0704 | 2 | 3 | 8 | AAI143-H | 4~20mA | N | %Z023108 | [5 empty] | 0 | 70 | t/h | %Z023108 | AI |  | 70CRB03 | [5 empty] | TBB05 | 15 | 16 |  |  | 70LBR20CF103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70LBR20CF104 | 低压联箱至老厂#3机组低压蒸汽管道供热蒸汽流量 | LP steam header to existing LP steam line of #3 unit heating steam flow | 70CRB01 | FCS0704 | 2 | 3 | 9 | AAI143-H | 4~20mA | N | %Z023109 | [5 empty] | 0 | 70 | t/h | %Z023109 | AI |  | 70CRB03 | [5 empty] | TBB05 | 17 | 18 |  |  | 70LBR20CF104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-002
|  | 70MAL21CT101 | 调节级前疏水阀(右)后温度 | Temperature after drain valve before djusting stage(right) | 70CRB01 | FCS0704 | 2 | 3 | 10 | AAI143-H | 4~20mA | N | %Z023110 | [5 empty] | 0 | 600 | ℃ | %Z023110 | AI |  | 70CRB03 | [5 empty] | TBB05 | 19 | 20 |  |  | 70MAL21CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-017
|  | 70MAL14CT101 | 主调门阀前疏水阀后温度 | Temperature after drain valve before GV | 70CRB01 | FCS0704 | 2 | 3 | 11 | AAI143-H | 4~20mA | N | %Z023111 | [5 empty] | 0 | 600 | ℃ | %Z023111 | AI |  | 70CRB03 | [5 empty] | TBB05 | 21 | 22 |  |  | 70MAL14CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-017
|  | 70MAL46CT101 | 蒸汽室疏水阀后温度 | Temperature after steam chamber drain valve | 70CRB01 | FCS0704 | 2 | 3 | 12 | AAI143-H | 4~20mA | N | %Z023112 | [5 empty] | 0 | 300 | ℃ | %Z023112 | AI |  | 70CRB03 | [5 empty] | TBB05 | 23 | 24 |  |  | 70MAL46CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-017
|  | 70MAL45CT101 | #2级调整抽汽逆止阀前和各插管母管疏水阀后温度 | Temperature after drain valve before #2 adjusting extraction steam check valve and intubation pipe | 70CRB01 | FCS0704 | 2 | 3 | 13 | AAI143-H | 4~20mA | N | %Z023113 | [5 empty] | 0 | 300 | ℃ | %Z023113 | AI |  | 70CRB03 | [5 empty] | TBB05 | 25 | 26 |  |  | 70MAL45CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 2 | 3 | 14 | AAI143-H | 4~20mA | N | %Z023114 | [8 empty] | %Z023114 | AI |  | 70CRB03 | [5 empty] | TBB05 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 2 | 3 | 15 | AAI143-H | 4~20mA | N | %Z023115 | [8 empty] | %Z023115 | AI |  | 70CRB03 | [5 empty] | TBB05 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 2 | 3 | 16 | AAI143-H | 4~20mA | N | %Z023116 | [8 empty] | %Z023116 | AI |  | 70CRB03 | [5 empty] | TBB05 | 31 | 32
|  | 70MAV31CP101 | 1#顶轴油泵出口压力 | 1# jacking oil pump outlet pressure | 70CRB01 | FCS0704 | 3 | 1 | 1 | AAI143-H | 4~20mA | N | %Z031101 | [5 empty] | 0 | 25 | Mpa | %Z031101 | AI |  | 70CRB03 | [5 empty] | TBC01 | 1 | 2 |  |  | 70MAV01GC001 | 4～20mA | AI | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV35CP101 | 顶轴油泵母管出口压力 | Jacking oil pump main outlet pressure | 70CRB01 | FCS0704 | 3 | 1 | 2 | AAI143-H | 4~20mA | N | %Z031102 | [5 empty] | 0 | 25 | Mpa | %Z031102 | AI |  | 70CRB03 | [5 empty] | TBC01 | 3 | 4 |  |  | 70MAV01GC001 | 4～20mA | AI | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAX01CP102 | 2#EH油泵出口油压 | 2# EH oil pump outlet oil Pressure | 70CRB01 | FCS0704 | 3 | 1 | 3 | AAI143-H | 4~20mA | N | %Z031103 | [5 empty] | 0 | 25 | Mpa | %Z031103 | AI |  | 70CRB03 | [5 empty] | TBC01 | 5 | 6 |  |  | 70MAX01GC001 | 4～20mA | AI | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAX01CP103 | EH油泵出口母管油压 | EH oil pump outlet main pipe oil pressure | 70CRB01 | FCS0704 | 3 | 1 | 4 | AAI143-H | 4~20mA | N | %Z031104 | [5 empty] | 0 | 25 | Mpa | %Z031104 | AI |  | 70CRB03 | [5 empty] | TBC01 | 7 | 8 |  |  | 70MAX01GC001 | 4～20mA | AI | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70LBQ20CP101 | 2#抽汽蒸汽压力 | 2# extraction steam pressure | 70CRB01 | FCS0704 | 3 | 1 | 5 | AAI143-H | 4~20mA | N | %Z031105 | [5 empty] | 0 | 2.5 | MPa | %Z031105 | AI |  | 70CRB03 | [5 empty] | TBC01 | 9 | 10 |  |  | 70LBQ20CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CT101 | 2#抽汽蒸汽温度 | 2# extraction steam temperature | 70CRB01 | FCS0704 | 3 | 1 | 6 | AAI143-H | 4~20mA | N | %Z031106 | [5 empty] | 0 | 400 | ℃ | %Z031106 | AI |  | 70CRB03 | [5 empty] | TBC01 | 11 | 12 |  |  | 70LBQ20CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CT102 | 2#抽汽逆止阀后管顶温度 | Top temperature of pipe after 2# extraction steam check valve | 70CRB01 | FCS0704 | 3 | 1 | 7 | AAI143-H | 4~20mA | N | %Z031107 | [5 empty] | 0 | 400 | ℃ | %Z031107 | AI |  | 70CRB03 | [5 empty] | TBC01 | 13 | 142 |  |  | 70LBQ20CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70GNR10CQ101 | 机组排水槽pH | Unit drain pit pH | 70CRB01 | FCS0704 | 3 | 1 | 8 | AAI143-H | 4~20mA | N | %Z031108 | [5 empty] | 0 | 14 |  | %Z031108 | AI |  | 70CRB03 | [5 empty] | TBC01 | 15 | 16 |  |  | 70GNR10CQ101 | 4~20mA | AI | [8 empty] | DAS | U |  | K0607-001
|  | 70GNR10CP101 | 机组排水槽废水泵出口母管压力 | Unit drain pit waste water pump outlet main pipe pressure | 70CRB01 | FCS0704 | 3 | 1 | 9 | AAI143-H | 4~20mA | N | %Z031109 | [5 empty] | 0 | 0.6 | Mpa | %Z031109 | AI |  | 70CRB03 | [5 empty] | TBC01 | 17 | 18 |  |  | 70GNR10CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0607-001
|  | 70LCA30CT102 | 轴封冷却器出口水温 | Gland steam condenser outlet temperature | 70CRB01 | FCS0704 | 3 | 1 | 10 | AAI143-H | 4~20mA | N | %Z031110 | [5 empty] | 0 | 200 | ℃ | %Z031110 | AI |  | 70CRB03 | [5 empty] | TBC01 | 19 | 20 |  |  | 70LCA30CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-008
[5 empty] | 70CRB01 | FCS0704 | 3 | 1 | 11 | AAI143-H | 4~20mA | N | %Z031111 | [8 empty] | %Z031111 | AI |  | 70CRB03 | [5 empty] | TBC01 | 21 | 22
[5 empty] | 70CRB01 | FCS0704 | 3 | 1 | 12 | AAI143-H | 4~20mA | N | %Z031112 | [8 empty] | %Z031112 | AI |  | 70CRB03 | [5 empty] | TBC01 | 23 | 24
[5 empty] | 70CRB01 | FCS0704 | 3 | 1 | 13 | AAI143-H | 4~20mA | N | %Z031113 | [8 empty] | %Z031113 | AI |  | 70CRB03 | [5 empty] | TBC01 | 25 | 26
[5 empty] | 70CRB01 | FCS0704 | 3 | 1 | 14 | AAI143-H | 4~20mA | N | %Z031114 | [8 empty] | %Z031114 | AI |  | 70CRB03 | [5 empty] | TBC01 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 3 | 1 | 15 | AAI143-H | 4~20mA | N | %Z031115 | [8 empty] | %Z031115 | AI |  | 70CRB03 | [5 empty] | TBC01 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 3 | 1 | 16 | AAI143-H | 4~20mA | N | %Z031116 | [8 empty] | %Z031116 | AI |  | 70CRB03 | [5 empty] | TBC01 | 31 | 32
|  | 70MAV32CP101 | 2#顶轴油泵出口压力 | 2# jacking oil pump outlet pressure | 70CRB01 | FCS0704 | 3 | 2 | 1 | AAI143-H | 4~20mA | N | %Z032101 | [5 empty] | 0 | 25 | Mpa | %Z032101 | AI |  | 70CRB03 | [5 empty] | TBC02 | 1 | 2 |  |  | 70MAV01GC001 | 4～20mA | AI | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV82CP101 | 排油烟管道压力 | Oil mist exhaust pressure | 70CRB01 | FCS0704 | 3 | 2 | 2 | AAI143-H | 4~20mA | N | %Z032102 | [5 empty] | 0 | 0.6 | Mpa | %Z032102 | AI |  | 70CRB03 | [5 empty] | TBC02 | 3 | 4 |  |  | 70MAV01GC001 | 4～20mA | AI | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70LBQ20CT103 | 2#抽汽逆止阀后管底温度 | Bottom temperature of pipe after 2# extraction steam check valve | 70CRB01 | FCS0704 | 3 | 2 | 3 | AAI143-H | 4~20mA | N | %Z032103 | [5 empty] | 0 | 400 | ℃ | %Z032103 | AI |  | 70CRB03 | [5 empty] | TBC02 | 5 | 6 |  |  | 70LBQ20CT103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CT104 | 2#抽汽电动阀前疏水温度 | Drain temperature before 2# extraction steam MOV | 70CRB01 | FCS0704 | 3 | 2 | 4 | AAI143-H | 4~20mA | N | %Z032104 | [5 empty] | 0 | 400 | ℃ | %Z032104 | AI |  | 70CRB03 | [5 empty] | TBC02 | 7 | 8 |  |  | 70LBQ20CT104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70MAL43CT101 | 2#抽汽和#1级非调整抽汽逆止阀前疏水阀后温度 | Temperature after drain valve before 2# extraction steam and #1 non-adjusting extraction steam check valve | 70CRB01 | FCS0704 | 3 | 2 | 5 | AAI143-H | 4~20mA | N | %Z032105 | [5 empty] | 0 | 400 | ℃ | %Z032105 | AI |  | 70CRB03 | [5 empty] | TBC02 | 9 | 10 |  |  | 70MAL43CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-017
|  | 70LBQ20CP103 | #1级非调整抽汽压力 | #1 non-regulated extraction steam pressure | 70CRB01 | FCS0704 | 3 | 2 | 6 | AAI143-H | 4~20mA | N | %Z032106 | [5 empty] | 0 | 2.5 | MPa | %Z032106 | AI |  | 70CRB03 | [5 empty] | TBC02 | 11 | 12 |  |  | 70LBQ20CP103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CT106 | #1级非调整抽汽温度 | #1 non-regulated extraction steam temperature | 70CRB01 | FCS0704 | 3 | 2 | 7 | AAI143-H | 4~20mA | N | %Z032107 | [5 empty] | 0 | 400 | ℃ | %Z032107 | AI |  | 70CRB03 | [5 empty] | TBC02 | 13 | 142 |  |  | 70LBQ20CT106 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CT107 | #1级非调整抽汽逆止阀后疏水温度1 | Drain temperature 1 after #1 non-regulated extraction steam check valve | 70CRB01 | FCS0704 | 3 | 2 | 8 | AAI143-H | 4~20mA | N | %Z032108 | [5 empty] | 0 | 400 | ℃ | %Z032108 | AI |  | 70CRB03 | [5 empty] | TBC02 | 15 | 16 |  |  | 70LBQ20CT107 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CP104 | #1级非调整抽汽减温减压(C)后蒸汽压力 | Steam pressure after #1 non-regulated extraction steam temperature and pressure reduction(C) | 70CRB01 | FCS0704 | 3 | 2 | 9 | AAI143-H | 4~20mA | N | %Z032109 | [5 empty] | 0 | 2 | MPa | %Z032109 | AI |  | 70CRB03 | [5 empty] | TBC02 | 17 | 18 |  |  | 70LBQ20CP104 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-005
|  | 70LBQ20CT110 | #1级非调整抽汽减温减压(C)后疏水温度 | Drain temperature after #1 non-regulated extraction steam temperature and pressure reduction(C) | 70CRB01 | FCS0704 | 3 | 2 | 10 | AAI143-H | 4~20mA | N | %Z032110 | [5 empty] | 0 | 300 | ℃ | %Z032110 | AI |  | 70CRB03 | [5 empty] | TBC02 | 19 | 20 |  |  | 70LBQ20CT110 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CF102 | 中压联箱进汽母管蒸汽流量 | MP steam header inlet main pipe steam flow | 70CRB01 | FCS0704 | 3 | 2 | 11 | AAI143-H | 4~20mA | N | %Z032111 | [5 empty] | 0 | 60 | t/h | %Z032111 | AI |  | 70CRB03 | [5 empty] | TBC02 | 21 | 22 |  |  | 70LBQ20CF102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CP107 | 中压联箱蒸汽压力 | MP steam header steam pressure | 70CRB01 | FCS0704 | 3 | 2 | 12 | AAI143-H | 4~20mA | N | %Z032112 | [5 empty] | 0 | 2 | MPa | %Z032112 | AI |  | 70CRB03 | [5 empty] | TBC02 | 23 | 24 |  |  | 70LBQ20CP107 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CF104 | 中压联箱至低压联箱蒸汽流量 | MP steam header to LP steam header steam flow | 70CRB01 | FCS0704 | 3 | 2 | 13 | AAI143-H | 4~20mA | N | %Z032113 | [5 empty] | 0 | 60 | t/h | %Z032113 | AI |  | 70CRB03 | [5 empty] | TBC02 | 25 | 26 |  |  | 70LBQ20CF104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CT115 | 中压蒸汽减温减压(E)后蒸汽温度 | Steam temperature after MP steam temperature and pressure reduction(E) | 70CRB01 | FCS0704 | 3 | 2 | 14 | AAI143-H | 4~20mA | N | %Z032114 | [5 empty] | 0 | 300 | ℃ | %Z032114 | AI |  | 70CRB03 | [5 empty] | TBC02 | 27 | 28 |  |  | 70LBQ20CT115 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-005
[5 empty] | 70CRB01 | FCS0704 | 3 | 2 | 15 | AAI143-H | 4~20mA | N | %Z032115 | [8 empty] | %Z032115 | AI |  | 70CRB03 | [5 empty] | TBC02 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 3 | 2 | 16 | AAI143-H | 4~20mA | N | %Z032116 | [8 empty] | %Z032116 | AI |  | 70CRB03 | [5 empty] | TBC02 | 31 | 32
|  | 70MAV21AP022XQ01 | 2#主油泵电流 | 2# main oil pump current | 70CRB01 | FCS0704 | 3 | 3 | 1 | AAI143-H | 4~20mA | N | %Z033101 | [7 empty] | A | %Z033101 | AI | 4W | 70CRB03 | [5 empty] | TBC03 | 2 | 1 |  |  | 70MAV21AP021 | 4～20mA | AI | [8 empty] | DAS | U |  | K0203-005
|  | 70MAV32AP001XQ01 | 2#顶轴油泵电流 | 2# jacking oil pump current | 70CRB01 | FCS0704 | 3 | 3 | 2 | AAI143-H | 4~20mA | N | %Z033102 | [7 empty] | A | %Z033102 | AI | 4W | 70CRB03 | [5 empty] | TBC03 | 4 | 3 |  |  | 70MAV32AP001 | 4～20mA | AI | [8 empty] | DAS | U |  | K0203-005
|  | 70MAX01AP002XQ01 | 2# EH油泵电流 | 2# EH oil pump current | 70CRB01 | FCS0704 | 3 | 3 | 3 | AAI143-H | 4~20mA | N | %Z033103 | [7 empty] | A | %Z033103 | AI | 4W | 70CRB03 | [5 empty] | TBC03 | 6 | 5 |  |  | 70MAX01GH001 | 4～20mA | AI | [8 empty] | DAS | U |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70LBQ20CT108 | #1级非调整抽汽逆止阀后疏水温度2 | Drain temperature 2 after #1 non-regulated extraction steam check valve | 70CRB01 | FCS0704 | 3 | 3 | 4 | AAI143-H | 4~20mA | N | %Z033104 | [5 empty] | 0 | 400 | ℃ | %Z033104 | AI |  | 70CRB03 | [5 empty] | TBC03 | 7 | 8 |  |  | 70LBQ20CT108 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CT109 | #1级非调整抽汽减温减压(C)后蒸汽温度 | Steam temperature after #1 non-regulated extraction steam temperature and pressure reduction(C) | 70CRB01 | FCS0704 | 3 | 3 | 5 | AAI143-H | 4~20mA | N | %Z033105 | [5 empty] | 0 | 300 | ℃ | %Z033105 | AI |  | 70CRB03 | [5 empty] | TBC03 | 9 | 10 |  |  | 70LBQ20CT109 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-005
|  | 70LBQ20CF101 | #1级非调整抽汽减温减压(C)后蒸汽流量 | Steam flow after #1 non-regulated extraction steam temperature and pressure reduction(C) | 70CRB01 | FCS0704 | 3 | 3 | 6 | AAI143-H | 4~20mA | N | %Z033106 | [5 empty] | 0 | 60 | t/h | %Z033106 | AI |  | 70CRB03 | [5 empty] | TBC03 | 11 | 12 |  |  | 70LBQ20CF101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-005
|  | 70LBQ20CP106 | 中压联箱进汽母管蒸汽压力 | MP steam header inlet main pipe steam pressure | 70CRB01 | FCS0704 | 3 | 3 | 7 | AAI143-H | 4~20mA | N | %Z033107 | [5 empty] | 0 | 2 | MPa | %Z033107 | AI |  | 70CRB03 | [5 empty] | TBC03 | 13 | 142 |  |  | 70LBQ20CP106 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CT113 | 中压联箱进汽母管蒸汽温度 | MP steam header inlet main pipe steam temperature | 70CRB01 | FCS0704 | 3 | 3 | 8 | AAI143-H | 4~20mA | N | %Z033108 | [5 empty] | 0 | 300 | ℃ | %Z033108 | AI |  | 70CRB03 | [5 empty] | TBC03 | 15 | 16 |  |  | 70LBQ20CT113 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CF103 | 中压联箱至老厂#6机组中压蒸汽管道供热蒸汽流量 | MP steam header to existing MP steam line of #6 unit heating steam flow | 70CRB01 | FCS0704 | 3 | 3 | 9 | AAI143-H | 4~20mA | N | %Z033109 | [5 empty] | 0 | 60 | t/h | %Z033109 | AI |  | 70CRB03 | [5 empty] | TBC03 | 17 | 18 |  |  | 70LBQ20CF103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CP108 | 中压蒸汽减温减压(E)后蒸汽压力 | Steam pressure after MP steam temperature and pressure reduction(E) | 70CRB01 | FCS0704 | 3 | 3 | 10 | AAI143-H | 4~20mA | N | %Z033110 | [5 empty] | 0 | 1 | MPa | %Z033110 | AI |  | 70CRB03 | [5 empty] | TBC03 | 19 | 20 |  |  | 70LBQ20CP108 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-005
|  | 70LBS20CT105 | 5#低加进汽温度 | 5# LP. heater inlet steam temperature | 70CRB01 | FCS0704 | 3 | 3 | 11 | AAI143-H | 4~20mA | N | %Z033111 | [5 empty] | 0 | 200 | ℃ | %Z033111 | AI |  | 70CRB03 | [5 empty] | TBC03 | 21 | 22 |  |  | 70LBS20CT105 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LCC20CL101 | 5#低加水位1 | 5# LP heater level 1 | 70CRB01 | FCS0704 | 3 | 3 | 12 | AAI143-H | 4~20mA | N | %Z033112 | [5 empty] | 0 | 1 | m | %Z033112 | AI |  | 70CRB03 | [5 empty] | TBC03 | 23 | 24 |  |  | 70LCC20CL101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC20CL103 | 5#低加水位3 | 5# LP heater level 3 | 70CRB01 | FCS0704 | 3 | 3 | 13 | AAI143-H | 4~20mA | N | %Z033113 | [5 empty] | 0 | 1 | m | %Z033113 | AI |  | 70CRB03 | [5 empty] | TBC03 | 25 | 26 |  |  | 70LCC20CL103 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC20CT102 | 5#低加危急疏水温度 | 5# LP heater emergency drain water temperature | 70CRB01 | FCS0704 | 3 | 3 | 14 | AAI143-H | 4~20mA | N | %Z033114 | [5 empty] | 0 | 200 | ℃ | %Z033114 | AI |  | 70CRB03 | [5 empty] | TBC03 | 27 | 28 |  |  | 70LCC20CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-012
[5 empty] | 70CRB01 | FCS0704 | 3 | 3 | 15 | AAI143-H | 4~20mA | N | %Z033115 | [8 empty] | %Z033115 | AI |  | 70CRB03 | [5 empty] | TBC03 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 3 | 3 | 16 | AAI143-H | 4~20mA | N | %Z033116 | [8 empty] | %Z033116 | AI |  | 70CRB03 | [5 empty] | TBC03 | 31 | 32
|  | 70LBQ20CP102 | 1#高压加热器进汽压力 | 1# HP heater inlet steam pressure | 70CRB01 | FCS0704 | 4 | 1 | 1 | AAI143-H | 4~20mA | N | %Z041101 | [5 empty] | 0 | 2.5 | MPa | %Z041101 | AI |  | 70CRB03 | [5 empty] | TBC04 | 1 | 2 |  |  | 70LBQ20CP102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBQ20CT105 | 1#高压加热器进汽温度 | 1# HP heater inlet steam temperature | 70CRB01 | FCS0704 | 4 | 1 | 2 | AAI143-H | 4~20mA | N | %Z041102 | [5 empty] | 0 | 400 | ℃ | %Z041102 | AI |  | 70CRB03 | [5 empty] | TBC04 | 3 | 4 |  |  | 70LBQ20CT105 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-005
|  | 70LBR10CP101 | 3#抽汽蒸汽压力 | 3# extraction steam pressure | 70CRB01 | FCS0704 | 4 | 1 | 3 | AAI143-H | 4~20mA | N | %Z041103 | [5 empty] | 0 | 1.44 | MPa | %Z041103 | AI |  | 70CRB03 | [5 empty] | TBC04 | 5 | 6 |  |  | 70LBR10CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBR10CT101 | 3#抽汽蒸汽温度 | 3# extraction steam temperature | 70CRB01 | FCS0704 | 4 | 1 | 4 | AAI143-H | 4~20mA | N | %Z041104 | [5 empty] | 0 | 300 | ℃ | %Z041104 | AI |  | 70CRB03 | [5 empty] | TBC04 | 7 | 8 |  |  | 70LBR10CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBR10CT102 | 3#抽汽逆止阀2后管顶温度 | Top temperature of pipe after 3# extraction steam check valve 2 | 70CRB01 | FCS0704 | 4 | 1 | 5 | AAI143-H | 4~20mA | N | %Z041105 | [5 empty] | 0 | 300 | ℃ | %Z041105 | AI |  | 70CRB03 | [5 empty] | TBC04 | 9 | 10 |  |  | 70LBR10CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBR10CT104 | 3#抽汽逆止阀2后疏水温度1 | Drain temperature 1 after 3# extraction steam check valve 2 | 70CRB01 | FCS0704 | 4 | 1 | 6 | AAI143-H | 4~20mA | N | %Z041106 | [5 empty] | 0 | 300 | ℃ | %Z041106 | AI |  | 70CRB03 | [5 empty] | TBC04 | 11 | 12 |  |  | 70LBR10CT104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBR10CT106 | 3#抽汽电动阀后旁路疏水温度 | Bypass drain temperature after 3# extraction steam MOV | 70CRB01 | FCS0704 | 4 | 1 | 7 | AAI143-H | 4~20mA | N | %Z041107 | [5 empty] | 0 | 300 | ℃ | %Z041107 | AI |  | 70CRB03 | [5 empty] | TBC04 | 13 | 142 |  |  | 70LBR10CT106 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBR10CT107 | 3#抽汽电动调节阀后疏水温度1 | Drain temperature 1 after 3# extraction steam regulating MOV | 70CRB01 | FCS0704 | 4 | 1 | 8 | AAI143-H | 4~20mA | N | %Z041108 | [5 empty] | 0 | 300 | ℃ | %Z041108 | AI |  | 70CRB03 | [5 empty] | TBC04 | 15 | 16 |  |  | 70LBR10CT107 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS20CP101 | 5#抽汽蒸汽压力 | 5# extraction steam pressure | 70CRB01 | FCS0704 | 4 | 1 | 9 | AAI143-H | 4~20mA | N | %Z041109 | [5 empty] | 0 | 0.2 | MPa | %Z041109 | AI |  | 70CRB03 | [5 empty] | TBC04 | 17 | 18 |  |  | 70LBS20CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS20CT101 | 5#抽汽蒸汽温度 | 5# extraction steam temperature | 70CRB01 | FCS0704 | 4 | 1 | 10 | AAI143-H | 4~20mA | N | %Z041110 | [5 empty] | 0 | 200 | ℃ | %Z041110 | AI |  | 70CRB03 | [5 empty] | TBC04 | 19 | 20 |  |  | 70LBS20CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS20CT102 | 5#抽汽逆止阀后管顶温度 | Top temperature of pipe after 5# extraction steam check valve | 70CRB01 | FCS0704 | 4 | 1 | 11 | AAI143-H | 4~20mA | N | %Z041111 | [5 empty] | 0 | 200 | ℃ | %Z041111 | AI |  | 70CRB03 | [5 empty] | TBC04 | 21 | 22 |  |  | 70LBS20CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
[5 empty] | 70CRB01 | FCS0704 | 4 | 1 | 12 | AAI143-H | 4~20mA | N | %Z041112 | [8 empty] | %Z041112 | AI |  | 70CRB03 | [5 empty] | TBC04 | 23 | 24
[5 empty] | 70CRB01 | FCS0704 | 4 | 1 | 13 | AAI143-H | 4~20mA | N | %Z041113 | [8 empty] | %Z041113 | AI |  | 70CRB03 | [5 empty] | TBC04 | 25 | 26
[5 empty] | 70CRB01 | FCS0704 | 4 | 1 | 14 | AAI143-H | 4~20mA | N | %Z041114 | [8 empty] | %Z041114 | AI |  | 70CRB03 | [5 empty] | TBC04 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 4 | 1 | 15 | AAI143-H | 4~20mA | N | %Z041115 | [8 empty] | %Z041115 | AI |  | 70CRB03 | [5 empty] | TBC04 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 4 | 1 | 16 | AAI143-H | 4~20mA | N | %Z041116 | [8 empty] | %Z041116 | AI |  | 70CRB03 | [5 empty] | TBC04 | 31 | 32
|  | 70LBQ10CP102 | 2#高压加热器进汽压力 | 2# HP heater inlet steam pressure | 70CRB01 | FCS0704 | 4 | 2 | 1 | AAI143-H | 4~20mA | N | %Z042101 | [5 empty] | 0 | 4 | MPa | %Z042101 | AI |  | 70CRB03 | [5 empty] | TBC05 | 1 | 2 |  |  | 70LBQ10CP102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBQ10CT105 | 2#高压加热器进汽温度 | 2# HP heater inlet steam temperature | 70CRB01 | FCS0704 | 4 | 2 | 2 | AAI143-H | 4~20mA | N | %Z042102 | [5 empty] | 0 | 400 | ℃ | %Z042102 | AI |  | 70CRB03 | [5 empty] | TBC05 | 3 | 4 |  |  | 70LBQ10CT105 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBR10CT103 | 3#抽汽逆止阀2后管底温度 | Bottom temperature of pipe after 3# extraction steam check valve 2 | 70CRB01 | FCS0704 | 4 | 2 | 3 | AAI143-H | 4~20mA | N | %Z042103 | [5 empty] | 0 | 300 | ℃ | %Z042103 | AI |  | 70CRB03 | [5 empty] | TBC05 | 5 | 6 |  |  | 70LBR10CT103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBR10CT105 | 3#抽汽逆止阀2后疏水温度2 | Drain temperature 2 after 3# extraction steam check valve 2 | 70CRB01 | FCS0704 | 4 | 2 | 4 | AAI143-H | 4~20mA | N | %Z042104 | [5 empty] | 0 | 300 | ℃ | %Z042104 | AI |  | 70CRB03 | [5 empty] | TBC05 | 7 | 8 |  |  | 70LBR10CT105 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBR10CT108 | 3#抽汽电动调节阀后疏水温度2 | Drain temperature 2 after 3# extraction steam regulating MOV | 70CRB01 | FCS0704 | 4 | 2 | 5 | AAI143-H | 4~20mA | N | %Z042105 | [5 empty] | 0 | 300 | ℃ | %Z042105 | AI |  | 70CRB03 | [5 empty] | TBC05 | 9 | 10 |  |  | 70LBR10CT108 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS30CP101 | 4#抽汽蒸汽压力1 | 4# extraction steam pressure 1 | 70CRB01 | FCS0704 | 4 | 2 | 6 | AAI143-H | 4~20mA | N | %Z042106 | [5 empty] | 0 | 1 | MPa | %Z042106 | AI |  | 70CRB03 | [5 empty] | TBC05 | 11 | 12 |  |  | 70LBS30CP101 | 4~20mA | AI | [8 empty] | ETS | D |  | K0204-004
|  | 70LBS30CT101 | 4#抽汽蒸汽温度 | 4# extraction steam temperature | 70CRB01 | FCS0704 | 4 | 2 | 7 | AAI143-H | 4~20mA | N | %Z042107 | [5 empty] | 0 | 300 | ℃ | %Z042107 | AI |  | 70CRB03 | [5 empty] | TBC05 | 13 | 142 |  |  | 70LBS30CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS30CT102 | 4#抽汽逆止阀后管顶温度 | Top temperature of pipe after 4# extraction steam check valve | 70CRB01 | FCS0704 | 4 | 2 | 8 | AAI143-H | 4~20mA | N | %Z042108 | [5 empty] | 0 | 300 | ℃ | %Z042108 | AI |  | 70CRB03 | [5 empty] | TBC05 | 15 | 16 |  |  | 70LBS30CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS30CT104 | 4#抽汽电动调节阀后疏水温度 | Drain temperature after 4# extraction steam regulating MOV | 70CRB01 | FCS0704 | 4 | 2 | 9 | AAI143-H | 4~20mA | N | %Z042109 | [5 empty] | 0 | 300 | ℃ | %Z042109 | AI |  | 70CRB03 | [5 empty] | TBC05 | 17 | 18 |  |  | 70LBS30CT104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS10CP101 | 6#抽汽蒸汽压力 | 6# extraction steam pressure | 70CRB01 | FCS0704 | 4 | 2 | 10 | AAI143-H | 4~20mA | N | %Z042110 | [5 empty] | 0 | 0.1 | MPa | %Z042110 | AI |  | 70CRB03 | [5 empty] | TBC05 | 19 | 20 |  |  | 70LBS10CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS10CT101 | 6#抽汽蒸汽温度 | 6# extraction steam temperature | 70CRB01 | FCS0704 | 4 | 2 | 11 | AAI143-H | 4~20mA | N | %Z042111 | [5 empty] | 0 | 100 | ℃ | %Z042111 | AI |  | 70CRB03 | [5 empty] | TBC05 | 21 | 22 |  |  | 70LBS10CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS10CT102 | 6#抽汽电动阀前疏水温度 | Drain temperature before 6# extraction steam MOV | 70CRB01 | FCS0704 | 4 | 2 | 12 | AAI143-H | 4~20mA | N | %Z042112 | [5 empty] | 0 | 100 | ℃ | %Z042112 | AI |  | 70CRB03 | [5 empty] | TBC05 | 23 | 24 |  |  | 70LBS10CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
[5 empty] | 70CRB01 | FCS0704 | 4 | 2 | 13 | AAI143-H | 4~20mA | N | %Z042113 | [8 empty] | %Z042113 | AI |  | 70CRB03 | [5 empty] | TBC05 | 25 | 26
[5 empty] | 70CRB01 | FCS0704 | 4 | 2 | 14 | AAI143-H | 4~20mA | N | %Z042114 | [8 empty] | %Z042114 | AI |  | 70CRB03 | [5 empty] | TBC05 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 4 | 2 | 15 | AAI143-H | 4~20mA | N | %Z042115 | [8 empty] | %Z042115 | AI |  | 70CRB03 | [5 empty] | TBC05 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 4 | 2 | 16 | AAI143-H | 4~20mA | N | %Z042116 | [8 empty] | %Z042116 | AI |  | 70CRB03 | [5 empty] | TBC05 | 31 | 32
|  | 70MAV24AP001XQ01 | 直流油泵电流 | DC oil pump current | 70CRB01 | FCS0704 | 4 | 3 | 1 | AAI143-H | 4~20mA | N | %Z043101 | [7 empty] | A | %Z043101 | AI | 4W | 70CRB03 | [5 empty] | TBC06 | 2 | 1 |  |  | 70MAV24AP001 | 4～20mA | AI | [8 empty] | DAS | U |  | K0203-005
|  | 70MAV31AP001XQ01 | 1#顶轴油泵电流 | 1# jacking oil pump current | 70CRB01 | FCS0704 | 4 | 3 | 2 | AAI143-H | 4~20mA | N | %Z043102 | [7 empty] | A | %Z043102 | AI | 4W | 70CRB03 | [5 empty] | TBC06 | 4 | 3 |  |  | 70MAV31AP001 | 4～20mA | AI | [8 empty] | DAS | U |  | K0203-005
|  | 70LBS30CP102 | 4#抽汽蒸汽压力2 | 4# extraction steam pressure 2 | 70CRB01 | FCS0704 | 4 | 3 | 3 | AAI143-H | 4~20mA | N | %Z043103 | [5 empty] | 0 | 1 | MPa | %Z043103 | AI |  | 70CRB03 | [5 empty] | TBC06 | 5 | 6 |  |  | 70LBS30CP102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS30CT103 | 4#抽汽逆止阀后管底温度 | Bottom temperature of pipe after 4# extraction steam check valve | 70CRB01 | FCS0704 | 4 | 3 | 4 | AAI143-H | 4~20mA | N | %Z043104 | [5 empty] | 0 | 300 | ℃ | %Z043104 | AI |  | 70CRB03 | [5 empty] | TBC06 | 7 | 8 |  |  | 70LBS30CT103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70MAL47CT101 | 4#抽汽逆止阀前疏水阀后温度 | Temperature after drain valve before 4# extraction steam check valve | 70CRB01 | FCS0704 | 4 | 3 | 5 | AAI143-H | 4~20mA | N | %Z043105 | [5 empty] | 0 | 300 | ℃ | %Z043105 | AI |  | 70CRB03 | [5 empty] | TBC06 | 9 | 10 |  |  | 70MAL47CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-017
|  | 70LBS20CT103 | 5#抽汽逆止阀后管底温度 | Bottom temperature of pipe after 5# extraction steam check valve | 70CRB01 | FCS0704 | 4 | 3 | 6 | AAI143-H | 4~20mA | N | %Z043106 | [5 empty] | 0 | 200 | ℃ | %Z043106 | AI |  | 70CRB03 | [5 empty] | TBC06 | 11 | 12 |  |  | 70LBS20CT103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LBS20CT104 | 5#抽汽逆止阀后疏水温度 | Drain temperature after 5# extraction steam check valve | 70CRB01 | FCS0704 | 4 | 3 | 7 | AAI143-H | 4~20mA | N | %Z043107 | [5 empty] | 0 | 200 | ℃ | %Z043107 | AI |  | 70CRB03 | [5 empty] | TBC06 | 13 | 142 |  |  | 70LBS20CT104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70MAL49CT101 | 5#抽汽逆止阀前疏水阀后温度 | Temperature after drain valve before 5# extraction steam check valve | 70CRB01 | FCS0704 | 4 | 3 | 8 | AAI143-H | 4~20mA | N | %Z043108 | [5 empty] | 0 | 400 | ℃ | %Z043108 | AI |  | 70CRB03 | [5 empty] | TBC06 | 15 | 16 |  |  | 70MAL49CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-017
|  | 70LBR20AA104XQ11 | 主蒸汽减温减压器B电动减压调节阀位置反馈 | Main steam pressure reducer desuperheater B pressure reduciong regulating MOV position feddback | 70CRB01 | FCS0704 | 4 | 3 | 9 | AAI143-H | 4~20mA | N | %Z043109 | [5 empty] | 0 | 100 | % | %Z043109 | AI | 4W | 70CRB03 | [5 empty] | TBC06 | 18 | 17 |  |  | 70LBR20AA104 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-002
|  | 70LBR20AA105XQ11 | 主蒸汽减温减压器B电动减温调节阀位置反馈 | Main steam pressure reducer desuperheater B temperature reduciong regulating MOV position feddback | 70CRB01 | FCS0704 | 4 | 3 | 10 | AAI143-H | 4~20mA | N | %Z043110 | [5 empty] | 0 | 100 | % | %Z043110 | AI | 4W | 70CRB03 | [5 empty] | TBC06 | 20 | 19 |  |  | 70LBR20AA105 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-002
|  | 70LBS10CT103 | 6#抽汽电动阀后疏水温度 | Drain temperature after 6# extraction steam MOV | 70CRB01 | FCS0704 | 4 | 3 | 11 | AAI143-H | 4~20mA | N | %Z043111 | [5 empty] | 0 | 100 | ℃ | %Z043111 | AI |  | 70CRB03 | [5 empty] | TBC06 | 21 | 22 |  |  | 70LBS10CT103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
[5 empty] | 70CRB01 | FCS0704 | 4 | 3 | 12 | AAI143-H | 4~20mA | N | %Z043112 | [8 empty] | %Z043112 | AI |  | 70CRB03 | [5 empty] | TBC06 | 23 | 24
[5 empty] | 70CRB01 | FCS0704 | 4 | 3 | 13 | AAI143-H | 4~20mA | N | %Z043113 | [8 empty] | %Z043113 | AI |  | 70CRB03 | [5 empty] | TBC06 | 25 | 26
[5 empty] | 70CRB01 | FCS0704 | 4 | 3 | 14 | AAI143-H | 4~20mA | N | %Z043114 | [8 empty] | %Z043114 | AI |  | 70CRB03 | [5 empty] | TBC06 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 4 | 3 | 15 | AAI143-H | 4~20mA | N | %Z043115 | [8 empty] | %Z043115 | AI |  | 70CRB03 | [5 empty] | TBC06 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 4 | 3 | 16 | AAI143-H | 4~20mA | N | %Z043116 | [8 empty] | %Z043116 | AI |  | 70CRB03 | [5 empty] | TBC06 | 31 | 32
|  | 70LAB50CT102 | 1#高加入口给水温度 | 1# HP heater inlet feedwater temp. | 70CRB01 | FCS0704 | 5 | 1 | 1 | AAI143-H | 4~20mA | N | %Z051101 | [5 empty] | 0 | 200 | ℃ | %Z051101 | AI |  | 70CRB03 | [5 empty] | TBF01 | 1 | 2 |  |  | 70LAB50CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-006
|  | 70LAD10CL101 | 1#高加水位1 | 1# HP heater level 1 | 70CRB01 | FCS0704 | 5 | 1 | 2 | AAI143-H | 4~20mA | N | %Z051102 | [5 empty] | 0 | 1.5 | m | %Z051102 | AI |  | 70CRB03 | [5 empty] | TBF01 | 3 | 4 |  |  | 70LAD10CL101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-011
|  | 70LAD10CL103 | 1#高加水位3 | 1# HP heater level 3 | 70CRB01 | FCS0704 | 5 | 1 | 3 | AAI143-H | 4~20mA | N | %Z051103 | [5 empty] | 0 | 1.5 | m | %Z051103 | AI |  | 70CRB03 | [5 empty] | TBF01 | 5 | 6 |  |  | 70LAD10CL103 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-011
|  | 70LAD10CT102 | 1#高加危急疏水温度 | 1# HP heater emergency drain water temperature | 70CRB01 | FCS0704 | 5 | 1 | 4 | AAI143-H | 4~20mA | N | %Z051104 | [5 empty] | 0 | 300 | ℃ | %Z051104 | AI |  | 70CRB03 | [5 empty] | TBF01 | 7 | 8 |  |  | 70LAD10CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-011
|  | 70LBS30CP103 | 4#低加进汽压力 | 4# LP. heater inlet steam pressure | 70CRB01 | FCS0704 | 5 | 1 | 5 | AAI143-H | 4~20mA | N | %Z051105 | [5 empty] | 0 | 1 | MPa | %Z051105 | AI |  | 70CRB03 | [5 empty] | TBF01 | 9 | 10 |  |  | 70LBS30CP103 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-004
|  | 70LCA30CT105 | 4#低加出口水温 | 4# LP. Heater outlet temperature | 70CRB01 | FCS0704 | 5 | 1 | 6 | AAI143-H | 4~20mA | N | %Z051106 | [5 empty] | 0 | 200 | ℃ | %Z051106 | AI |  | 70CRB03 | [5 empty] | TBF01 | 11 | 12 |  |  | 70LCA30CT105 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-008
|  | 70LCC30CL102 | 4#低加水位2 | 4# LP heater level 2 | 70CRB01 | FCS0704 | 5 | 1 | 7 | AAI143-H | 4~20mA | N | %Z051107 | [5 empty] | 0 | 1 | m | %Z051107 | AI |  | 70CRB03 | [5 empty] | TBF01 | 13 | 142 |  |  | 70LCC30CL102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC30CT101 | 4#低加正常疏水温度 | 4# LP heater drain water temperature | 70CRB01 | FCS0704 | 5 | 1 | 8 | AAI143-H | 4~20mA | N | %Z051108 | [5 empty] | 0 | 200 | ℃ | %Z051108 | AI |  | 70CRB03 | [5 empty] | TBF01 | 15 | 16 |  |  | 70LCC30CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-012
|  | 70LBS10CT104 | 6#低加进汽温度 | 6# LP. heater inlet steam temperature | 70CRB01 | FCS0704 | 5 | 1 | 9 | AAI143-H | 4~20mA | N | %Z051109 | [5 empty] | 0 | 100 | ℃ | %Z051109 | AI |  | 70CRB03 | [5 empty] | TBF01 | 17 | 18 |  |  | 70LBS10CT104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LCA30CT103 | 6#低加出口水温 | 6# LP. Heater outlet temperature | 70CRB01 | FCS0704 | 5 | 1 | 10 | AAI143-H | 4~20mA | N | %Z051110 | [5 empty] | 0 | 200 | ℃ | %Z051110 | AI |  | 70CRB03 | [5 empty] | TBF01 | 19 | 20 |  |  | 70LCA30CT103 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-008
|  | 70LCC10CL102 | 6#低加水位2 | 6# LP heater level 2 | 70CRB01 | FCS0704 | 5 | 1 | 11 | AAI143-H | 4~20mA | N | %Z051111 | [5 empty] | 0 | 1 | m | %Z051111 | AI |  | 70CRB03 | [5 empty] | TBF01 | 21 | 22 |  |  | 70LCC10CL102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC10CT101 | 6#低加正常疏水温度 | 6# LP heater drain water temperature | 70CRB01 | FCS0704 | 5 | 1 | 12 | AAI143-H | 4~20mA | N | %Z051112 | [5 empty] | 0 | 200 | ℃ | %Z051112 | AI |  | 70CRB03 | [5 empty] | TBF01 | 23 | 24 |  |  | 70LCC10CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-012
|  | 70LBS30AA101XQ11 | 4#抽汽电动调节阀位置指令 | 4# extraction steam regulating MOV position feedback | 70CRB01 | FCS0704 | 5 | 1 | 13 | AAI143-H | 4~20mA | N | %Z051113 | [5 empty] | 0 | 100 | % | %Z051113 | AI | 4W | 70CRB03 | [5 empty] | TBF01 | 26 | 25 |  |  | 70LBS30AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-004
[5 empty] | 70CRB01 | FCS0704 | 5 | 1 | 14 | AAI143-H | 4~20mA | N | %Z051114 | [8 empty] | %Z051114 | AI |  | 70CRB03 | [5 empty] | TBF01 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 5 | 1 | 15 | AAI143-H | 4~20mA | N | %Z051115 | [8 empty] | %Z051115 | AI |  | 70CRB03 | [5 empty] | TBF01 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 5 | 1 | 16 | AAI143-H | 4~20mA | N | %Z051116 | [8 empty] | %Z051116 | AI |  | 70CRB03 | [5 empty] | TBF01 | 31 | 32
|  | 70LAB60CT101 | 1#高加出口给水温度 | 1# HP heater outlet feedwater temp. | 70CRB01 | FCS0704 | 5 | 2 | 1 | AAI143-H | 4~20mA | N | %Z052101 | [5 empty] | 0 | 300 | ℃ | %Z052101 | AI |  | 70CRB03 | [5 empty] | TBF02 | 1 | 2 |  |  | 70LAB60CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-006
|  | 70LAD10CL102 | 1#高加水位2 | 1# HP heater level 2 | 70CRB01 | FCS0704 | 5 | 2 | 2 | AAI143-H | 4~20mA | N | %Z052102 | [5 empty] | 0 | 1.5 | m | %Z052102 | AI |  | 70CRB03 | [5 empty] | TBF02 | 3 | 4 |  |  | 70LAD10CL102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-011
|  | 70LAD10CT101 | 1#高加正常疏水温度 | 1# HP heater drain water temperature | 70CRB01 | FCS0704 | 5 | 2 | 3 | AAI143-H | 4~20mA | N | %Z052103 | [5 empty] | 0 | 300 | ℃ | %Z052103 | AI |  | 70CRB03 | [5 empty] | TBF02 | 5 | 6 |  |  | 70LAD10CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-011
|  | 70LAD10AA101XQ11 | 1#高加正常疏水气动调节阀位置反馈 | 1# HP heater drain water regulating PV position feedback | 70CRB01 | FCS0704 | 5 | 2 | 4 | AAI143-H | 4~20mA | N | %Z052104 | [5 empty] | 0 | 100 | % | %Z052104 | AI | 4W | 70CRB03 | [5 empty] | TBF02 | 8 | 7 |  |  | 70LAD10AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-011
|  | 70LCC30AA101XQ11 | 4#低加正常疏水气动调节阀位置反馈 | 4# LP heater drain water regulating PV position feedback | 70CRB01 | FCS0704 | 5 | 2 | 5 | AAI143-H | 4~20mA | N | %Z052105 | [5 empty] | 0 | 100 | % | %Z052105 | AI | 4W | 70CRB03 | [5 empty] | TBF02 | 10 | 9 |  |  | 70LCC30AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-012
|  | 70LCC20AA101XQ11 | 5#低加正常疏水气动调节阀位置反馈 | 5# LP heater drain water regulating PV position feedback | 70CRB01 | FCS0704 | 5 | 2 | 6 | AAI143-H | 4~20mA | N | %Z052106 | [5 empty] | 0 | 100 | % | %Z052106 | AI | 4W | 70CRB03 | [5 empty] | TBF02 | 12 | 11 |  |  | 70LCC20AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-012
|  | 70LCC10AA101XQ11 | 6#低加正常疏水气动调节阀位置反馈 | 6# LP heater drain water regulating PV position feedback | 70CRB01 | FCS0704 | 5 | 2 | 7 | AAI143-H | 4~20mA | N | %Z052107 | [5 empty] | 0 | 100 | % | %Z052107 | AI | 4W | 70CRB03 | [5 empty] | TBF02 | 14 | 13 |  |  | 70LCC10AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-012
|  | 70LBS30CT105 | 4#低加进汽温度 | 4# LP. heater inlet steam temperature | 70CRB01 | FCS0704 | 5 | 2 | 8 | AAI143-H | 4~20mA | N | %Z052108 | [5 empty] | 0 | 300 | ℃ | %Z052108 | AI |  | 70CRB03 | [5 empty] | TBF02 | 15 | 16 |  |  | 70LBS30CT105 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LCC30CL101 | 4#低加水位1 | 4# LP heater level 1 | 70CRB01 | FCS0704 | 5 | 2 | 9 | AAI143-H | 4~20mA | N | %Z052109 | [5 empty] | 0 | 1 | m | %Z052109 | AI |  | 70CRB03 | [5 empty] | TBF02 | 17 | 18 |  |  | 70LCC30CL101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC30CL103 | 4#低加水位3 | 4# LP heater level 3 | 70CRB01 | FCS0704 | 5 | 2 | 10 | AAI143-H | 4~20mA | N | %Z052110 | [5 empty] | 0 | 1 | m | %Z052110 | AI |  | 70CRB03 | [5 empty] | TBF02 | 19 | 20 |  |  | 70LCC30CL103 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC30CT102 | 4#低加危急疏水温度 | 4# LP heater emergency drain water temperature | 70CRB01 | FCS0704 | 5 | 2 | 11 | AAI143-H | 4~20mA | N | %Z052111 | [5 empty] | 0 | 200 | ℃ | %Z052111 | AI |  | 70CRB03 | [5 empty] | TBF02 | 21 | 22 |  |  | 70LCC30CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-012
|  | 70LBS10CP102 | 6#低加进汽压力 | 6# LP. heater inlet steam pressure | 70CRB01 | FCS0704 | 5 | 2 | 12 | AAI143-H | 4~20mA | N | %Z052112 | [5 empty] | 0 | 0.1 | MPa | %Z052112 | AI |  | 70CRB03 | [5 empty] | TBF02 | 23 | 24 |  |  | 70LBS10CP102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LCC10CL101 | 6#低加水位1 | 6# LP heater level 1 | 70CRB01 | FCS0704 | 5 | 2 | 13 | AAI143-H | 4~20mA | N | %Z052113 | [5 empty] | 0 | 1 | m | %Z052113 | AI |  | 70CRB03 | [5 empty] | TBF02 | 25 | 26 |  |  | 70LCC10CL101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC10CL103 | 6#低加水位3 | 6# LP heater level 3 | 70CRB01 | FCS0704 | 5 | 2 | 14 | AAI143-H | 4~20mA | N | %Z052114 | [5 empty] | 0 | 1 | m | %Z052114 | AI |  | 70CRB03 | [5 empty] | TBF02 | 27 | 28 |  |  | 70LCC10CL103 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC10CT102 | 6#低加危急疏水温度 | 6# LP heater emergency drain water temperature | 70CRB01 | FCS0704 | 5 | 2 | 15 | AAI143-H | 4~20mA | N | %Z052115 | [5 empty] | 0 | 200 | ℃ | %Z052115 | AI |  | 70CRB03 | [5 empty] | TBF02 | 29 | 30 |  |  | 70LCC10CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-012
[5 empty] | 70CRB01 | FCS0704 | 5 | 2 | 16 | AAI143-H | 4~20mA | N | %Z052116 | [8 empty] | %Z052116 | AI |  | 70CRB03 | [5 empty] | TBF02 | 31 | 32
|  | 70LAD20CL101 | 2#高加水位1 | 2# HP heater level 1 | 70CRB01 | FCS0704 | 6 | 1 | 1 | AAI143-H | 4~20mA | N | %Z061101 | [5 empty] | 0 | 1.5 | m | %Z061101 | AI |  | 70CRB03 | [5 empty] | TBF04 | 1 | 2 |  |  | 70LAD20CL101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-011
|  | 70LAD20CL103 | 2#高加水位3 | 2# HP heater level 3 | 70CRB01 | FCS0704 | 6 | 1 | 2 | AAI143-H | 4~20mA | N | %Z061102 | [5 empty] | 0 | 1.5 | m | %Z061102 | AI |  | 70CRB03 | [5 empty] | TBF04 | 3 | 4 |  |  | 70LAD20CL103 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-011
|  | 70LAD20CT102 | 2#高加危急疏水温度 | 2# HP heater emergency drain water temperature | 70CRB01 | FCS0704 | 6 | 1 | 3 | AAI143-H | 4~20mA | N | %Z061103 | [5 empty] | 0 | 300 | ℃ | %Z061103 | AI |  | 70CRB03 | [5 empty] | TBF04 | 5 | 6 |  |  | 70LAD20CT102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-011
|  | 70LBS20CP102 | 5#低加进汽压力 | 5# LP. heater inlet steam pressure | 70CRB01 | FCS0704 | 6 | 1 | 4 | AAI143-H | 4~20mA | N | %Z061104 | [5 empty] | 0 | 0.2 | MPa | %Z061104 | AI |  | 70CRB03 | [5 empty] | TBF04 | 7 | 8 |  |  | 70LBS20CP102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LCA30CT104 | 5#低加出口水温 | 5# LP. Heater outlet temperature | 70CRB01 | FCS0704 | 6 | 1 | 5 | AAI143-H | 4~20mA | N | %Z061105 | [5 empty] | 0 | 200 | ℃ | %Z061105 | AI |  | 70CRB03 | [5 empty] | TBF04 | 9 | 10 |  |  | 70LCA30CT104 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-008
|  | 70LCC20CL102 | 5#低加水位2 | 5# LP heater level 2 | 70CRB01 | FCS0704 | 6 | 1 | 6 | AAI143-H | 4~20mA | N | %Z061106 | [5 empty] | 0 | 1 | m | %Z061106 | AI |  | 70CRB03 | [5 empty] | TBF04 | 11 | 12 |  |  | 70LCC20CL102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC20CT101 | 5#低加正常疏水温度 | 5# LP heater drain water temperature | 70CRB01 | FCS0704 | 6 | 1 | 7 | AAI143-H | 4~20mA | N | %Z061107 | [5 empty] | 0 | 200 | ℃ | %Z061107 | AI |  | 70CRB03 | [5 empty] | TBF04 | 13 | 142 |  |  | 70LCC20CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-012
|  | 70LBQ20AA104XQ11 | 主蒸汽减温减压器A电动减压调节阀位置反馈 | Main steam pressure reducer desuperheater A pressure reduciong regulating MOV position feddback | 70CRB01 | FCS0704 | 6 | 1 | 8 | AAI143-H | 4~20mA | N | %Z061108 | [5 empty] | 0 | 100 | % | %Z061108 | AI | 4W | 70CRB03 | [5 empty] | TBF04 | 16 | 15 |  |  | 70LBQ20AA104 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-005
|  | 70LBQ20AA103XQ11 | 主蒸汽减温减压器A电动减温调节阀位置反馈 | Main steam pressure reducer desuperheater A temperature reduciong regulating MOV position feddback | 70CRB01 | FCS0704 | 6 | 1 | 9 | AAI143-H | 4~20mA | N | %Z061109 | [5 empty] | 0 | 100 | % | %Z061109 | AI | 4W | 70CRB03 | [5 empty] | TBF04 | 18 | 17 |  |  | 70LBQ20AA103 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-005
|  | 70LBR10AA101XQ11 | 3#抽汽电动调节阀位置指令 | 3# extraction steam regulating MOV position feedback | 70CRB01 | FCS0704 | 6 | 1 | 10 | AAI143-H | 4~20mA | N | %Z061110 | [5 empty] | 0 | 100 | % | %Z061110 | AI | 4W | 70CRB03 | [5 empty] | TBF04 | 20 | 19 |  |  | 70LBR10AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-004
|  | 70LBR20AA102XQ11 | #2级调整抽汽减温减压器D电动减压调节阀位置反馈 | #2 regulated extraction steam pressure reducer desuperheater D pressure reduciong regulating MOV position feddback | 70CRB01 | FCS0704 | 6 | 1 | 11 | AAI143-H | 4~20mA | N | %Z061111 | [5 empty] | 0 | 100 | % | %Z061111 | AI | 4W | 70CRB03 | [5 empty] | TBF04 | 22 | 21 |  |  | 70LBR20AA102 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-002
|  | 70LBQ20AA102XQ11 | #1级非调整抽汽减温减压器C电动减压调节阀位置反馈 | #1 non-regulated extraction steam pressure reducer desuperheater C pressure reduciong regulating MOV position feddback | 70CRB01 | FCS0704 | 6 | 1 | 12 | AAI143-H | 4~20mA | N | %Z061112 | [5 empty] | 0 | 100 | % | %Z061112 | AI | 4W | 70CRB03 | [5 empty] | TBF04 | 24 | 23 |  |  | 70LBQ20AA102 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-005
|  | 70LBQ20AA106XQ11 | 中压联箱至低压联箱减温减压器E电动减压调节阀位置反馈 | MP steam header to LP steam header pressure reducer desuperheater E pressure reduciong regulating MOV position feddback | 70CRB01 | FCS0704 | 6 | 1 | 13 | AAI143-H | 4~20mA | N | %Z061113 | [5 empty] | 0 | 100 | % | %Z061113 | AI | 4W | 70CRB03 | [5 empty] | TBF04 | 26 | 25 |  |  | 70LBQ20AA106 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-005
|  | 70MAC01AA051XQ11 | 排汽缸减温水气动调节阀位置反馈 | Exhaust hood attemperating water regulating PV position feedback | 70CRB01 | FCS0704 | 6 | 1 | 14 | AAI143-H | 4~20mA | N | %Z061114 | [5 empty] | 0 | 100 | % | %Z061114 | AI | 4W | 70CRB03 | [5 empty] | TBF04 | 28 | 27 |  |  | 70MAC01AA051 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-009
|  | 70MAW10AA051XQ11 | 汽封母管供汽气动调节阀位置反馈 | Gland seal main steam regulating PV position feedback | 70CRB01 | FCS0704 | 6 | 1 | 15 | AAI143-H | 4~20mA | N | %Z061115 | [5 empty] | 0 | 100 | % | %Z061115 | AI | 4W | 70CRB03 | [5 empty] | TBF04 | 30 | 29 |  |  | 70MAW10AA051 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-016
[5 empty] | 70CRB01 | FCS0704 | 6 | 1 | 16 | AAI143-H | 4~20mA | N | %Z061116 | [8 empty] | %Z061116 | AI |  | 70CRB03 | [5 empty] | TBF04 | 31 | 32
|  | 70LAB70CT101 | 2#高加出口给水温度 | 2# HP heater outlet feedwater temp. | 70CRB01 | FCS0704 | 6 | 2 | 1 | AAI143-H | 4~20mA | N | %Z062101 | [5 empty] | 0 | 300 | ℃ | %Z062101 | AI |  | 70CRB03 | [5 empty] | TBF05 | 1 | 2 |  |  | 70LAB70CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-006
|  | 70LAD20CL102 | 2#高加水位2 | 2# HP heater level 2 | 70CRB01 | FCS0704 | 6 | 2 | 2 | AAI143-H | 4~20mA | N | %Z062102 | [5 empty] | 0 | 1.5 | m | %Z062102 | AI |  | 70CRB03 | [5 empty] | TBF05 | 3 | 4 |  |  | 70LAD20CL102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-011
|  | 70LAD20CT101 | 2#高加正常疏水温度 | 2# HP heater drain water temperature | 70CRB01 | FCS0704 | 6 | 2 | 3 | AAI143-H | 4~20mA | N | %Z062103 | [5 empty] | 0 | 300 | ℃ | %Z062103 | AI |  | 70CRB03 | [5 empty] | TBF05 | 5 | 6 |  |  | 70LAD20CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-011
|  | 70LAD20AA101XQ11 | 2#高加正常疏水气动调节阀位置反馈 | 2# HP heater drain water regulating PV position feedback | 70CRB01 | FCS0704 | 6 | 2 | 4 | AAI143-H | 4~20mA | N | %Z062104 | [5 empty] | 0 | 100 | % | %Z062104 | AI | 4W | 70CRB03 | [5 empty] | TBF05 | 8 | 7 |  |  | 70LAD20AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-011
|  | 70LCC30AA102XQ11 | 4#低加危急疏水气动调节阀位置反馈 | 4# LP heater emergency drain water regulating PV position feedback | 70CRB01 | FCS0704 | 6 | 2 | 5 | AAI143-H | 4~20mA | N | %Z062105 | [5 empty] | 0 | 100 | % | %Z062105 | AI | 4W | 70CRB03 | [5 empty] | TBF05 | 10 | 9 |  |  | 70LCC30AA102 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-012
|  | 70LCC20AA102XQ11 | 5#低加危急疏水气动调节阀位置反馈 | 5# LP heater emergency drain water regulating PV position feedback | 70CRB01 | FCS0704 | 6 | 2 | 6 | AAI143-H | 4~20mA | N | %Z062106 | [5 empty] | 0 | 100 | % | %Z062106 | AI | 4W | 70CRB03 | [5 empty] | TBF05 | 12 | 11 |  |  | 70LCC20AA102 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-012
|  | 70LCC10AA102XQ11 | 6#低加危急疏水气动调节阀位置反馈 | 6# LP heater emergency drain water regulating PV position feedback | 70CRB01 | FCS0704 | 6 | 2 | 7 | AAI143-H | 4~20mA | N | %Z062107 | [5 empty] | 0 | 100 | % | %Z062107 | AI | 4W | 70CRB03 | [5 empty] | TBF05 | 14 | 13 |  |  | 70LCC10AA102 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-012
|  | 70LBR20AA103XQ11 | #2级调整抽汽减温减压器D电动减温调节阀位置反馈 | #2 regulated extraction steam pressure reducer desuperheater D temperature reduciong regulating MOV position feddback | 70CRB01 | FCS0704 | 6 | 2 | 8 | AAI143-H | 4~20mA | N | %Z062108 | [5 empty] | 0 | 100 | % | %Z062108 | AI | 4W | 70CRB03 | [5 empty] | TBF05 | 16 | 15 |  |  | 70LBR20AA103 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-002
|  | 70LBQ20AA101XQ11 | #1级非调整抽汽减温减压器C电动减温调节阀位置反馈 | #1 non-regulated extraction steam pressure reducer desuperheater C temperature reduciong regulating MOV position feddback | 70CRB01 | FCS0704 | 6 | 2 | 9 | AAI143-H | 4~20mA | N | %Z062109 | [5 empty] | 0 | 100 | % | %Z062109 | AI | 4W | 70CRB03 | [5 empty] | TBF05 | 18 | 17 |  |  | 70LBQ20AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-005
|  | 70LBQ20AA105XQ11 | 中压联箱至低压联箱减温减压器E电动减温调节阀位置反馈 | MP steam header to LP steam header pressure reducer desuperheater E temperature reduciong regulating MOV position feddback | 70CRB01 | FCS0704 | 6 | 2 | 10 | AAI143-H | 4~20mA | N | %Z062110 | [5 empty] | 0 | 100 | % | %Z062110 | AI | 4W | 70CRB03 | [5 empty] | TBF05 | 20 | 19 |  |  | 70LBQ20AA105 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-005
|  | 70LCA33AA101XQ11 | 本体疏水集管B1减温水气动调节阀位置反馈 | Body drain header nozzle B1 attemperating water regulating PV position feedback | 70CRB01 | FCS0704 | 6 | 2 | 11 | AAI143-H | 4~20mA | N | %Z062111 | [5 empty] | 0 | 100 | % | %Z062111 | AI | 4W | 70CRB03 | [5 empty] | TBF05 | 22 | 21 |  |  | 70LCA33AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-009
|  | 70MAW50AA051XQ11 | 汽封母管供汽溢流气动调节阀位置反馈 | Gland seal main steam overflow regulating PV position feedback | 70CRB01 | FCS0704 | 6 | 2 | 12 | AAI143-H | 4~20mA | N | %Z062112 | [5 empty] | 0 | 100 | % | %Z062112 | AI | 4W | 70CRB03 | [5 empty] | TBF05 | 24 | 23 |  |  | 70MAW50AA051 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-016
[5 empty] | 70CRB01 | FCS0704 | 6 | 2 | 13 | AAI143-H | 4~20mA | N | %Z062113 | [8 empty] | %Z062113 | AI |  | 70CRB03 | [5 empty] | TBF05 | 25 | 26
[5 empty] | 70CRB01 | FCS0704 | 6 | 2 | 14 | AAI143-H | 4~20mA | N | %Z062114 | [8 empty] | %Z062114 | AI |  | 70CRB03 | [5 empty] | TBF05 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 6 | 2 | 15 | AAI143-H | 4~20mA | N | %Z062115 | [8 empty] | %Z062115 | AI |  | 70CRB03 | [5 empty] | TBF05 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 6 | 2 | 16 | AAI143-H | 4~20mA | N | %Z062116 | [8 empty] | %Z062116 | AI |  | 70CRB03 | [5 empty] | TBF05 | 31 | 32
|  | 70MKA20CT101 | 6#定子槽内线棒层间温度 | Temperature between stator bars in 6# slot | 70CRB01 | FCS0704 | 2 | 4 | 1 | AAR181-S | PT100 | N | %Z024101 | [5 empty] | 0 | 180 | ℃ | %Z024101 | AI |  | 70CRB01 | [5 empty] | TBF01 | 1 | 2 | 3 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA20CT102 | 12#定子槽内线棒层间温度 | Temperature between stator bars in 12# slot | 70CRB01 | FCS0704 | 2 | 4 | 2 | AAR181-S | PT100 | N | %Z024102 | [5 empty] | 0 | 180 | ℃ | %Z024102 | AI |  | 70CRB01 | [5 empty] | TBF01 | 4 | 5 | 6 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA20CT103 | 18#定子槽内线棒层间温度 | Temperature between stator bars in 18# slot | 70CRB01 | FCS0704 | 2 | 4 | 3 | AAR181-S | PT100 | N | %Z024103 | [5 empty] | 0 | 180 | ℃ | %Z024103 | AI |  | 70CRB01 | [5 empty] | TBF01 | 7 | 8 | 9 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA20CT104 | 24#定子槽内线棒层间温度 | Temperature between stator bars in 24# slot | 70CRB01 | FCS0704 | 2 | 4 | 4 | AAR181-S | PT100 | N | %Z024104 | [5 empty] | 0 | 180 | ℃ | %Z024104 | AI |  | 70CRB01 | [5 empty] | TBF01 | 10 | 11 | 12 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA20CT105 | 30#定子槽内线棒层间温度 | Temperature between stator bars in 30# slot | 70CRB01 | FCS0704 | 2 | 4 | 5 | AAR181-S | PT100 | N | %Z024105 | [5 empty] | 0 | 180 | ℃ | %Z024105 | AI |  | 70CRB01 | [5 empty] | TBF01 | 13 | 14 | 15 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA20CT106 | 36#定子槽内线棒层间温度 | Temperature between stator bars in 36# slot | 70CRB01 | FCS0704 | 2 | 4 | 6 | AAR181-S | PT100 | N | %Z024106 | [5 empty] | 0 | 180 | ℃ | %Z024106 | AI |  | 70CRB01 | [5 empty] | TBF01 | 16 | 17 | 18 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA20CT107 | 42#定子槽内线棒层间温度 | Temperature between stator bars in 42# slot | 70CRB01 | FCS0704 | 2 | 4 | 7 | AAR181-S | PT100 | N | %Z024107 | [5 empty] | 0 | 180 | ℃ | %Z024107 | AI |  | 70CRB01 | [5 empty] | TBF01 | 19 | 20 | 21 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MAV71CT103 | 发电机汽端轴承排油温度 | Generator bearing(turbine side) drain oil temperature | 70CRB01 | FCS0704 | 2 | 4 | 8 | AAR181-S | PT100 | N | %Z024108 | [5 empty] | 0 | 200 | ℃ | %Z024108 | AI |  | 70CRB01 | [5 empty] | TBF01 | 22 | 23 | 24 |  | 70MAV71CT103 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-006
|  | 70MAV71CT104 | 发电机励端轴承排油温度 | Generator bearing(exciter side) drain oil temperature | 70CRB01 | FCS0704 | 2 | 4 | 9 | AAR181-S | PT100 | N | %Z024109 | [5 empty] | 0 | 200 | ℃ | %Z024109 | AI |  | 70CRB01 | [5 empty] | TBF01 | 25 | 26 | 27 |  | 70MAV71CT104 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-006
|  | 70MAW10CT102 | 汽封供汽支管温度2 | Gland seal by-Pass steam temperature 2 | 70CRB01 | FCS0704 | 2 | 4 | 10 | AAR181-S | PT100 | N | %Z024110 | [5 empty] | 0 | 400 | ℃ | %Z024110 | AI |  | 70CRB01 | [5 empty] | TBF01 | 28 | 29 | 30 |  | 70MAW10CT102 | PT100 | RTD | [8 empty] | MCS | D |  | K0204-016
[5 empty] | 70CRB01 | FCS0704 | 2 | 4 | 11 | AAR181-S | PT100 | N | %Z024111 | [8 empty] | %Z024111 | AI |  | 70CRB01 | [5 empty] | TBF01 | 31 | 32 | 33
[5 empty] | 70CRB01 | FCS0704 | 2 | 4 | 12 | AAR181-S | PT100 | N | %Z024112 | [8 empty] | %Z024112 | AI |  | 70CRB01 | [5 empty] | TBF01 | 34 | 35 | 36
|  | 70MAV35CT101 | 顶轴油泵母管出口温度 | Jacking oil pump main outlet temperature | 70CRB01 | FCS0704 | 3 | 4 | 1 | AAR181-S | PT100 | N | %Z034101 | [5 empty] | 0 | 100 | ℃ | %Z034101 | AI |  | 70CRB01 | [5 empty] | TBF02 | 1 | 2 | 3 |  | 70MAV01GC001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV10CT101 | 润滑油箱温度 | Lube oil tank temperature | 70CRB01 | FCS0704 | 3 | 4 | 2 | AAR181-S | PT100 | N | %Z034102 | [5 empty] | 0 | 100 | ℃ | %Z034102 | AI |  | 70CRB01 | [5 empty] | TBF02 | 4 | 5 | 6 |  | 70MAV01GC001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV41CT101 | 冷油器出口母管温度 | Oil cooler outlet main pipe temperature | 70CRB01 | FCS0704 | 3 | 4 | 3 | AAR181-S | PT100 | N | %Z034103 | [5 empty] | 0 | 100 | ℃ | %Z034103 | AI |  | 70CRB01 | [5 empty] | TBF02 | 7 | 8 | 9 |  | 70MAV01GC001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MKA20CT108 | 48#定子槽内线棒层间温度 | Temperature between stator bars in 48# slot | 70CRB01 | FCS0704 | 3 | 4 | 4 | AAR181-S | PT100 | N | %Z034104 | [5 empty] | 0 | 180 | ℃ | %Z034104 | AI |  | 70CRB01 | [5 empty] | TBF02 | 10 | 11 | 12 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA20CT109 | 54#定子槽内线棒层间温度 | Temperature between stator bars in 54# slot | 70CRB01 | FCS0704 | 3 | 4 | 5 | AAR181-S | PT100 | N | %Z034105 | [5 empty] | 0 | 180 | ℃ | %Z034105 | AI |  | 70CRB01 | [5 empty] | TBF02 | 13 | 14 | 15 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA20CT110 | 60#定子槽内线棒层间温度 | Temperature between stator bars in 60# slot | 70CRB01 | FCS0704 | 3 | 4 | 6 | AAR181-S | PT100 | N | %Z034106 | [5 empty] | 0 | 180 | ℃ | %Z034106 | AI |  | 70CRB01 | [5 empty] | TBF02 | 16 | 17 | 18 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA20CT111 | 66#定子槽内线棒层间温度 | Temperature between stator bars in 66# slot | 70CRB01 | FCS0704 | 3 | 4 | 7 | AAR181-S | PT100 | N | %Z034107 | [5 empty] | 0 | 180 | ℃ | %Z034107 | AI |  | 70CRB01 | [5 empty] | TBF02 | 19 | 20 | 21 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA20CT112 | 72#定子槽内线棒层间温度 | Temperature between stator bars in 72# slot | 70CRB01 | FCS0704 | 3 | 4 | 8 | AAR181-S | PT100 | N | %Z034108 | [5 empty] | 0 | 180 | ℃ | %Z034108 | AI |  | 70CRB01 | [5 empty] | TBF02 | 22 | 23 | 24 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
[5 empty] | 70CRB01 | FCS0704 | 3 | 4 | 9 | AAR181-S | PT100 | N | %Z034109 | [8 empty] | %Z034109 | AI |  | 70CRB01 | [5 empty] | TBF02 | 25 | 26 | 27
[5 empty] | 70CRB01 | FCS0704 | 3 | 4 | 10 | AAR181-S | PT100 | N | %Z034110 | [8 empty] | %Z034110 | AI |  | 70CRB01 | [5 empty] | TBF02 | 28 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 3 | 4 | 11 | AAR181-S | PT100 | N | %Z034111 | [8 empty] | %Z034111 | AI |  | 70CRB01 | [5 empty] | TBF02 | 31 | 32 | 33
[5 empty] | 70CRB01 | FCS0704 | 3 | 4 | 12 | AAR181-S | PT100 | N | %Z034112 | [8 empty] | %Z034112 | AI |  | 70CRB01 | [5 empty] | TBF02 | 34 | 35 | 36
|  | 70MAX01CT201 | EH油箱油温 | EH oil tank oil temperature | 70CRB01 | FCS0704 | 4 | 4 | 1 | AAR181-S | PT100 | N | %Z044101 | [5 empty] | 0 | 100 | ℃ | %Z044101 | AI |  | 70CRB01 | [5 empty] | TBF03 | 1 | 2 | 3 |  | 70MAX01GC001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MKA34CT101 | 出线端定子铁心轭部温度1 | Temperature 1 of outlet end stator core yoke | 70CRB01 | FCS0704 | 4 | 4 | 2 | AAR181-S | PT100 | N | %Z044102 | [5 empty] | 0 | 180 | ℃ | %Z044102 | AI |  | 70CRB01 | [5 empty] | TBF03 | 4 | 5 | 6 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA34CT102 | 出线端定子铁心齿部温度1 | Temperature 1 of outlet end stator core tooth | 70CRB01 | FCS0704 | 4 | 4 | 3 | AAR181-S | PT100 | N | %Z044103 | [5 empty] | 0 | 180 | ℃ | %Z044103 | AI |  | 70CRB01 | [5 empty] | TBF03 | 7 | 8 | 9 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA34CT107 | 非出线端定子铁心轭部温度1 | Temperature 1 of non-outlet end stator core yoke | 70CRB01 | FCS0704 | 4 | 4 | 4 | AAR181-S | PT100 | N | %Z044104 | [5 empty] | 0 | 180 | ℃ | %Z044104 | AI |  | 70CRB01 | [5 empty] | TBF03 | 10 | 11 | 12 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA34CT108 | 非出线端定子铁心齿部温度1 | Temperature 1 of non-outlet end stator core tooth | 70CRB01 | FCS0704 | 4 | 4 | 5 | AAR181-S | PT100 | N | %Z044105 | [5 empty] | 0 | 180 | ℃ | %Z044105 | AI |  | 70CRB01 | [5 empty] | TBF03 | 13 | 14 | 15 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKD11CT101 | 发电机汽端轴承瓦温 | Generator bearing(turbine side) bush temperature | 70CRB01 | FCS0704 | 4 | 4 | 6 | AAR181-S | PT100 | N | %Z044106 | [5 empty] | 0 | 200 | ℃ | %Z044106 | AI |  | 70CRB01 | [5 empty] | TBF03 | 16 | 17 | 18 |  | 70MKD11CT101 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-006
|  | 70MKD12CT101 | 发电机励端轴承瓦温 | Generator bearing(exciter side) bush temperature | 70CRB01 | FCS0704 | 4 | 4 | 7 | AAR181-S | PT100 | N | %Z044107 | [5 empty] | 0 | 200 | ℃ | %Z044107 | AI |  | 70CRB01 | [5 empty] | TBF03 | 19 | 20 | 21 |  | 70MKD12CT101 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-006
|  | 70MAW10CT101 | 汽封供汽支管温度1 | Gland seal by-Pass steam temperature 1 | 70CRB01 | FCS0704 | 4 | 4 | 8 | AAR181-S | PT100 | N | %Z044108 | [5 empty] | 0 | 400 | ℃ | %Z044108 | AI |  | 70CRB01 | [5 empty] | TBF03 | 22 | 23 | 24 |  | 70MAW10CT101 | PT100 | RTD | [8 empty] | MCS | D |  | K0204-016
[5 empty] | 70CRB01 | FCS0704 | 4 | 4 | 9 | AAR181-S | PT100 | N | %Z044109 | [8 empty] | %Z044109 | AI |  | 70CRB01 | [5 empty] | TBF03 | 25 | 26 | 27
[5 empty] | 70CRB01 | FCS0704 | 4 | 4 | 10 | AAR181-S | PT100 | N | %Z044110 | [8 empty] | %Z044110 | AI |  | 70CRB01 | [5 empty] | TBF03 | 28 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 4 | 4 | 11 | AAR181-S | PT100 | N | %Z044111 | [8 empty] | %Z044111 | AI |  | 70CRB01 | [5 empty] | TBF03 | 31 | 32 | 33
[5 empty] | 70CRB01 | FCS0704 | 4 | 4 | 12 | AAR181-S | PT100 | N | %Z044112 | [8 empty] | %Z044112 | AI |  | 70CRB01 | [5 empty] | TBF03 | 34 | 35 | 36
|  | 70MKA34CT103 | 出线端定子铁心轭部温度2 | Temperature 2 of outlet end stator core yoke | 70CRB01 | FCS0704 | 5 | 4 | 1 | AAR181-S | PT100 | N | %Z054101 | [5 empty] | 0 | 100 | ℃ | %Z054101 | AI |  | 70CRB01 | [5 empty] | TBG02 | 1 | 2 | 3 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA34CT104 | 出线端定子铁心齿部温度2 | Temperature 2 of outlet end stator core tooth | 70CRB01 | FCS0704 | 5 | 4 | 2 | AAR181-S | PT100 | N | %Z054102 | [5 empty] | 0 | 180 | ℃ | %Z054102 | AI |  | 70CRB01 | [5 empty] | TBG02 | 4 | 5 | 6 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA34CT109 | 非出线端定子铁心轭部温度2 | Temperature 2 of non-outlet end stator core yoke | 70CRB01 | FCS0704 | 5 | 4 | 3 | AAR181-S | PT100 | N | %Z054103 | [5 empty] | 0 | 180 | ℃ | %Z054103 | AI |  | 70CRB01 | [5 empty] | TBG02 | 7 | 8 | 9 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA34CT110 | 非出线端定子铁心齿部温度2 | Temperature 2 of non-outlet end stator core tooth | 70CRB01 | FCS0704 | 5 | 4 | 4 | AAR181-S | PT100 | N | %Z054104 | [5 empty] | 0 | 180 | ℃ | %Z054104 | AI |  | 70CRB01 | [5 empty] | TBG02 | 10 | 11 | 12 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA38CT101 | 出线端齿压板温度1 | Temperature 1 of outlet end finger plate | 70CRB01 | FCS0704 | 5 | 4 | 5 | AAR181-S | PT100 | N | %Z054105 | [5 empty] | 0 | 180 | ℃ | %Z054105 | AI |  | 70CRB01 | [5 empty] | TBG02 | 13 | 14 | 15 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA38CT103 | 非出线端齿压板温度1 | Temperature 1 of non-outlet end finger plate | 70CRB01 | FCS0704 | 5 | 4 | 6 | AAR181-S | PT100 | N | %Z054106 | [5 empty] | 0 | 180 | ℃ | %Z054106 | AI |  | 70CRB01 | [5 empty] | TBG02 | 16 | 17 | 18 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA75CT101 | 出线端冷风温度 | Temperature of outlet end cold air | 70CRB01 | FCS0704 | 5 | 4 | 7 | AAR181-S | PT100 | N | %Z054107 | [5 empty] | 0 | 180 | ℃ | %Z054107 | AI |  | 70CRB01 | [5 empty] | TBG02 | 19 | 20 | 21 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA75CT103 | 本体段冷风温度 | Temperature of body section cold air | 70CRB01 | FCS0704 | 5 | 4 | 8 | AAR181-S | PT100 | N | %Z054108 | [5 empty] | 0 | 180 | ℃ | %Z054108 | AI |  | 70CRB01 | [5 empty] | TBG02 | 22 | 23 | 24 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA75CT105 | 非出线端冷风温度 | Temperature of non-outlet end cold air | 70CRB01 | FCS0704 | 5 | 4 | 9 | AAR181-S | PT100 | N | %Z054109 | [5 empty] | 0 | 180 | ℃ | %Z054109 | AI |  | 70CRB01 | [5 empty] | TBG02 | 25 | 26 | 27 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA75CT107 | 刷架冷风温度 | Brush carrier cold air temperature | 70CRB01 | FCS0704 | 5 | 4 | 10 | AAR181-S | PT100 | N | %Z054110 | [5 empty] | 0 | 180 | ℃ | %Z054110 | AI |  | 70CRB01 | [5 empty] | TBG02 | 28 | 29 | 30 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
[5 empty] | 70CRB01 | FCS0704 | 5 | 4 | 11 | AAR181-S | PT100 | N | %Z054111 | [8 empty] | %Z054111 | AI |  | 70CRB01 | [5 empty] | TBG02 | 31 | 32 | 33
[5 empty] | 70CRB01 | FCS0704 | 5 | 4 | 12 | AAR181-S | PT100 | N | %Z054112 | [8 empty] | %Z054112 | AI |  | 70CRB01 | [5 empty] | TBG02 | 34 | 35 | 36
|  | 70MKA34CT105 | 出线端定子铁心轭部温度3 | Temperature 3 of outlet end stator core yoke | 70CRB01 | FCS0704 | 6 | 4 | 1 | AAR181-S | PT100 | N | %Z064101 | [5 empty] | 0 | 100 | ℃ | %Z064101 | AI |  | 70CRB01 | [5 empty] | TBG03 | 1 | 2 | 3 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA34CT106 | 出线端定子铁心齿部温度3 | Temperature 3 of outlet end stator core tooth | 70CRB01 | FCS0704 | 6 | 4 | 2 | AAR181-S | PT100 | N | %Z064102 | [5 empty] | 0 | 180 | ℃ | %Z064102 | AI |  | 70CRB01 | [5 empty] | TBG03 | 4 | 5 | 6 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA34CT111 | 非出线端定子铁心轭部温度3 | Temperature 3 of non-outlet end stator core yoke | 70CRB01 | FCS0704 | 6 | 4 | 3 | AAR181-S | PT100 | N | %Z064103 | [5 empty] | 0 | 180 | ℃ | %Z064103 | AI |  | 70CRB01 | [5 empty] | TBG03 | 7 | 8 | 9 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA34CT112 | 非出线端定子铁心齿部温度3 | Temperature 3 of non-outlet end stator core tooth | 70CRB01 | FCS0704 | 6 | 4 | 4 | AAR181-S | PT100 | N | %Z064104 | [5 empty] | 0 | 180 | ℃ | %Z064104 | AI |  | 70CRB01 | [5 empty] | TBG03 | 10 | 11 | 12 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA38CT102 | 出线端齿压板温度2 | Temperature 2 of outlet end finger plate | 70CRB01 | FCS0704 | 6 | 4 | 5 | AAR181-S | PT100 | N | %Z064105 | [5 empty] | 0 | 180 | ℃ | %Z064105 | AI |  | 70CRB01 | [5 empty] | TBG03 | 13 | 14 | 15 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA38CT104 | 非出线端齿压板温度2 | Temperature 2 of non-outlet end finger plate | 70CRB01 | FCS0704 | 6 | 4 | 6 | AAR181-S | PT100 | N | %Z064106 | [5 empty] | 0 | 180 | ℃ | %Z064106 | AI |  | 70CRB01 | [5 empty] | TBG03 | 16 | 17 | 18 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA75CT102 | 出线端热风温度 | Temperature of outlet end hot air | 70CRB01 | FCS0704 | 6 | 4 | 7 | AAR181-S | PT100 | N | %Z064107 | [5 empty] | 0 | 180 | ℃ | %Z064107 | AI |  | 70CRB01 | [5 empty] | TBG03 | 19 | 20 | 21 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA75CT104 | 非出线端热风温度 | Temperature of non-outlet end hot air | 70CRB01 | FCS0704 | 6 | 4 | 8 | AAR181-S | PT100 | N | %Z064108 | [5 empty] | 0 | 180 | ℃ | %Z064108 | AI |  | 70CRB01 | [5 empty] | TBG03 | 22 | 23 | 24 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
|  | 70MKA75CT106 | 刷架热风温度 | Brush carrier hot air temperature | 70CRB01 | FCS0704 | 6 | 4 | 9 | AAR181-S | PT100 | N | %Z064109 | [5 empty] | 0 | 180 | ℃ | %Z064109 | AI |  | 70CRB01 | [5 empty] | TBG03 | 25 | 26 | 27 |  | 70MKA20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
[5 empty] | 70CRB01 | FCS0704 | 6 | 4 | 10 | AAR181-S | PT100 | N | %Z064110 | [8 empty] | %Z064110 | AI |  | 70CRB01 | [5 empty] | TBG03 | 28 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 6 | 4 | 11 | AAR181-S | PT100 | N | %Z064111 | [8 empty] | %Z064111 | AI |  | 70CRB01 | [5 empty] | TBG03 | 31 | 32 | 33
[5 empty] | 70CRB01 | FCS0704 | 6 | 4 | 12 | AAR181-S | PT100 | N | %Z064112 | [8 empty] | %Z064112 | AI |  | 70CRB01 | [5 empty] | TBG03 | 34 | 35 | 36
|  | 70LBA10CT101 | 主蒸汽温度1(汽机侧) | Main steam temperature 1(turbine side) | 70CRB01 | FCS0704 | 2 | 5 | 1 | AAT141-S | TC | N | %Z025101 | [5 empty] | 0 | 600 | ℃ | %Z025101 | AI |  | 70CRB01 | [5 empty] | TBG01 | 1 | 2 |  |  | 70LBA10CT101 | K | TC | [8 empty] | DAS | D |  | K0204-001
|  | 70LBA10CT102 | 主蒸汽温度2(汽机侧) | Main steam temperature 2(turbine side) | 70CRB01 | FCS0704 | 2 | 5 | 2 | AAT141-S | TC | N | %Z025102 | [5 empty] | 0 | 600 | ℃ | %Z025102 | AI |  | 70CRB01 | [5 empty] | TBG01 | 3 | 4 |  |  | 70LBA10CT102 | K | TC | [8 empty] | DAS | D |  | K0204-001
|  | 70LBR20CT108 | 低压联箱蒸汽温度 | LP steam header steam temperature | 70CRB01 | FCS0704 | 2 | 5 | 3 | AAT141-S | TC | N | %Z025103 | [5 empty] | 0 | 300 | ℃ | %Z025103 | AI |  | 70CRB01 | [5 empty] | TBG01 | 5 | 6 |  |  | 70LBR20CT108 | K | TC | [8 empty] | DAS | D |  | K0204-002
|  | 70LBQ20CT114 | 中压联箱蒸汽温度 | MP steam header steam temperature | 70CRB01 | FCS0704 | 2 | 5 | 4 | AAT141-S | TC | N | %Z025104 | [5 empty] | 0 | 300 | ℃ | %Z025104 | AI |  | 70CRB01 | [5 empty] | TBG01 | 7 | 8 |  |  | 70LBQ20CT114 | K | TC | [8 empty] | DAS | D |  | K0204-005
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 5 | AAT141-S | TC | N | %Z025105 | [8 empty] | %Z025105 | AI |  | 70CRB01 | [5 empty] | TBG01 | 9 | 10
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 6 | AAT141-S | TC | N | %Z025106 | [8 empty] | %Z025106 | AI |  | 70CRB01 | [5 empty] | TBG01 | 11 | 12
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 7 | AAT141-S | TC | N | %Z025107 | [8 empty] | %Z025107 | AI |  | 70CRB01 | [5 empty] | TBG01 | 13 | 14
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 8 | AAT141-S | TC | N | %Z025108 | [8 empty] | %Z025108 | AI |  | 70CRB01 | [5 empty] | TBG01 | 15 | 16
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 9 | AAT141-S | TC | N | %Z025109 | [8 empty] | %Z025109 | AI |  | 70CRB01 | [5 empty] | TBG01 | 17 | 18
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 10 | AAT141-S | TC | N | %Z025110 | [8 empty] | %Z025110 | AI |  | 70CRB01 | [5 empty] | TBG01 | 19 | 20
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 11 | AAT141-S | TC | N | %Z025111 | [8 empty] | %Z025111 | AI |  | 70CRB01 | [5 empty] | TBG01 | 21 | 22
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 12 | AAT141-S | TC | N | %Z025112 | [8 empty] | %Z025112 | AI |  | 70CRB01 | [5 empty] | TBG01 | 23 | 24
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 13 | AAT141-S | TC | N | %Z025113 | [8 empty] | %Z025113 | AI |  | 70CRB01 | [5 empty] | TBG01 | 25 | 26
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 14 | AAT141-S | TC | N | %Z025114 | [8 empty] | %Z025114 | AI |  | 70CRB01 | [5 empty] | TBG01 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 15 | AAT141-S | TC | N | %Z025115 | [8 empty] | %Z025115 | AI |  | 70CRB01 | [5 empty] | TBG01 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 2 | 5 | 16 | AAT141-S | TC | N | %Z025116 | [8 empty] | %Z025116 | AI |  | 70CRB01 | [5 empty] | TBG01 | 31 | 32
|  | 70LAD10AA101YQ01 | 1#高加正常疏水气动调节阀控制指令 | 1# HP heater drain water regulating PV position command | 70CRB01 | FCS0704 | 5 | 3 | 1 | AAI543-H | 4~20mA | N | %Z053101 | [5 empty] | 0 | 100 | % | %Z053101 | AO |  | 70CRB03 | [5 empty] | TBF03 | 1 | 2 |  |  | 70LAD10AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-011
|  | 70LCC30AA101YQ01 | 4#低加正常疏水气动调节阀控制指令 | 4# LP heater drain water regulating PV position command | 70CRB01 | FCS0704 | 5 | 3 | 2 | AAI543-H | 4~20mA | N | %Z053102 | [5 empty] | 0 | 100 | % | %Z053102 | AO |  | 70CRB03 | [5 empty] | TBF03 | 3 | 4 |  |  | 70LCC30AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC20AA101YQ01 | 5#低加正常疏水气动调节阀控制指令 | 5# LP heater drain water regulating PV position command | 70CRB01 | FCS0704 | 5 | 3 | 3 | AAI543-H | 4~20mA | N | %Z053103 | [5 empty] | 0 | 100 | % | %Z053103 | AO |  | 70CRB03 | [5 empty] | TBF03 | 5 | 6 |  |  | 70LCC20AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC10AA101YQ01 | 6#低加正常疏水气动调节阀控制指令 | 6# LP heater drain water regulating PV position command | 70CRB01 | FCS0704 | 5 | 3 | 4 | AAI543-H | 4~20mA | N | %Z053104 | [5 empty] | 0 | 100 | % | %Z053104 | AO |  | 70CRB03 | [5 empty] | TBF03 | 7 | 8 |  |  | 70LCC10AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-012
|  | 70LBQ20AA104YQ01 | 主蒸汽减温减压器A电动减压调节阀控制指令 | Main steam pressure reducer desuperheater A pressure reduciong regulating MOV position command | 70CRB01 | FCS0704 | 5 | 3 | 5 | AAI543-H | 4~20mA | N | %Z053105 | [5 empty] | 0 | 100 | % | %Z053105 | AO |  | 70CRB03 | [5 empty] | TBF03 | 9 | 10 |  |  | 70LBQ20AA104 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-005
|  | 70LBQ20AA103YQ01 | 主蒸汽减温减压器A电动减温调节阀控制指令 | Main steam pressure reducer desuperheater A temperature reduciong regulating MOV position command | 70CRB01 | FCS0704 | 5 | 3 | 6 | AAI543-H | 4~20mA | N | %Z053106 | [5 empty] | 0 | 100 | % | %Z053106 | AO |  | 70CRB03 | [5 empty] | TBF03 | 11 | 12 |  |  | 70LBQ20AA103 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-005
|  | 70LBS30AA101YQ01 | 4#抽汽电动调节阀控制指令 | 4# extraction steam regulating MOV position command | 70CRB01 | FCS0704 | 5 | 3 | 7 | AAI543-H | 4~20mA | N | %Z053107 | [5 empty] | 0 | 100 | % | %Z053107 | AO |  | 70CRB03 | [5 empty] | TBF03 | 13 | 14 |  |  | 70LBS30AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-004
[5 empty] | 70CRB01 | FCS0704 | 5 | 3 | 8 | AAI543-H | 4~20mA | N | %Z053108 | [8 empty] | %Z053108 | AO |  | 70CRB03 | [5 empty] | TBF03 | 15 | 16
|  | 70CJJ01XQ04 | 遥控负荷给定 | Remote control load given | 70CRB01 | FCS0704 | 5 | 3 | 9 | AAI543-H | 4~20mA | N | %Z053109 | [5 empty] | 0 | 100 | MW | %Z053109 | AO |  | 70CRB03 | [5 empty] | TBF03 | 17 | 18 |  |  | 70CJJ01 | 4～20mA | AO | [8 empty] | MCS | D |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
|  | 70LBR20AA102YQ01 | #2级调整抽汽减温减压器D电动减压调节阀控制指令 | #2 regulated extraction steam pressure reducer desuperheater D pressure reduciong regulating MOV position command | 70CRB01 | FCS0704 | 5 | 3 | 10 | AAI543-H | 4~20mA | N | %Z053110 | [5 empty] | 0 | 100 | % | %Z053110 | AO |  | 70CRB03 | [5 empty] | TBF03 | 19 | 20 |  |  | 70LBR20AA102 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-002
|  | 70LBQ20AA102YQ01 | #1级非调整抽汽减温减压器C电动减压调节阀控制指令 | #1 non-regulated extraction steam pressure reducer desuperheater C pressure reduciong regulating MOV position command | 70CRB01 | FCS0704 | 5 | 3 | 11 | AAI543-H | 4~20mA | N | %Z053111 | [5 empty] | 0 | 100 | % | %Z053111 | AO |  | 70CRB03 | [5 empty] | TBF03 | 21 | 22 |  |  | 70LBQ20AA102 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-005
|  | 70LBQ20AA106YQ01 | 中压联箱至低压联箱减温减压器E电动减压调节阀控制指令 | MP steam header to LP steam header pressure reducer desuperheater E pressure reduciong regulating MOV position command | 70CRB01 | FCS0704 | 5 | 3 | 12 | AAI543-H | 4~20mA | N | %Z053112 | [5 empty] | 0 | 100 | % | %Z053112 | AO |  | 70CRB03 | [5 empty] | TBF03 | 23 | 24 |  |  | 70LBQ20AA106 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-005
|  | 70MAC01AA051YQ01 | 排汽缸减温水气动调节阀控制指令 | Exhaust hood attemperating water regulating PV position command | 70CRB01 | FCS0704 | 5 | 3 | 13 | AAI543-H | 4~20mA | N | %Z053113 | [5 empty] | 0 | 100 | % | %Z053113 | AO |  | 70CRB03 | [5 empty] | TBF03 | 25 | 26 |  |  | 70MAC01AA051 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-009
|  | 70MAW10AA051YQ01 | 汽封母管供汽气动调节阀控制指令 | Gland seal main steam regulating PV position command | 70CRB01 | FCS0704 | 5 | 3 | 14 | AAI543-H | 4~20mA | N | %Z053114 | [5 empty] | 0 | 100 | % | %Z053114 | AO |  | 70CRB03 | [5 empty] | TBF03 | 27 | 28 |  |  | 70MAW10AA051 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-016
[5 empty] | 70CRB01 | FCS0704 | 5 | 3 | 15 | AAI543-H | 4~20mA | N | %Z053115 | [8 empty] | %Z053115 | AO |  | 70CRB03 | [5 empty] | TBF03 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 5 | 3 | 16 | AAI543-H | 4~20mA | N | %Z053116 | [8 empty] | %Z053116 | AO |  | 70CRB03 | [5 empty] | TBF03 | 31 | 32
|  | 70LAD20AA101YQ01 | 2#高加正常疏水气动调节阀控制指令 | 2# HP heater drain water regulating PV position command | 70CRB01 | FCS0704 | 6 | 3 | 1 | AAI543-H | 4~20mA | N | %Z063101 | [5 empty] | 0 | 100 | % | %Z063101 | AO |  | 70CRB03 | [5 empty] | TBF06 | 1 | 2 |  |  | 70LAD20AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-011
|  | 70LCC30AA102YQ01 | 4#低加危急疏水气动调节阀控制指令 | 4# LP heater emergency drain water regulating PV position command | 70CRB01 | FCS0704 | 6 | 3 | 2 | AAI543-H | 4~20mA | N | %Z063102 | [5 empty] | 0 | 100 | % | %Z063102 | AO |  | 70CRB03 | [5 empty] | TBF06 | 3 | 4 |  |  | 70LCC30AA102 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC20AA102YQ01 | 5#低加危急疏水气动调节阀控制指令 | 5# LP heater emergency drain water regulating PV position command | 70CRB01 | FCS0704 | 6 | 3 | 3 | AAI543-H | 4~20mA | N | %Z063103 | [5 empty] | 0 | 100 | % | %Z063103 | AO |  | 70CRB03 | [5 empty] | TBF06 | 5 | 6 |  |  | 70LCC20AA102 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-012
|  | 70LCC10AA102YQ01 | 6#低加危急疏水气动调节阀控制指令 | 6# LP heater emergency drain water regulating PV position command | 70CRB01 | FCS0704 | 6 | 3 | 4 | AAI543-H | 4~20mA | N | %Z063104 | [5 empty] | 0 | 100 | % | %Z063104 | AO |  | 70CRB03 | [5 empty] | TBF06 | 7 | 8 |  |  | 70LCC10AA102 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-012
|  | 70LBR20AA104YQ01 | 主蒸汽减温减压器B电动减压调节阀控制指令 | Main steam pressure reducer desuperheater B pressure reduciong regulating MOV position command | 70CRB01 | FCS0704 | 6 | 3 | 5 | AAI543-H | 4~20mA | N | %Z063105 | [5 empty] | 0 | 100 | % | %Z063105 | AO |  | 70CRB03 | [5 empty] | TBF06 | 9 | 10 |  |  | 70LBR20AA104 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-002
|  | 70LBR20AA105YQ01 | 主蒸汽减温减压器B电动减温调节阀控制指令 | Main steam pressure reducer desuperheater B temperature reduciong regulating MOV position command | 70CRB01 | FCS0704 | 6 | 3 | 6 | AAI543-H | 4~20mA | N | %Z063106 | [5 empty] | 0 | 100 | % | %Z063106 | AO |  | 70CRB03 | [5 empty] | TBF06 | 11 | 12 |  |  | 70LBR20AA105 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-002
|  | 70LBR10AA101YQ01 | 3#抽汽电动调节阀控制指令 | 3# extraction steam regulating MOV position command | 70CRB01 | FCS0704 | 6 | 3 | 7 | AAI543-H | 4~20mA | N | %Z063107 | [5 empty] | 0 | 100 | % | %Z063107 | AO |  | 70CRB03 | [5 empty] | TBF06 | 13 | 14 |  |  | 70LBR10AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-004
|  | 70LBR20AA103YQ01 | #2级调整抽汽减温减压器D电动减温调节阀控制指令 | #2 regulated extraction steam pressure reducer desuperheater D temperature reduciong regulating MOV position command | 70CRB01 | FCS0704 | 6 | 3 | 8 | AAI543-H | 4~20mA | N | %Z063108 | [5 empty] | 0 | 100 | % | %Z063108 | AO |  | 70CRB03 | [5 empty] | TBF06 | 15 | 16 |  |  | 70LBR20AA103 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-002
|  | 70LBQ20AA101YQ01 | #1级非调整抽汽减温减压器C电动减温调节阀控制指令 | #1 non-regulated extraction steam pressure reducer desuperheater C temperature reduciong regulating MOV position command | 70CRB01 | FCS0704 | 6 | 3 | 9 | AAI543-H | 4~20mA | N | %Z063109 | [5 empty] | 0 | 100 | % | %Z063109 | AO |  | 70CRB03 | [5 empty] | TBF06 | 17 | 18 |  |  | 70LBQ20AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-005
|  | 70LBQ20AA105YQ01 | 中压联箱至低压联箱减温减压器E电动减温调节阀控制指令 | MP steam header to LP steam header pressure reducer desuperheater E temperature reduciong regulating MOV position command | 70CRB01 | FCS0704 | 6 | 3 | 10 | AAI543-H | 4~20mA | N | %Z063110 | [5 empty] | 0 | 100 | % | %Z063110 | AO |  | 70CRB03 | [5 empty] | TBF06 | 19 | 20 |  |  | 70LBQ20AA105 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-005
|  | 70LCA33AA101YQ01 | 本体疏水集管B1减温水气动调节阀控制指令 | Body drain header nozzle B1 attemperating water regulating PV position command | 70CRB01 | FCS0704 | 6 | 3 | 11 | AAI543-H | 4~20mA | N | %Z063111 | [5 empty] | 0 | 100 | % | %Z063111 | AO |  | 70CRB03 | [5 empty] | TBF06 | 21 | 22 |  |  | 70LCA33AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-009
|  | 70MAW50AA051YQ01 | 汽封母管供汽溢流气动调节阀控制指令 | Gland seal main steam overflow regulating PV position command | 70CRB01 | FCS0704 | 6 | 3 | 12 | AAI543-H | 4~20mA | N | %Z063112 | [5 empty] | 0 | 100 | % | %Z063112 | AO |  | 70CRB03 | [5 empty] | TBF06 | 23 | 24 |  |  | 70MAW50AA051 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-016
[5 empty] | 70CRB01 | FCS0704 | 6 | 3 | 13 | AAI543-H | 4~20mA | N | %Z063113 | [8 empty] | %Z063113 | AO |  | 70CRB03 | [5 empty] | TBF06 | 25 | 26
[5 empty] | 70CRB01 | FCS0704 | 6 | 3 | 14 | AAI543-H | 4~20mA | N | %Z063114 | [8 empty] | %Z063114 | AO |  | 70CRB03 | [5 empty] | TBF06 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 6 | 3 | 15 | AAI543-H | 4~20mA | N | %Z063115 | [8 empty] | %Z063115 | AO |  | 70CRB03 | [5 empty] | TBF06 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 6 | 3 | 16 | AAI543-H | 4~20mA | N | %Z063116 | [8 empty] | %Z063116 | AO |  | 70CRB03 | [5 empty] | TBF06 | 31 | 32
|  | 70MAV21AP021XB01 | 1#主油泵运行 | 1# main oil pump running | 70CRB01 | FCS0704 | 2 | 6 | 1 | ADV151-P | SI | N | %Z026101 | [8 empty] | %Z026101 | DI |  | 70CRB03 | [5 empty] | TBG01 | 1 | 2 |  |  | 70MAV21AP021 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV21AP021XB11 | 1#主油泵停止 | 1# main oil pump stopped | 70CRB01 | FCS0704 | 2 | 6 | 2 | ADV151-P | SI | N | %Z026102 | [8 empty] | %Z026102 | DI |  | 70CRB03 | [5 empty] | TBG01 | 3 | 4 |  |  | 70MAV21AP021 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV21AP021XB21 | 1#主油泵远方控制允许 | 1# main oil pump remote control permitted | 70CRB01 | FCS0704 | 2 | 6 | 3 | ADV151-P | SI | N | %Z026103 | [8 empty] | %Z026103 | DI |  | 70CRB03 | [5 empty] | TBG01 | 5 | 6 |  |  | 70MAV21AP021 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV21AP021XB31 | 1#主油泵控制电源消失 | 1# main oil pump control circuit broken | 70CRB01 | FCS0704 | 2 | 6 | 4 | ADV151-P | SI | N | %Z026104 | [8 empty] | %Z026104 | DI |  | 70CRB03 | [5 empty] | TBG01 | 7 | 8 |  |  | 70MAV21AP021 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV21AP021XB32 | 1#主油泵故障输出 | 1# main oil pump fault output | 70CRB01 | FCS0704 | 2 | 6 | 5 | ADV151-P | SI | N | %Z026105 | [8 empty] | %Z026105 | DI |  | 70CRB03 | [5 empty] | TBG01 | 9 | 10 |  |  | 70MAV21AP021 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAX01AP001XB01 | 1# EH油泵运行状态反馈 | 1# EH oil pump running status feedback | 70CRB01 | FCS0704 | 2 | 6 | 6 | ADV151-P | SI | N | %Z026106 | [8 empty] | %Z026106 | DI |  | 70CRB03 | [5 empty] | TBG01 | 11 | 12 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP001XB11 | 1# EH油泵停止状态反馈 | 1# EH oil pump stopped status feedback | 70CRB01 | FCS0704 | 2 | 6 | 7 | ADV151-P | SI | N | %Z026107 | [8 empty] | %Z026107 | DI |  | 70CRB03 | [5 empty] | TBG01 | 13 | 14 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP001XB31 | 1# EH油泵电源故障 | 1# EH oil pump power fault | 70CRB01 | FCS0704 | 2 | 6 | 8 | ADV151-P | SI | N | %Z026108 | [8 empty] | %Z026108 | DI |  | 70CRB03 | [5 empty] | TBG01 | 15 | 16 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP011XB01 | 1# EH油循环泵运行状态反馈 | 1# EH oil circulating pump running status feedback | 70CRB01 | FCS0704 | 2 | 6 | 9 | ADV151-P | SI | N | %Z026109 | [8 empty] | %Z026109 | DI |  | 70CRB03 | [5 empty] | TBG01 | 17 | 18 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP011XB11 | 1# EH油循环泵停止状态反馈 | 1# EH oil circulating pump stopped status feedback | 70CRB01 | FCS0704 | 2 | 6 | 10 | ADV151-P | SI | N | %Z026110 | [8 empty] | %Z026110 | DI |  | 70CRB03 | [5 empty] | TBG01 | 19 | 20 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP011XB31 | 1# EH油循环泵电源故障 | 1# EH oil circulating pump power fault | 70CRB01 | FCS0704 | 2 | 6 | 11 | ADV151-P | SI | N | %Z026111 | [8 empty] | %Z026111 | DI |  | 70CRB03 | [5 empty] | TBG01 | 21 | 22 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AH001XB01 | EH油箱电加热器运行状态反馈 | EH oil tank heater running status feedback | 70CRB01 | FCS0704 | 2 | 6 | 12 | ADV151-P | SI | N | %Z026112 | [8 empty] | %Z026112 | DI |  | 70CRB03 | [5 empty] | TBG01 | 23 | 24 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AH001XB11 | EH油箱电加热器停止状态反馈 | EH oil tank heater stopped status feedback | 70CRB01 | FCS0704 | 2 | 6 | 13 | ADV151-P | SI | N | %Z026113 | [8 empty] | %Z026113 | DI |  | 70CRB03 | [5 empty] | TBG01 | 25 | 26 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AH001XB31 | EH油箱电加热器电源故障 | EH oil tank heater power fault | 70CRB01 | FCS0704 | 2 | 6 | 14 | ADV151-P | SI | N | %Z026114 | [8 empty] | %Z026114 | DI |  | 70CRB03 | [5 empty] | TBG01 | 27 | 28 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
[5 empty] | 70CRB01 | FCS0704 | 2 | 6 | 15 | ADV151-P | SI | N | %Z026115 | [8 empty] | %Z026115 | DI |  | 70CRB03 | [5 empty] | TBG01 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 2 | 6 | 16 | ADV151-P | SI | N | %Z026116 | [8 empty] | %Z026116 | DI |  | 70CRB03 | [5 empty] | TBG01 | 31 | 32
|  | 70CJJ01YB02 | 遥控功率已投 | Remote control power input | 70CRB01 | FCS0704 | 2 | 6 | 17 | ADV151-P | SI | N | %Z026117 | [8 empty] | %Z026117 | DI |  | 70CRB03 | [5 empty] | TBG01 | 33 | 34 |  |  | 70CJJ01 | NO | DI | [8 empty] | SCS | D |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
|  | 70CAA01YB17 | 汽机已遮断2 | Turbine tripped 2 | 70CRB01 | FCS0704 | 2 | 6 | 18 | ADV151-P | SI | N | %Z026118 | [8 empty] | %Z026118 | DI |  | 70CRB03 | [5 empty] | TBG01 | 35 | 36 |  |  | 70CAA01 | NO | DI | [8 empty] | SCS | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB18 | 汽机已遮断3 | Turbine tripped 3 | 70CRB01 | FCS0704 | 2 | 6 | 19 | ADV151-P | SI | N | %Z026119 | [8 empty] | %Z026119 | DI |  | 70CRB03 | [5 empty] | TBG01 | 37 | 38 |  |  | 70CAA01 | NO | DI | [8 empty] | SCS | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CFA01YB03 | 相对振动报警 | Relative vibration alarm | 70CRB01 | FCS0704 | 2 | 6 | 20 | ADV151-P | SI | N | %Z026120 | [8 empty] | %Z026120 | DI |  | 70CRB03 | [5 empty] | TBG01 | 39 | 40 |  |  | 70CFA01 | NO | DI | [8 empty] | DAS | D |  | K0203-001 | 汽机TSI控制柜 | Turbine TSI control cabinet
|  | 70CFA01YB05 | 轴向位移报警 | Rotor position alarm | 70CRB01 | FCS0704 | 2 | 6 | 21 | ADV151-P | SI | N | %Z026121 | [8 empty] | %Z026121 | DI |  | 70CRB03 | [5 empty] | TBG01 | 41 | 42 |  |  | 70CFA01 | NO | DI | [8 empty] | DAS | D |  | K0203-001 | 汽机TSI控制柜 | Turbine TSI control cabinet
|  | 70CSB11XB31 | 主厂房热控400VAC电源柜电源失电报警 | Main building I&C 400VAC power cabinet power lost alarm | 70CRB01 | FCS0704 | 2 | 6 | 22 | ADV151-P | SI | N | %Z026122 | [8 empty] | %Z026122 | DI |  | 70CRB03 | [5 empty] | TBG01 | 43 | 44 |  |  | 70CSB11 | NO | DI | [8 empty] | DAS | D |  |  | 主厂房热控400VAC电源柜A | Main building I&C 400VAC power cabinet A
|  | 70CSB11XB32 | 主厂房热控400VAC电源柜ATS主电源失去报警 | Main building I&C 400VAC power cabinet ATS main Power Lost Alarm | 70CRB01 | FCS0704 | 2 | 6 | 23 | ADV151-P | SI | N | %Z026123 | [8 empty] | %Z026123 | DI |  | 70CRB03 | [5 empty] | TBG01 | 45 | 46 |  |  | 70CSB11 | NO | DI | [8 empty] | DAS | D |  |  | 主厂房热控400VAC电源柜A | Main building I&C 400VAC power cabinet A
|  | 70CSB11XB33 | 主厂房热控400VAC电源柜ATS副电源失去报警 | Main building I&C 400VAC power cabinet A Vice Power Lost Alarm | 70CRB01 | FCS0704 | 2 | 6 | 24 | ADV151-P | SI | N | %Z026124 | [8 empty] | %Z026124 | DI |  | 70CRB03 | [5 empty] | TBG01 | 47 | 48 |  |  | 70CSB11 | NO | DI | [8 empty] | DAS | D |  |  | 主厂房热控400VAC电源柜A | Main building I&C 400VAC power cabinet A
|  | 70LBQ10AA201XB01 | 1#抽汽逆止阀全开状态 | 1# extraction steam check valve full opened status | 70CRB01 | FCS0704 | 2 | 6 | 25 | ADV151-P | SI | N | %Z026125 | [8 empty] | %Z026125 | DI |  | 70CRB03 | [5 empty] | TBG01 | 49 | 50 |  |  | 70LBQ10AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBQ10AA201XB11 | 1#抽汽逆止阀全关状态 | 1# extraction steam check valve full closed status | 70CRB01 | FCS0704 | 2 | 6 | 26 | ADV151-P | SI | N | %Z026126 | [8 empty] | %Z026126 | DI |  | 70CRB03 | [5 empty] | TBG01 | 51 | 52 |  |  | 70LBQ10AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBQ10AA402XB01 | 1#抽汽逆止阀后疏水阀全开状态 | Drain valve after 1# extraction steam check valve full opened status | 70CRB01 | FCS0704 | 2 | 6 | 27 | ADV151-P | SI | N | %Z026127 | [8 empty] | %Z026127 | DI |  | 70CRB03 | [5 empty] | TBG01 | 53 | 54 |  |  | 70LBQ10AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBQ10AA402XB11 | 1#抽汽逆止阀后疏水阀全关状态 | Drain valve after 1# extraction steam check valve full closed status | 70CRB01 | FCS0704 | 2 | 6 | 28 | ADV151-P | SI | N | %Z026128 | [8 empty] | %Z026128 | DI |  | 70CRB03 | [5 empty] | TBG01 | 55 | 56 |  |  | 70LBQ10AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-004
[5 empty] | 70CRB01 | FCS0704 | 2 | 6 | 29 | ADV151-P | SI | N | %Z026129 | [8 empty] | %Z026129 | DI |  | 70CRB03 | [5 empty] | TBG01 | 57 | 58
[5 empty] | 70CRB01 | FCS0704 | 2 | 6 | 30 | ADV151-P | SI | N | %Z026130 | [8 empty] | %Z026130 | DI |  | 70CRB03 | [5 empty] | TBG01 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 2 | 6 | 31 | ADV151-P | SI | N | %Z026131 | [8 empty] | %Z026131 | DI |  | 70CRB03 | [5 empty] | TBG01 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 2 | 6 | 32 | ADV151-P | SI | N | %Z026132 | [8 empty] | %Z026132 | DI |  | 70CRB03 | [5 empty] | TBG01 | 63 | 64
|  | A0LBA10AA001XB01 | 主蒸汽联络管电动阀全开状态 | Main steam contact pipe MOV full opened status | 70CRB01 | FCS0704 | 2 | 7 | 1 | ADV151-P | SI | N | %Z027101 | [8 empty] | %Z027101 | DI |  | 70CRB03 | [5 empty] | TBG02 | 1 | 2 |  |  | A0LBA10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | A0LBA10AA001XB11 | 主蒸汽联络管电动阀全关状态 | Main steam contact pipe MOV full closed status | 70CRB01 | FCS0704 | 2 | 7 | 2 | ADV151-P | SI | N | %Z027102 | [8 empty] | %Z027102 | DI |  | 70CRB03 | [5 empty] | TBG02 | 3 | 4 |  |  | A0LBA10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | A0LBA10AA001XB31 | 主蒸汽联络管电动阀故障 | Main steam contact pipe MOV fault | 70CRB01 | FCS0704 | 2 | 7 | 3 | ADV151-P | SI | N | %Z027103 | [8 empty] | %Z027103 | DI |  | 70CRB03 | [5 empty] | TBG02 | 5 | 6 |  |  | A0LBA10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | A0LBA10AA402XB01 | 主蒸汽联络管疏水阀全开状态 | Main steam contact pipe drain valve full opened status | 70CRB01 | FCS0704 | 2 | 7 | 4 | ADV151-P | SI | N | %Z027104 | [8 empty] | %Z027104 | DI |  | 70CRB03 | [5 empty] | TBG02 | 7 | 8 |  |  | A0LBA10AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | A0LBA10AA402XB11 | 主蒸汽联络管疏水阀全关状态 | Main steam contact pipe drain valve full closed status | 70CRB01 | FCS0704 | 2 | 7 | 5 | ADV151-P | SI | N | %Z027105 | [8 empty] | %Z027105 | DI |  | 70CRB03 | [5 empty] | TBG02 | 9 | 10 |  |  | A0LBA10AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA10AA002XB01 | 主蒸汽电动阀全开状态 | Main steam MOV full opened status | 70CRB01 | FCS0704 | 2 | 7 | 6 | ADV151-P | SI | N | %Z027106 | [8 empty] | %Z027106 | DI |  | 70CRB03 | [5 empty] | TBG02 | 11 | 12 |  |  | 70LBA10AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA10AA002XB11 | 主蒸汽电动阀全关状态 | Main steam MOV full closed status | 70CRB01 | FCS0704 | 2 | 7 | 7 | ADV151-P | SI | N | %Z027107 | [8 empty] | %Z027107 | DI |  | 70CRB03 | [5 empty] | TBG02 | 13 | 14 |  |  | 70LBA10AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA10AA002XB31 | 主蒸汽电动阀故障 | Main steam MOV fault | 70CRB01 | FCS0704 | 2 | 7 | 8 | ADV151-P | SI | N | %Z027108 | [8 empty] | %Z027108 | DI |  | 70CRB03 | [5 empty] | TBG02 | 15 | 16 |  |  | 70LBA10AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA10AA406XB01 | 主蒸汽电动阀前疏水阀全开状态 | Drain valve before main steam MOV full opened status | 70CRB01 | FCS0704 | 2 | 7 | 9 | ADV151-P | SI | N | %Z027109 | [8 empty] | %Z027109 | DI |  | 70CRB03 | [5 empty] | TBG02 | 17 | 18 |  |  | 70LBA10AA406 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA10AA406XB11 | 主蒸汽电动阀前疏水阀全关状态 | Drain valve before main steam MOV full closed status | 70CRB01 | FCS0704 | 2 | 7 | 10 | ADV151-P | SI | N | %Z027110 | [8 empty] | %Z027110 | DI |  | 70CRB03 | [5 empty] | TBG02 | 19 | 20 |  |  | 70LBA10AA406 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70MAX01CP013 | 1#冷油器回油滤器差压高 | 1# oil cooler return oil differential pressure H | 70CRB01 | FCS0704 | 2 | 7 | 11 | ADV151-P | SI | N | %Z027111 | [7 empty] | bar | %Z027111 | DI |  | 70CRB03 | [5 empty] | TBG02 | 21 | 22 |  |  | 70MAX01GC001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAX01CL001H | EH油箱油位高 | EH oil tank oil level H | 70CRB01 | FCS0704 | 2 | 7 | 12 | ADV151-P | SI | N | %Z027112 | [7 empty] | mm | %Z027112 | DI |  | 70CRB03 | [5 empty] | TBG02 | 23 | 24 |  |  | 70MAX01GC001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAX01CL001LL | EH油箱油位低低 | EH oil tank oil level LL | 70CRB01 | FCS0704 | 2 | 7 | 13 | ADV151-P | SI | N | %Z027113 | [7 empty] | mm | %Z027113 | DI |  | 70CRB03 | [5 empty] | TBG02 | 25 | 26 |  |  | 70MAX01GC001 | NO | DI |  |  |  |  | √ |  |  |  | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAX01CP004 | 1#冷油器前压力 | 1# oil cooler inlet pressure | 70CRB01 | FCS0704 | 2 | 7 | 14 | ADV151-P | SI | N | %Z027114 | [7 empty] | bar | %Z027114 | DI |  | 70CRB03 | [5 empty] | TBG02 | 27 | 28 |  |  | 70MAX01GC001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAX01CP011 | 1#控制油泵滤器差压高 | 1# control oil pump filter differential pressure H | 70CRB01 | FCS0704 | 2 | 7 | 15 | ADV151-P | SI | N | %Z027115 | [7 empty] | bar | %Z027115 | DI |  | 70CRB03 | [5 empty] | TBG02 | 29 | 30 |  |  | 70MAX01GC001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAA11CG101B | 主汽门(左)全关#2 | MSV(left) full close #2 | 70CRB01 | FCS0704 | 2 | 7 | 16 | ADV151-P | SI | N | %Z027116 | [8 empty] | %Z027116 | DI |  | 70CRB03 | [5 empty] | TBG02 | 31 | 32 |  |  | 70MAA11GC001 | NO | DI | [8 empty] | SCS | D |  | K0203-004 | 主汽门油动机(左)接线盒 | MSV actuator (left) junction box
|  | 70CAA01YB19 | 汽机已遮断4 | Turbine tripped 4 | 70CRB01 | FCS0704 | 2 | 7 | 17 | ADV151-P | SI | N | %Z027117 | [8 empty] | %Z027117 | DI |  | 70CRB03 | [5 empty] | TBG02 | 33 | 34 |  |  | 70CAA01 | NO | DI | [8 empty] | SCS | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB20 | 停机扩展至DCS | Trip expansion to DCS | 70CRB01 | FCS0704 | 2 | 7 | 18 | ADV151-P | SI | N | %Z027118 | [8 empty] | %Z027118 | DI |  | 70CRB03 | [5 empty] | TBG02 | 35 | 36 |  |  | 70CAA01 | NO | DI | [8 empty] | SCS | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CFA01YB07 | 差胀报警 | Differential expansion alarm | 70CRB01 | FCS0704 | 2 | 7 | 19 | ADV151-P | SI | N | %Z027119 | [8 empty] | %Z027119 | DI |  | 70CRB03 | [5 empty] | TBG02 | 37 | 38 |  |  | 70CFA01 | NO | DI | [8 empty] | DAS | D |  | K0203-001 | 汽机TSI控制柜 | Turbine TSI control cabinet
|  | 70CFA01YB09 | 偏心报警 | Eccentricity alarm | 70CRB01 | FCS0704 | 2 | 7 | 20 | ADV151-P | SI | N | %Z027120 | [8 empty] | %Z027120 | DI |  | 70CRB03 | [5 empty] | TBG02 | 39 | 40 |  |  | 70CFA01 | NO | DI | [8 empty] | DAS | D |  | K0203-001 | 汽机TSI控制柜 | Turbine TSI control cabinet
|  | 70CFA01YB10 | 零转速报警 | Zero rotation speed alarm | 70CRB01 | FCS0704 | 2 | 7 | 21 | ADV151-P | SI | N | %Z027121 | [8 empty] | %Z027121 | DI |  | 70CRB03 | [5 empty] | TBG02 | 41 | 42 |  |  | 70CFA01 | NO | DI | [8 empty] | DAS | D |  | K0203-001 | 汽机TSI控制柜 | Turbine TSI control cabinet
|  | 70CSB02XB31 | 主厂房热控220VAC电源柜电源失电报警 | Main building I&C 220VAC power cabinet power lost alarm | 70CRB01 | FCS0704 | 2 | 7 | 22 | ADV151-P | SI | N | %Z027122 | [8 empty] | %Z027122 | DI |  | 70CRB03 | [5 empty] | TBG02 | 43 | 44 |  |  | 70CSB02 | NO | DI | [8 empty] | DAS | D |  |  | 主厂房热控220VAC电源柜A | Main building I&C 220VAC power cabinet A
|  | 70CSB02XB32 | 主厂房热控220VAC电源柜ATS主电源失去报警 | Main building I&C 220VAC power cabinet ATS main Power Lost Alarm | 70CRB01 | FCS0704 | 2 | 7 | 23 | ADV151-P | SI | N | %Z027123 | [8 empty] | %Z027123 | DI |  | 70CRB03 | [5 empty] | TBG02 | 45 | 46 |  |  | 70CSB02 | NO | DI | [8 empty] | DAS | D |  |  | 主厂房热控220VAC电源柜A | Main building I&C 220VAC power cabinet A
|  | 70CSB02XB33 | 主厂房热控220VAC电源柜ATS副电源失去报警 | Main building I&C 220VAC power cabinet ATS Vice Power Lost Alarm | 70CRB01 | FCS0704 | 2 | 7 | 24 | ADV151-P | SI | N | %Z027124 | [8 empty] | %Z027124 | DI |  | 70CRB03 | [5 empty] | TBG02 | 47 | 48 |  |  | 70CSB02 | NO | DI | [8 empty] | DAS | D |  |  | 主厂房热控220VAC电源柜A | Main building I&C 220VAC power cabinet A
|  | 70LBQ10AA001XB01 | 1#抽汽电动阀全开状态 | 1# extraction steam MOV full opened status | 70CRB01 | FCS0704 | 2 | 7 | 25 | ADV151-P | SI | N | %Z027125 | [8 empty] | %Z027125 | DI |  | 70CRB03 | [5 empty] | TBG02 | 49 | 50 |  |  | 70LBQ10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBQ10AA001XB11 | 1#抽汽电动阀全关状态 | 1# extraction steam MOV full closed status | 70CRB01 | FCS0704 | 2 | 7 | 26 | ADV151-P | SI | N | %Z027126 | [8 empty] | %Z027126 | DI |  | 70CRB03 | [5 empty] | TBG02 | 51 | 52 |  |  | 70LBQ10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBQ10AA001XB31 | 1#抽汽电动阀故障 | 1# extraction steam MOV fault | 70CRB01 | FCS0704 | 2 | 7 | 27 | ADV151-P | SI | N | %Z027127 | [8 empty] | %Z027127 | DI |  | 70CRB03 | [5 empty] | TBG02 | 53 | 54 |  |  | 70LBQ10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70MAL41AA051XB01 | 1#抽汽逆止阀前疏水阀全开状态 | Drain valve before 1# extraction steam check valve full opened status | 70CRB01 | FCS0704 | 2 | 7 | 28 | ADV151-P | SI | N | %Z027128 | [8 empty] | %Z027128 | DI |  | 70CRB03 | [5 empty] | TBG02 | 55 | 56 |  |  | 70MAL41AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL41AA051XB11 | 1#抽汽逆止阀前疏水阀全关状态 | Drain valve before 1# extraction steam check valve full closed status | 70CRB01 | FCS0704 | 2 | 7 | 29 | ADV151-P | SI | N | %Z027129 | [8 empty] | %Z027129 | DI |  | 70CRB03 | [5 empty] | TBG02 | 57 | 58 |  |  | 70MAL41AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 2 | 7 | 30 | ADV151-P | SI | N | %Z027130 | [8 empty] | %Z027130 | DI |  | 70CRB03 | [5 empty] | TBG02 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 2 | 7 | 31 | ADV151-P | SI | N | %Z027131 | [8 empty] | %Z027131 | DI |  | 70CRB03 | [5 empty] | TBG02 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 2 | 7 | 32 | ADV151-P | SI | N | %Z027132 | [8 empty] | %Z027132 | DI |  | 70CRB03 | [5 empty] | TBG02 | 63 | 64
|  | 70MAV21AP022XB01 | 2#主油泵运行 | 2# main oil pump running | 70CRB01 | FCS0704 | 3 | 6 | 1 | ADV151-P | SI | N | %Z036101 | [8 empty] | %Z036101 | DI |  | 70CRB04 | [5 empty] | TBB01 | 1 | 2 |  |  | 70MAV21AP021 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV21AP022XB11 | 2#主油泵停止 | 2# main oil pump stopped | 70CRB01 | FCS0704 | 3 | 6 | 2 | ADV151-P | SI | N | %Z036102 | [8 empty] | %Z036102 | DI |  | 70CRB04 | [5 empty] | TBB01 | 3 | 4 |  |  | 70MAV21AP021 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV21AP022XB21 | 2#主油泵远方控制允许 | 2# main oil pump remote control permitted | 70CRB01 | FCS0704 | 3 | 6 | 3 | ADV151-P | SI | N | %Z036103 | [8 empty] | %Z036103 | DI |  | 70CRB04 | [5 empty] | TBB01 | 5 | 6 |  |  | 70MAV21AP021 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV21AP022XB31 | 2#主油泵控制电源消失 | 2# main oil pump control circuit broken | 70CRB01 | FCS0704 | 3 | 6 | 4 | ADV151-P | SI | N | %Z036104 | [8 empty] | %Z036104 | DI |  | 70CRB04 | [5 empty] | TBB01 | 7 | 8 |  |  | 70MAV21AP021 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV21AP022XB32 | 2#主油泵故障输出 | 2# main oil pump fault output | 70CRB01 | FCS0704 | 3 | 6 | 5 | ADV151-P | SI | N | %Z036105 | [8 empty] | %Z036105 | DI |  | 70CRB04 | [5 empty] | TBB01 | 9 | 10 |  |  | 70MAV21AP021 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV32AP001XB01 | 2#顶轴油泵运行 | 2# jacking oil pump running | 70CRB01 | FCS0704 | 3 | 6 | 6 | ADV151-P | SI | N | %Z036106 | [8 empty] | %Z036106 | DI |  | 70CRB04 | [5 empty] | TBB01 | 11 | 12 |  |  | 70MAV32AP001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV32AP001XB11 | 2#顶轴油泵停止 | 2# jacking oil pump stopped | 70CRB01 | FCS0704 | 3 | 6 | 7 | ADV151-P | SI | N | %Z036107 | [8 empty] | %Z036107 | DI |  | 70CRB04 | [5 empty] | TBB01 | 13 | 14 |  |  | 70MAV32AP001 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV32AP001XB21 | 2#顶轴油泵远方控制允许 | 2# jacking oil pump remote control permitted | 70CRB01 | FCS0704 | 3 | 6 | 8 | ADV151-P | SI | N | %Z036108 | [8 empty] | %Z036108 | DI |  | 70CRB04 | [5 empty] | TBB01 | 15 | 16 |  |  | 70MAV32AP001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV32AP001XB31 | 2#顶轴油泵控制电源消失 | 2# jacking oil pump control circuit broken | 70CRB01 | FCS0704 | 3 | 6 | 9 | ADV151-P | SI | N | %Z036109 | [8 empty] | %Z036109 | DI |  | 70CRB04 | [5 empty] | TBB01 | 17 | 18 |  |  | 70MAV32AP001 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV32AP001XB32 | 2#顶轴油泵故障输出 | 2# jacking oil pump fault output | 70CRB01 | FCS0704 | 3 | 6 | 10 | ADV151-P | SI | N | %Z036110 | [8 empty] | %Z036110 | DI |  | 70CRB04 | [5 empty] | TBB01 | 19 | 20 |  |  | 70MAV32AP001 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV82AN002XB01 | 2#排烟风机运行 | 2# exhaust smoke fan running | 70CRB01 | FCS0704 | 3 | 6 | 11 | ADV151-P | SI | N | %Z036111 | [8 empty] | %Z036111 | DI |  | 70CRB04 | [5 empty] | TBB01 | 21 | 22 |  |  | 70MAV82AN002 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV82AN002XB11 | 2#排烟风机停止 | 2# exhaust smoke fan stopped | 70CRB01 | FCS0704 | 3 | 6 | 12 | ADV151-P | SI | N | %Z036112 | [8 empty] | %Z036112 | DI |  | 70CRB04 | [5 empty] | TBB01 | 23 | 24 |  |  | 70MAV82AN002 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV82AN002XB21 | 2#排烟风机远方控制允许 | 2# exhaust smoke fan remote control permitted | 70CRB01 | FCS0704 | 3 | 6 | 13 | ADV151-P | SI | N | %Z036113 | [8 empty] | %Z036113 | DI |  | 70CRB04 | [5 empty] | TBB01 | 25 | 26 |  |  | 70MAV82AN002 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV82AN002XB31 | 2#排烟风机控制电源消失 | 2# exhaust smoke fan control circuit broken | 70CRB01 | FCS0704 | 3 | 6 | 14 | ADV151-P | SI | N | %Z036114 | [8 empty] | %Z036114 | DI |  | 70CRB04 | [5 empty] | TBB01 | 27 | 28 |  |  | 70MAV82AN002 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV82AN002XB32 | 2#排烟风机故障输出 | 2# exhaust smoke fan fault output | 70CRB01 | FCS0704 | 3 | 6 | 15 | ADV151-P | SI | N | %Z036115 | [8 empty] | %Z036115 | DI |  | 70CRB04 | [5 empty] | TBB01 | 29 | 30 |  |  | 70MAV82AN002 | NO | DI | [8 empty] | SCS | D |  | K0203-005
[5 empty] | 70CRB01 | FCS0704 | 3 | 6 | 16 | ADV151-P | SI | N | %Z036116 | [8 empty] | %Z036116 | DI |  | 70CRB04 | [5 empty] | TBB01 | 31 | 32
|  | 70MAV24CP001L | 直流油泵出口压力低 | DC oil pump outlet pressure L | 70CRB01 | FCS0704 | 3 | 6 | 17 | ADV151-P | SI | N | %Z036117 | [7 empty] | Mpa | %Z036117 | DI |  | 70CRB04 | [5 empty] | TBB01 | 33 | 34 |  |  | 70MAV01GC001 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV21CP006L | 2#主油泵出口压力低 | 2# main oil pump outlet pressure L | 70CRB01 | FCS0704 | 3 | 6 | 18 | ADV151-P | SI | N | %Z036118 | [7 empty] | Mpa | %Z036118 | DI |  | 70CRB04 | [5 empty] | TBB01 | 35 | 36 |  |  | 70MAV01GC001 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV21CP001L | 主油泵出口母管压力低 | Main oil pump outlet main pipe pressure L | 70CRB01 | FCS0704 | 3 | 6 | 19 | ADV151-P | SI | N | %Z036119 | [7 empty] | Mpa | %Z036119 | DI |  | 70CRB04 | [5 empty] | TBB01 | 37 | 38 |  |  | 70MAV01GC001 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV42CP019L | 润滑油母管压力低（交流试验） | Lube oil main pipe pressure L(AC test) | 70CRB01 | FCS0704 | 3 | 6 | 20 | ADV151-P | SI | N | %Z036120 | [8 empty] | %Z036120 | DI |  | 70CRB04 | [5 empty] | TBB01 | 39 | 40 |  |  | 70MAV01GC001 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAX01AP002XB01 | 2# EH油泵运行状态反馈 | 2# EH oil pump running status feedback | 70CRB01 | FCS0704 | 3 | 6 | 21 | ADV151-P | SI | N | %Z036121 | [8 empty] | %Z036121 | DI |  | 70CRB04 | [5 empty] | TBB01 | 41 | 42 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP002XB11 | 2# EH油泵停止状态反馈 | 2# EH oil pump stopped status feedback | 70CRB01 | FCS0704 | 3 | 6 | 22 | ADV151-P | SI | N | %Z036122 | [8 empty] | %Z036122 | DI |  | 70CRB04 | [5 empty] | TBB01 | 43 | 44 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP002XB31 | 2# EH油泵电源故障 | 2# EH oil pump power fault | 70CRB01 | FCS0704 | 3 | 6 | 23 | ADV151-P | SI | N | %Z036123 | [8 empty] | %Z036123 | DI |  | 70CRB04 | [5 empty] | TBB01 | 45 | 46 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP012XB01 | 2# EH油循环泵运行状态反馈 | 2# EH oil circulating pump running status feedback | 70CRB01 | FCS0704 | 3 | 6 | 24 | ADV151-P | SI | N | %Z036124 | [8 empty] | %Z036124 | DI |  | 70CRB04 | [5 empty] | TBB01 | 47 | 48 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP012XB11 | 2# EH油循环泵停止状态反馈 | 2# EH oil circulating pump stopped status feedback | 70CRB01 | FCS0704 | 3 | 6 | 25 | ADV151-P | SI | N | %Z036125 | [8 empty] | %Z036125 | DI |  | 70CRB04 | [5 empty] | TBB01 | 49 | 50 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP012XB31 | 2# EH油循环泵电源故障 | 2# EH oil circulating pump power fault | 70CRB01 | FCS0704 | 3 | 6 | 26 | ADV151-P | SI | N | %Z036126 | [8 empty] | %Z036126 | DI |  | 70CRB04 | [5 empty] | TBB01 | 51 | 52 |  |  | 70MAX01GH001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70LBQ20AA201XB01 | 2#抽汽逆止阀全开状态 | 2# extraction steam check valve full opened status | 70CRB01 | FCS0704 | 3 | 6 | 27 | ADV151-P | SI | N | %Z036127 | [8 empty] | %Z036127 | DI |  | 70CRB04 | [5 empty] | TBB01 | 53 | 54 |  |  | 70LBQ20AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA201XB11 | 2#抽汽逆止阀全关状态 | 2# extraction steam check valve full closed status | 70CRB01 | FCS0704 | 3 | 6 | 28 | ADV151-P | SI | N | %Z036128 | [8 empty] | %Z036128 | DI |  | 70CRB04 | [5 empty] | TBB01 | 55 | 56 |  |  | 70LBQ20AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA402XB01 | 2#抽汽电动阀前疏水阀全开状态 | 2# extraction steam MOV front drain vlave full opened status | 70CRB01 | FCS0704 | 3 | 6 | 29 | ADV151-P | SI | N | %Z036129 | [8 empty] | %Z036129 | DI |  | 70CRB04 | [5 empty] | TBB01 | 57 | 58 |  |  | 70LBQ20AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA402XB11 | 2#抽汽电动阀前疏水阀全关状态 | 2# extraction steam MOV front drain vlave full closed status | 70CRB01 | FCS0704 | 3 | 6 | 30 | ADV151-P | SI | N | %Z036130 | [8 empty] | %Z036130 | DI |  | 70CRB04 | [5 empty] | TBB01 | 59 | 60 |  |  | 70LBQ20AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-005
[5 empty] | 70CRB01 | FCS0704 | 3 | 6 | 31 | ADV151-P | SI | N | %Z036131 | [8 empty] | %Z036131 | DI |  | 70CRB04 | [5 empty] | TBB01 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 3 | 6 | 32 | ADV151-P | SI | N | %Z036132 | [8 empty] | %Z036132 | DI |  | 70CRB04 | [5 empty] | TBB01 | 63 | 64
|  | 70MAV35CP016H | 顶轴油滤油器差压高 | Jacking oil filter differential pressure H | 70CRB01 | FCS0704 | 3 | 7 | 1 | ADV151-P | SI | N | %Z037101 | [8 empty] | %Z037101 | DI |  | 70CRB04 | [5 empty] | TBB02 | 1 | 2 |  |  | 70MAV01GC001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV21CP005L | 1#主油泵出口压力低 | 1# main oil pump outlet pressure L | 70CRB01 | FCS0704 | 3 | 7 | 2 | ADV151-P | SI | N | %Z037102 | [7 empty] | Mpa | %Z037102 | DI |  | 70CRB04 | [5 empty] | TBB02 | 3 | 4 |  |  | 70MAV01GC001 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV10CT011L | 润滑油箱温度低 | Lube oil tank temperature L | 70CRB01 | FCS0704 | 3 | 7 | 3 | ADV151-P | SI | N | %Z037103 | [7 empty] | ℃ | %Z037103 | DI |  | 70CRB04 | [5 empty] | TBB02 | 5 | 6 |  |  | 70MAV01GC001 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV42CP012L | 润滑油母管压力低（直流试验） | Lube oil main pipe pressure L(DC test) | 70CRB01 | FCS0704 | 3 | 7 | 4 | ADV151-P | SI | N | %Z037104 | [8 empty] | %Z037104 | DI |  | 70CRB04 | [5 empty] | TBB02 | 7 | 8 |  |  | 70MAV01GC001 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV42CP013H | 润滑油滤油器差压高 | Lube oil filter differential pressure H | 70CRB01 | FCS0704 | 3 | 7 | 5 | ADV151-P | SI | N | %Z037105 | [7 empty] | Mpa | %Z037105 | DI |  | 70CRB04 | [5 empty] | TBB02 | 9 | 10 |  |  | 70MAV01GC001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70LBR20AA002XB01 | 主蒸汽低压旁路管道电动阀全开状态 | Main steam LP bypass pipe MOV full opened status | 70CRB01 | FCS0704 | 3 | 7 | 6 | ADV151-P | SI | N | %Z037106 | [8 empty] | %Z037106 | DI |  | 70CRB04 | [5 empty] | TBB02 | 11 | 12 |  |  | 70LBR20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA002XB11 | 主蒸汽低压旁路管道电动阀全关状态 | Main steam LP bypass pipe MOV full closed status | 70CRB01 | FCS0704 | 3 | 7 | 7 | ADV151-P | SI | N | %Z037107 | [8 empty] | %Z037107 | DI |  | 70CRB04 | [5 empty] | TBB02 | 13 | 14 |  |  | 70LBR20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA002XB31 | 主蒸汽低压旁路管道电动阀故障 | Main steam LP bypass pipe MOV fault | 70CRB01 | FCS0704 | 3 | 7 | 8 | ADV151-P | SI | N | %Z037108 | [8 empty] | %Z037108 | DI |  | 70CRB04 | [5 empty] | TBB02 | 15 | 16 |  |  | 70LBR20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA402XB01 | 主蒸汽低压旁路管道电动阀后疏水阀全开状态 | Drain valve after main steam LP bypass pipe MOV full opened status | 70CRB01 | FCS0704 | 3 | 7 | 9 | ADV151-P | SI | N | %Z037109 | [8 empty] | %Z037109 | DI |  | 70CRB04 | [5 empty] | TBB02 | 17 | 18 |  |  | 70LBR20AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA402XB11 | 主蒸汽低压旁路管道电动阀后疏水阀全关状态 | Drain valve after main steam LP bypass pipe MOV full closed status | 70CRB01 | FCS0704 | 3 | 7 | 10 | ADV151-P | SI | N | %Z037110 | [8 empty] | %Z037110 | DI |  | 70CRB04 | [5 empty] | TBB02 | 19 | 20 |  |  | 70LBR20AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBQ20AA003XB01 | 主蒸汽中压旁路管道电动阀全开状态 | Main steam MP bypass pipe MOV full opened status | 70CRB01 | FCS0704 | 3 | 7 | 11 | ADV151-P | SI | N | %Z037111 | [8 empty] | %Z037111 | DI |  | 70CRB04 | [5 empty] | TBB02 | 21 | 22 |  |  | 70LBQ20AA003 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA003XB11 | 主蒸汽中压旁路管道电动阀全关状态 | Main steam MP bypass pipe MOV full closed status | 70CRB01 | FCS0704 | 3 | 7 | 12 | ADV151-P | SI | N | %Z037112 | [8 empty] | %Z037112 | DI |  | 70CRB04 | [5 empty] | TBB02 | 23 | 24 |  |  | 70LBQ20AA003 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA003XB31 | 主蒸汽中压旁路管道电动阀故障 | Main steam MP bypass pipe MOV fault | 70CRB01 | FCS0704 | 3 | 7 | 13 | ADV151-P | SI | N | %Z037113 | [8 empty] | %Z037113 | DI |  | 70CRB04 | [5 empty] | TBB02 | 25 | 26 |  |  | 70LBQ20AA003 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBR20AA416XB01 | 主蒸汽中压旁路管道电动阀后疏水阀全开状态 | Drain valve after main steam MP bypass pipe MOV full opened status | 70CRB01 | FCS0704 | 3 | 7 | 14 | ADV151-P | SI | N | %Z037114 | [8 empty] | %Z037114 | DI |  | 70CRB04 | [5 empty] | TBB02 | 27 | 28 |  |  | 70LBR20AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBR20AA416XB11 | 主蒸汽中压旁路管道电动阀后疏水阀全关状态 | Drain valve after main steam MP bypass pipe MOV full closed status | 70CRB01 | FCS0704 | 3 | 7 | 15 | ADV151-P | SI | N | %Z037115 | [8 empty] | %Z037115 | DI |  | 70CRB04 | [5 empty] | TBB02 | 29 | 30 |  |  | 70LBR20AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70MAX01CP014 | 2#冷油器回油滤器差压高 | 2# oil cooler return oil differential pressure H | 70CRB01 | FCS0704 | 3 | 7 | 16 | ADV151-P | SI | N | %Z037116 | [7 empty] | bar | %Z037116 | DI |  | 70CRB04 | [5 empty] | TBB02 | 31 | 32 |  |  | 70MAX01GC001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAX01CL002L | EH油箱油位低 | EH oil tank oil level L | 70CRB01 | FCS0704 | 3 | 7 | 17 | ADV151-P | SI | N | %Z037117 | [7 empty] | mm | %Z037117 | DI |  | 70CRB04 | [5 empty] | TBB02 | 33 | 34 |  |  | 70MAX01GC001 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAX01CL002LLL | EH油箱油位低低低 | EH oil tank oil level LLL | 70CRB01 | FCS0704 | 3 | 7 | 18 | ADV151-P | SI | N | %Z037118 | [7 empty] | mm | %Z037118 | DI |  | 70CRB04 | [5 empty] | TBB02 | 35 | 36 |  |  | 70MAX01GC001 | NO | DI | [5 empty] | √ |  |  | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAX01CP005 | 2#冷油器前压力 | 2# oil cooler inlet pressure | 70CRB01 | FCS0704 | 3 | 7 | 19 | ADV151-P | SI | N | %Z037119 | [7 empty] | bar | %Z037119 | DI |  | 70CRB04 | [5 empty] | TBB02 | 37 | 38 |  |  | 70MAX01GC001 | NO | DI | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAX01CP012 | 2#控制油泵滤器差压高 | 2# control oil pump filter differential pressure H | 70CRB01 | FCS0704 | 3 | 7 | 20 | ADV151-P | SI | N | %Z037120 | [7 empty] | bar | %Z037120 | DI |  | 70CRB04 | [5 empty] | TBB02 | 39 | 40 |  |  | 70MAX01GC001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
|  | 70MAA21CG101B | 主汽门(右)全关#2 | MSV(right) full close #2 | 70CRB01 | FCS0704 | 3 | 7 | 21 | ADV151-P | SI | N | %Z037121 | [8 empty] | %Z037121 | DI |  | 70CRB04 | [5 empty] | TBB02 | 41 | 42 |  |  | 70MAA21GC001 | NO | DI | [8 empty] | SCS | D |  | K0203-004 | 主汽门油动机(右)接线盒 | MSV actuator (right) junction box
|  | 70LBQ20AA001XB01 | 2#抽汽电动阀全开状态 | 2# extraction steam MOV full opened status | 70CRB01 | FCS0704 | 3 | 7 | 22 | ADV151-P | SI | N | %Z037122 | [8 empty] | %Z037122 | DI |  | 70CRB04 | [5 empty] | TBB02 | 43 | 44 |  |  | 70LBQ20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA001XB11 | 2#抽汽电动阀全关状态 | 2# extraction steam MOV full closed status | 70CRB01 | FCS0704 | 3 | 7 | 23 | ADV151-P | SI | N | %Z037123 | [8 empty] | %Z037123 | DI |  | 70CRB04 | [5 empty] | TBB02 | 45 | 46 |  |  | 70LBQ20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA001XB31 | 2#抽汽电动阀故障 | 2# extraction steam MOV fault | 70CRB01 | FCS0704 | 3 | 7 | 24 | ADV151-P | SI | N | %Z037124 | [8 empty] | %Z037124 | DI |  | 70CRB04 | [5 empty] | TBB02 | 47 | 48 |  |  | 70LBQ20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70MAL43AA051XB01 | 2#抽汽和#1级非调整抽汽逆止阀前疏水阀全开状态 | Drain valve before 2# extraction steam and #1 non-adjusting extraction steam check valve full opened status | 70CRB01 | FCS0704 | 3 | 7 | 25 | ADV151-P | SI | N | %Z037125 | [8 empty] | %Z037125 | DI |  | 70CRB04 | [5 empty] | TBB02 | 49 | 50 |  |  | 70MAL43AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL43AA051XB11 | 2#抽汽和#1级非调整抽汽逆止阀前疏水阀全关状态 | Drain valve before 2# extraction steam and #1 non-adjusting extraction steam check valve full closed status | 70CRB01 | FCS0704 | 3 | 7 | 26 | ADV151-P | SI | N | %Z037126 | [8 empty] | %Z037126 | DI |  | 70CRB04 | [5 empty] | TBB02 | 51 | 52 |  |  | 70MAL43AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 3 | 7 | 27 | ADV151-P | SI | N | %Z037127 | [8 empty] | %Z037127 | DI |  | 70CRB04 | [5 empty] | TBB02 | 53 | 54
[5 empty] | 70CRB01 | FCS0704 | 3 | 7 | 28 | ADV151-P | SI | N | %Z037128 | [8 empty] | %Z037128 | DI |  | 70CRB04 | [5 empty] | TBB02 | 55 | 56
[5 empty] | 70CRB01 | FCS0704 | 3 | 7 | 29 | ADV151-P | SI | N | %Z037129 | [8 empty] | %Z037129 | DI |  | 70CRB04 | [5 empty] | TBB02 | 57 | 58
[5 empty] | 70CRB01 | FCS0704 | 3 | 7 | 30 | ADV151-P | SI | N | %Z037130 | [8 empty] | %Z037130 | DI |  | 70CRB04 | [5 empty] | TBB02 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 3 | 7 | 31 | ADV151-P | SI | N | %Z037131 | [8 empty] | %Z037131 | DI |  | 70CRB04 | [5 empty] | TBB02 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 3 | 7 | 32 | ADV151-P | SI | N | %Z037132 | [8 empty] | %Z037132 | DI |  | 70CRB04 | [5 empty] | TBB02 | 63 | 64
|  | 70MAV24AP001XB01 | 直流油泵运行 | DC oil pump running | 70CRB01 | FCS0704 | 4 | 6 | 1 | ADV151-P | SI | N | %Z046101 | [8 empty] | %Z046101 | DI |  | 70CRB04 | [5 empty] | TBC01 | 1 | 2 |  |  | 70MAV24AP001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV24AP001XB11 | 直流油泵停止 | DC oil pump stopped | 70CRB01 | FCS0704 | 4 | 6 | 2 | ADV151-P | SI | N | %Z046102 | [8 empty] | %Z046102 | DI |  | 70CRB04 | [5 empty] | TBC01 | 3 | 4 |  |  | 70MAV24AP001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV24AP001XB21 | 直流油泵远方控制允许 | DC oil pump remote control permitted | 70CRB01 | FCS0704 | 4 | 6 | 3 | ADV151-P | SI | N | %Z046103 | [8 empty] | %Z046103 | DI |  | 70CRB04 | [5 empty] | TBC01 | 5 | 6 |  |  | 70MAV24AP001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV24AP001XB31 | 直流油泵故障 | DC oil pump fault | 70CRB01 | FCS0704 | 4 | 6 | 4 | ADV151-P | SI | N | %Z046104 | [8 empty] | %Z046104 | DI |  | 70CRB04 | [5 empty] | TBC01 | 7 | 8 |  |  | 70MAV24AP001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV31AP001XB01 | 1#顶轴油泵运行 | 1# jacking oil pump running | 70CRB01 | FCS0704 | 4 | 6 | 5 | ADV151-P | SI | N | %Z046105 | [8 empty] | %Z046105 | DI |  | 70CRB04 | [5 empty] | TBC01 | 9 | 10 |  |  | 70MAV31AP001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV31AP001XB11 | 1#顶轴油泵停止 | 1# jacking oil pump stopped | 70CRB01 | FCS0704 | 4 | 6 | 6 | ADV151-P | SI | N | %Z046106 | [8 empty] | %Z046106 | DI |  | 70CRB04 | [5 empty] | TBC01 | 11 | 12 |  |  | 70MAV31AP001 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV31AP001XB21 | 1#顶轴油泵远方控制允许 | 1# jacking oil pump remote control permitted | 70CRB01 | FCS0704 | 4 | 6 | 7 | ADV151-P | SI | N | %Z046107 | [8 empty] | %Z046107 | DI |  | 70CRB04 | [5 empty] | TBC01 | 13 | 14 |  |  | 70MAV31AP001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV31AP001XB31 | 1#顶轴油泵控制电源消失 | 1# jacking oil pump control circuit broken | 70CRB01 | FCS0704 | 4 | 6 | 8 | ADV151-P | SI | N | %Z046108 | [8 empty] | %Z046108 | DI |  | 70CRB04 | [5 empty] | TBC01 | 15 | 16 |  |  | 70MAV31AP001 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV31AP001XB32 | 1#顶轴油泵故障输出 | 1# jacking oil pump fault output | 70CRB01 | FCS0704 | 4 | 6 | 9 | ADV151-P | SI | N | %Z046109 | [8 empty] | %Z046109 | DI |  | 70CRB04 | [5 empty] | TBC01 | 17 | 18 |  |  | 70MAV31AP001 | NC | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV82AN001XB01 | 1#排烟风机运行 | 1# exhaust smoke fan running | 70CRB01 | FCS0704 | 4 | 6 | 10 | ADV151-P | SI | N | %Z046110 | [8 empty] | %Z046110 | DI |  | 70CRB04 | [5 empty] | TBC01 | 19 | 20 |  |  | 70MAV82AN001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV82AN001XB11 | 1#排烟风机停止 | 1# exhaust smoke fan stopped | 70CRB01 | FCS0704 | 4 | 6 | 11 | ADV151-P | SI | N | %Z046111 | [8 empty] | %Z046111 | DI |  | 70CRB04 | [5 empty] | TBC01 | 21 | 22 |  |  | 70MAV82AN001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV82AN001XB21 | 1#排烟风机远方控制允许 | 1# exhaust smoke fan remote control permitted | 70CRB01 | FCS0704 | 4 | 6 | 12 | ADV151-P | SI | N | %Z046112 | [8 empty] | %Z046112 | DI |  | 70CRB04 | [5 empty] | TBC01 | 23 | 24 |  |  | 70MAV82AN001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV82AN001XB31 | 1#排烟风机控制电源消失 | 1# exhaust smoke fan control circuit broken | 70CRB01 | FCS0704 | 4 | 6 | 13 | ADV151-P | SI | N | %Z046113 | [8 empty] | %Z046113 | DI |  | 70CRB04 | [5 empty] | TBC01 | 25 | 26 |  |  | 70MAV82AN001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
|  | 70MAV82AN001XB32 | 1#排烟风机故障输出 | 1# exhaust smoke fan fault output | 70CRB01 | FCS0704 | 4 | 6 | 14 | ADV151-P | SI | N | %Z046114 | [8 empty] | %Z046114 | DI |  | 70CRB04 | [5 empty] | TBC01 | 27 | 28 |  |  | 70MAV82AN001 | NO | DI | [8 empty] | SCS | D |  | K0203-005
[5 empty] | 70CRB01 | FCS0704 | 4 | 6 | 15 | ADV151-P | SI | N | %Z046115 | [8 empty] | %Z046115 | DI |  | 70CRB04 | [5 empty] | TBC01 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 4 | 6 | 16 | ADV151-P | SI | N | %Z046116 | [8 empty] | %Z046116 | DI |  | 70CRB04 | [5 empty] | TBC01 | 31 | 32
|  | 70LBR10AA201XB01 | 3#抽汽逆止阀1全开状态 | 3# extraction steam check valve 1 full opened status | 70CRB01 | FCS0704 | 4 | 6 | 17 | ADV151-P | SI | N | %Z046117 | [8 empty] | %Z046117 | DI |  | 70CRB04 | [5 empty] | TBC01 | 33 | 34 |  |  | 70LBR10AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA201XB11 | 3#抽汽逆止阀1全关状态 | 3# extraction steam check valve 1 full closed status | 70CRB01 | FCS0704 | 4 | 6 | 18 | ADV151-P | SI | N | %Z046118 | [8 empty] | %Z046118 | DI |  | 70CRB04 | [5 empty] | TBC01 | 35 | 36 |  |  | 70LBR10AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA404XB01 | 3#抽汽逆止阀2后疏水阀1全开状态 | Drain valve 1 after 3# extraction steam check valve 2 full opened status | 70CRB01 | FCS0704 | 4 | 6 | 19 | ADV151-P | SI | N | %Z046119 | [8 empty] | %Z046119 | DI |  | 70CRB04 | [5 empty] | TBC01 | 37 | 38 |  |  | 70LBR10AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA404XB11 | 3#抽汽逆止阀2后疏水阀1全关状态 | Drain valve 1 after 3# extraction steam check valve 2 full closed status | 70CRB01 | FCS0704 | 4 | 6 | 20 | ADV151-P | SI | N | %Z046120 | [8 empty] | %Z046120 | DI |  | 70CRB04 | [5 empty] | TBC01 | 39 | 40 |  |  | 70LBR10AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA406XB01 | 3#抽汽电动调节阀后疏水阀1全开状态 | Drain valve 1 after 3# extraction steam regulating MOV full opened status | 70CRB01 | FCS0704 | 4 | 6 | 21 | ADV151-P | SI | N | %Z046121 | [8 empty] | %Z046121 | DI |  | 70CRB04 | [5 empty] | TBC01 | 41 | 42 |  |  | 70LBR10AA406 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA406XB11 | 3#抽汽电动调节阀后疏水阀1全关状态 | Drain valve 1 after 3# extraction steam regulating MOV full closed status | 70CRB01 | FCS0704 | 4 | 6 | 22 | ADV151-P | SI | N | %Z046122 | [8 empty] | %Z046122 | DI |  | 70CRB04 | [5 empty] | TBC01 | 43 | 44 |  |  | 70LBR10AA406 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR20AA003XB01 | 低压联箱启动排汽电动阀全开状态 | LP steam header start exhaust MOV full opened status | 70CRB01 | FCS0704 | 4 | 6 | 23 | ADV151-P | SI | N | %Z046123 | [8 empty] | %Z046123 | DI |  | 70CRB04 | [5 empty] | TBC01 | 45 | 46 |  |  | 70LBR20AA003 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA003XB11 | 低压联箱启动排汽电动阀全关状态 | LP steam header start exhaust MOV full closed status | 70CRB01 | FCS0704 | 4 | 6 | 24 | ADV151-P | SI | N | %Z046124 | [8 empty] | %Z046124 | DI |  | 70CRB04 | [5 empty] | TBC01 | 47 | 48 |  |  | 70LBR20AA003 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA003XB31 | 低压联箱启动排汽电动阀故障 | LP steam header start exhaust MOV fault | 70CRB01 | FCS0704 | 4 | 6 | 25 | ADV151-P | SI | N | %Z046125 | [8 empty] | %Z046125 | DI |  | 70CRB04 | [5 empty] | TBC01 | 49 | 50 |  |  | 70LBR20AA003 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBA10AA404XB01 | 汽机(左)进汽管道疏水阀全开状态 | Turbine(left) main steam inlet pipe drain valve full opened status | 70CRB01 | FCS0704 | 4 | 6 | 26 | ADV151-P | SI | N | %Z046126 | [8 empty] | %Z046126 | DI |  | 70CRB04 | [5 empty] | TBC01 | 51 | 52 |  |  | 70LBA10AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA10AA404XB11 | 汽机(左)进汽管道疏水阀全关状态 | Turbine(left) main steam inlet pipe drain valve full closed status | 70CRB01 | FCS0704 | 4 | 6 | 27 | ADV151-P | SI | N | %Z046127 | [8 empty] | %Z046127 | DI |  | 70CRB04 | [5 empty] | TBC01 | 53 | 54 |  |  | 70LBA10AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-001
[5 empty] | 70CRB01 | FCS0704 | 4 | 6 | 28 | ADV151-P | SI | N | %Z046128 | [8 empty] | %Z046128 | DI |  | 70CRB04 | [5 empty] | TBC01 | 55 | 56
[5 empty] | 70CRB01 | FCS0704 | 4 | 6 | 29 | ADV151-P | SI | N | %Z046129 | [8 empty] | %Z046129 | DI |  | 70CRB04 | [5 empty] | TBC01 | 57 | 58
[5 empty] | 70CRB01 | FCS0704 | 4 | 6 | 30 | ADV151-P | SI | N | %Z046130 | [8 empty] | %Z046130 | DI |  | 70CRB04 | [5 empty] | TBC01 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 4 | 6 | 31 | ADV151-P | SI | N | %Z046131 | [8 empty] | %Z046131 | DI |  | 70CRB04 | [5 empty] | TBC01 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 4 | 6 | 32 | ADV151-P | SI | N | %Z046132 | [8 empty] | %Z046132 | DI |  | 70CRB04 | [5 empty] | TBC01 | 63 | 64
|  | 70LBR10AA202XB01 | 3#抽汽逆止阀2全开状态 | 3# extraction steam check valve 2 full opened status | 70CRB01 | FCS0704 | 4 | 7 | 1 | ADV151-P | SI | N | %Z047101 | [8 empty] | %Z047101 | DI |  | 70CRB04 | [5 empty] | TBC02 | 1 | 2 |  |  | 70LBR10AA202 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA202XB11 | 3#抽汽逆止阀2全关状态 | 3# extraction steam check valve 2 full closed status | 70CRB01 | FCS0704 | 4 | 7 | 2 | ADV151-P | SI | N | %Z047102 | [8 empty] | %Z047102 | DI |  | 70CRB04 | [5 empty] | TBC02 | 3 | 4 |  |  | 70LBR10AA202 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA410XB01 | 3#抽汽逆止阀2后疏水阀2全开状态 | Drain valve 2 after 3# extraction steam check valve 2 full opened status | 70CRB01 | FCS0704 | 4 | 7 | 3 | ADV151-P | SI | N | %Z047103 | [8 empty] | %Z047103 | DI |  | 70CRB04 | [5 empty] | TBC02 | 5 | 6 |  |  | 70LBR10AA410 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA410XB11 | 3#抽汽逆止阀2后疏水阀2全关状态 | Drain valve 2 after 3# extraction steam check valve 2 full closed status | 70CRB01 | FCS0704 | 4 | 7 | 4 | ADV151-P | SI | N | %Z047104 | [8 empty] | %Z047104 | DI |  | 70CRB04 | [5 empty] | TBC02 | 7 | 8 |  |  | 70LBR10AA410 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA001XB01 | 3#抽汽电动阀全开状态 | 3# extraction steam MOV full opened status | 70CRB01 | FCS0704 | 4 | 7 | 5 | ADV151-P | SI | N | %Z047105 | [8 empty] | %Z047105 | DI |  | 70CRB04 | [5 empty] | TBC02 | 9 | 10 |  |  | 70LBR10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA001XB11 | 3#抽汽电动阀全关状态 | 3# extraction steam MOV full closed status | 70CRB01 | FCS0704 | 4 | 7 | 6 | ADV151-P | SI | N | %Z047106 | [8 empty] | %Z047106 | DI |  | 70CRB04 | [5 empty] | TBC02 | 11 | 12 |  |  | 70LBR10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA001XB31 | 3#抽汽电动阀故障 | 3# extraction steam MOV fault | 70CRB01 | FCS0704 | 4 | 7 | 7 | ADV151-P | SI | N | %Z047107 | [8 empty] | %Z047107 | DI |  | 70CRB04 | [5 empty] | TBC02 | 13 | 14 |  |  | 70LBR10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA412XB01 | 3#抽汽电动阀后旁路疏水阀全开状态 | Bypass drain valve after 3# extraction steam MOV full opened status | 70CRB01 | FCS0704 | 4 | 7 | 8 | ADV151-P | SI | N | %Z047108 | [8 empty] | %Z047108 | DI |  | 70CRB04 | [5 empty] | TBC02 | 15 | 16 |  |  | 70LBR10AA412 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA412XB11 | 3#抽汽电动阀后旁路疏水阀全关状态 | Bypass drain valve after 3# extraction steam MOV full closed status | 70CRB01 | FCS0704 | 4 | 7 | 9 | ADV151-P | SI | N | %Z047109 | [8 empty] | %Z047109 | DI |  | 70CRB04 | [5 empty] | TBC02 | 17 | 18 |  |  | 70LBR10AA412 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA408XB01 | 3#抽汽电动调节阀后疏水阀2全开状态 | Drain valve 2 after 3# extraction steam regulating MOV full opened status | 70CRB01 | FCS0704 | 4 | 7 | 10 | ADV151-P | SI | N | %Z047110 | [8 empty] | %Z047110 | DI |  | 70CRB04 | [5 empty] | TBC02 | 19 | 20 |  |  | 70LBR10AA408 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR10AA408XB11 | 3#抽汽电动调节阀后疏水阀2全关状态 | Drain valve 2 after 3# extraction steam regulating MOV full closed status | 70CRB01 | FCS0704 | 4 | 7 | 11 | ADV151-P | SI | N | %Z047111 | [8 empty] | %Z047111 | DI |  | 70CRB04 | [5 empty] | TBC02 | 21 | 22 |  |  | 70LBR10AA408 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBQ20AA004XB01 | 中压联箱启动排汽电动阀全开状态 | MP steam header start exhaust MOV full opened status | 70CRB01 | FCS0704 | 4 | 7 | 12 | ADV151-P | SI | N | %Z047112 | [8 empty] | %Z047112 | DI |  | 70CRB04 | [5 empty] | TBC02 | 23 | 24 |  |  | 70LBQ20AA004 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA004XB11 | 中压联箱启动排汽电动阀全关状态 | MP steam header start exhaust MOV full closed status | 70CRB01 | FCS0704 | 4 | 7 | 13 | ADV151-P | SI | N | %Z047113 | [8 empty] | %Z047113 | DI |  | 70CRB04 | [5 empty] | TBC02 | 25 | 26 |  |  | 70LBQ20AA004 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA004XB31 | 中压联箱启动排汽电动阀故障 | MP steam header start exhaust MOV fault | 70CRB01 | FCS0704 | 4 | 7 | 14 | ADV151-P | SI | N | %Z047114 | [8 empty] | %Z047114 | DI |  | 70CRB04 | [5 empty] | TBC02 | 27 | 28 |  |  | 70LBQ20AA004 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBA10AA402XB01 | 汽机(右)进汽管道疏水阀全开状态 | Turbine(right) main steam inlet pipe drain valve full opened status | 70CRB01 | FCS0704 | 4 | 7 | 15 | ADV151-P | SI | N | %Z047115 | [8 empty] | %Z047115 | DI |  | 70CRB04 | [5 empty] | TBC02 | 29 | 30 |  |  | 70LBA10AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA10AA402XB11 | 汽机(右)进汽管道疏水阀全关状态 | Turbine(right) main steam inlet pipe drain valve full closed status | 70CRB01 | FCS0704 | 4 | 7 | 16 | ADV151-P | SI | N | %Z047116 | [8 empty] | %Z047116 | DI |  | 70CRB04 | [5 empty] | TBC02 | 31 | 32 |  |  | 70LBA10AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70MAW10CL001H | 轴封冷却器液位高 | Gland steam condenser level H | 70CRB01 | FCS0704 | 4 | 7 | 17 | ADV151-P | SI | N | %Z047117 | [8 empty] | %Z047117 | DI |  | 70CRB04 | [5 empty] | TBC02 | 33 | 34 |  |  | 70MAW10CL001 | NO | DI | [8 empty] | SCS | D |  | K0204-012
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 18 | ADV151-P | SI | N | %Z047118 | [8 empty] | %Z047118 | DI |  | 70CRB04 | [5 empty] | TBC02 | 35 | 36
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 19 | ADV151-P | SI | N | %Z047119 | [8 empty] | %Z047119 | DI |  | 70CRB04 | [5 empty] | TBC02 | 37 | 38
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 20 | ADV151-P | SI | N | %Z047120 | [8 empty] | %Z047120 | DI |  | 70CRB04 | [5 empty] | TBC02 | 39 | 40
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 21 | ADV151-P | SI | N | %Z047121 | [8 empty] | %Z047121 | DI |  | 70CRB04 | [5 empty] | TBC02 | 41 | 42
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 22 | ADV151-P | SI | N | %Z047122 | [8 empty] | %Z047122 | DI |  | 70CRB04 | [5 empty] | TBC02 | 43 | 44
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 23 | ADV151-P | SI | N | %Z047123 | [8 empty] | %Z047123 | DI |  | 70CRB04 | [5 empty] | TBC02 | 45 | 46
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 24 | ADV151-P | SI | N | %Z047124 | [8 empty] | %Z047124 | DI |  | 70CRB04 | [5 empty] | TBC02 | 47 | 48
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 25 | ADV151-P | SI | N | %Z047125 | [8 empty] | %Z047125 | DI |  | 70CRB04 | [5 empty] | TBC02 | 49 | 50
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 26 | ADV151-P | SI | N | %Z047126 | [8 empty] | %Z047126 | DI |  | 70CRB04 | [5 empty] | TBC02 | 51 | 52
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 27 | ADV151-P | SI | N | %Z047127 | [8 empty] | %Z047127 | DI |  | 70CRB04 | [5 empty] | TBC02 | 53 | 54
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 28 | ADV151-P | SI | N | %Z047128 | [8 empty] | %Z047128 | DI |  | 70CRB04 | [5 empty] | TBC02 | 55 | 56
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 29 | ADV151-P | SI | N | %Z047129 | [8 empty] | %Z047129 | DI |  | 70CRB04 | [5 empty] | TBC02 | 57 | 58
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 30 | ADV151-P | SI | N | %Z047130 | [8 empty] | %Z047130 | DI |  | 70CRB04 | [5 empty] | TBC02 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 31 | ADV151-P | SI | N | %Z047131 | [8 empty] | %Z047131 | DI |  | 70CRB04 | [5 empty] | TBC02 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 4 | 7 | 32 | ADV151-P | SI | N | %Z047132 | [8 empty] | %Z047132 | DI |  | 70CRB04 | [5 empty] | TBC02 | 63 | 64
|  | 70LAB50AA001XB01 | 1#高加入口给水电动阀全开状态 | 1# HP heater inlet feedwater MOV full opened status | 70CRB01 | FCS0704 | 5 | 6 | 1 | ADV151-P | SI | N | %Z056101 | [8 empty] | %Z056101 | DI |  | 70CRB04 | [5 empty] | TBF01 | 1 | 2 |  |  | 70LAB50AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB50AA001XB11 | 1#高加入口给水电动阀全关状态 | 1# HP heater inlet feedwater MOV full closed status | 70CRB01 | FCS0704 | 5 | 6 | 2 | ADV151-P | SI | N | %Z056102 | [8 empty] | %Z056102 | DI |  | 70CRB04 | [5 empty] | TBF01 | 3 | 4 |  |  | 70LAB50AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB50AA001XB31 | 1#高加入口给水电动阀故障 | 1# HP heater inlet feedwater MOV fault | 70CRB01 | FCS0704 | 5 | 6 | 3 | ADV151-P | SI | N | %Z056103 | [8 empty] | %Z056103 | DI |  | 70CRB04 | [5 empty] | TBF01 | 5 | 6 |  |  | 70LAB50AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAD10AA005XB01 | 1#高加危急疏水电动阀全开状态 | 1# HP heater emergency drain water MOV full opened status | 70CRB01 | FCS0704 | 5 | 6 | 4 | ADV151-P | SI | N | %Z056104 | [8 empty] | %Z056104 | DI |  | 70CRB04 | [5 empty] | TBF01 | 7 | 8 |  |  | 70LAD10AA005 | NO | DI | [8 empty] | SCS | D |  | K0204-011
|  | 70LAD10AA005XB11 | 1#高加危急疏水电动阀全关状态 | 1# HP heater emergency drain water MOV full closed status | 70CRB01 | FCS0704 | 5 | 6 | 5 | ADV151-P | SI | N | %Z056105 | [8 empty] | %Z056105 | DI |  | 70CRB04 | [5 empty] | TBF01 | 9 | 10 |  |  | 70LAD10AA005 | NO | DI | [8 empty] | SCS | D |  | K0204-011
|  | 70LAD10AA005XB31 | 1#高加危急疏水电动阀故障 | 1# HP heater emergency drain water MOV fault | 70CRB01 | FCS0704 | 5 | 6 | 6 | ADV151-P | SI | N | %Z056106 | [8 empty] | %Z056106 | DI |  | 70CRB04 | [5 empty] | TBF01 | 11 | 12 |  |  | 70LAD10AA005 | NO | DI | [8 empty] | SCS | D |  | K0204-011
|  | 70LAB51AA001XB01 | 高加给水旁路电动阀全开状态 | HP feedwater bypass MOV full opened status | 70CRB01 | FCS0704 | 5 | 6 | 7 | ADV151-P | SI | N | %Z056107 | [8 empty] | %Z056107 | DI |  | 70CRB04 | [5 empty] | TBF01 | 13 | 14 |  |  | 70LAB51AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB51AA001XB11 | 高加给水旁路电动阀全关状态 | HP feedwater bypass MOV full closed status | 70CRB01 | FCS0704 | 5 | 6 | 8 | ADV151-P | SI | N | %Z056108 | [8 empty] | %Z056108 | DI |  | 70CRB04 | [5 empty] | TBF01 | 15 | 16 |  |  | 70LAB51AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB51AA001XB31 | 高加给水旁路电动阀故障 | HP feedwater bypass MOV fault | 70CRB01 | FCS0704 | 5 | 6 | 9 | ADV151-P | SI | N | %Z056109 | [8 empty] | %Z056109 | DI |  | 70CRB04 | [5 empty] | TBF01 | 17 | 18 |  |  | 70LAB51AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LBS30AA201XB01 | 4#抽汽逆止阀全开状态 | 4# extraction steam check valve full opened status | 70CRB01 | FCS0704 | 5 | 6 | 10 | ADV151-P | SI | N | %Z056110 | [8 empty] | %Z056110 | DI |  | 70CRB04 | [5 empty] | TBF01 | 19 | 20 |  |  | 70LBS30AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS30AA201XB11 | 4#抽汽逆止阀全关状态 | 4# extraction steam check valve full closed status | 70CRB01 | FCS0704 | 5 | 6 | 11 | ADV151-P | SI | N | %Z056111 | [8 empty] | %Z056111 | DI |  | 70CRB04 | [5 empty] | TBF01 | 21 | 22 |  |  | 70LBS30AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS30AA402XB01 | 4#抽汽电动调节阀后疏水阀全开状态 | Drain valve after 4# extraction steam regulating MOV full opened status | 70CRB01 | FCS0704 | 5 | 6 | 12 | ADV151-P | SI | N | %Z056112 | [8 empty] | %Z056112 | DI |  | 70CRB04 | [5 empty] | TBF01 | 23 | 24 |  |  | 70LBS30AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS30AA402XB11 | 4#抽汽电动调节阀后疏水阀全关状态 | Drain valve after 4# extraction steam regulating MOV full closed status | 70CRB01 | FCS0704 | 5 | 6 | 13 | ADV151-P | SI | N | %Z056113 | [8 empty] | %Z056113 | DI |  | 70CRB04 | [5 empty] | TBF01 | 25 | 26 |  |  | 70LBS30AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS20AA201XB01 | 5#抽汽逆止阀全开状态 | 5# extraction steam check valve full opened status | 70CRB01 | FCS0704 | 5 | 6 | 14 | ADV151-P | SI | N | %Z056114 | [8 empty] | %Z056114 | DI |  | 70CRB04 | [5 empty] | TBF01 | 27 | 28 |  |  | 70LBS20AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS20AA201XB11 | 5#抽汽逆止阀全关状态 | 5# extraction steam check valve full closed status | 70CRB01 | FCS0704 | 5 | 6 | 15 | ADV151-P | SI | N | %Z056115 | [8 empty] | %Z056115 | DI |  | 70CRB04 | [5 empty] | TBF01 | 29 | 30 |  |  | 70LBS20AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS20AA402XB01 | 5#抽汽逆止阀后疏水阀全开状态 | Drain valve after 5# extraction steam check valve full opened status | 70CRB01 | FCS0704 | 5 | 6 | 16 | ADV151-P | SI | N | %Z056116 | [8 empty] | %Z056116 | DI |  | 70CRB04 | [5 empty] | TBF01 | 31 | 32 |  |  | 70LBS20AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS20AA402XB11 | 5#抽汽逆止阀后疏水阀全关状态 | Drain valve after 5# extraction steam check valve full closed status | 70CRB01 | FCS0704 | 5 | 6 | 17 | ADV151-P | SI | N | %Z056117 | [8 empty] | %Z056117 | DI |  | 70CRB04 | [5 empty] | TBF01 | 33 | 34 |  |  | 70LBS20AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBQ20AA406XB01 | #1级非调整抽汽逆止阀后疏水阀2全开状态 | Drain valve 2 after #1 non-regulated extraction steam check valve full opened status | 70CRB01 | FCS0704 | 5 | 6 | 18 | ADV151-P | SI | N | %Z056118 | [8 empty] | %Z056118 | DI |  | 70CRB04 | [5 empty] | TBF01 | 35 | 36 |  |  | 70LBQ20AA406 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA406XB11 | #1级非调整抽汽逆止阀后疏水阀2全关状态 | Drain valve 2 after #1 non-regulated extraction steam check valve full closed status | 70CRB01 | FCS0704 | 5 | 6 | 19 | ADV151-P | SI | N | %Z056119 | [8 empty] | %Z056119 | DI |  | 70CRB04 | [5 empty] | TBF01 | 37 | 38 |  |  | 70LBQ20AA406 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA002XB01 | #1级非调整抽汽电动阀全开状态 | #1 non-regulated extraction steam MOV full opened status | 70CRB01 | FCS0704 | 5 | 6 | 20 | ADV151-P | SI | N | %Z056120 | [8 empty] | %Z056120 | DI |  | 70CRB04 | [5 empty] | TBF01 | 39 | 40 |  |  | 70LBQ20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA002XB11 | #1级非调整抽汽电动阀全关状态 | #1 non-regulated extraction steam MOV full closed status | 70CRB01 | FCS0704 | 5 | 6 | 21 | ADV151-P | SI | N | %Z056121 | [8 empty] | %Z056121 | DI |  | 70CRB04 | [5 empty] | TBF01 | 41 | 42 |  |  | 70LBQ20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA002XB31 | #1级非调整抽汽电动阀故障 | #1 non-regulated extraction steam MOV fault | 70CRB01 | FCS0704 | 5 | 6 | 22 | ADV151-P | SI | N | %Z056122 | [8 empty] | %Z056122 | DI |  | 70CRB04 | [5 empty] | TBF01 | 43 | 44 |  |  | 70LBQ20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBG10AA001XB01 | 辅助蒸汽母管电动阀全开状态 | Auxiliary steam main pipe MOV full opened status | 70CRB01 | FCS0704 | 5 | 6 | 23 | ADV151-P | SI | N | %Z056123 | [8 empty] | %Z056123 | DI |  | 70CRB04 | [5 empty] | TBF01 | 45 | 46 |  |  | 70LBG10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-010
|  | 70LBG10AA001XB11 | 辅助蒸汽母管电动阀全关状态 | Auxiliary steam main pipe MOV full closed status | 70CRB01 | FCS0704 | 5 | 6 | 24 | ADV151-P | SI | N | %Z056124 | [8 empty] | %Z056124 | DI |  | 70CRB04 | [5 empty] | TBF01 | 47 | 48 |  |  | 70LBG10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-010
|  | 70LBG10AA001XB31 | 辅助蒸汽母管电动阀故障 | Auxiliary steam main pipe MOV fault | 70CRB01 | FCS0704 | 5 | 6 | 25 | ADV151-P | SI | N | %Z056125 | [8 empty] | %Z056125 | DI |  | 70CRB04 | [5 empty] | TBF01 | 49 | 50 |  |  | 70LBG10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-010
[5 empty] | 70CRB01 | FCS0704 | 5 | 6 | 26 | ADV151-P | SI | N | %Z056126 | [8 empty] | %Z056126 | DI |  | 70CRB04 | [5 empty] | TBF01 | 51 | 52
[5 empty] | 70CRB01 | FCS0704 | 5 | 6 | 27 | ADV151-P | SI | N | %Z056127 | [8 empty] | %Z056127 | DI |  | 70CRB04 | [5 empty] | TBF01 | 53 | 54
[5 empty] | 70CRB01 | FCS0704 | 5 | 6 | 28 | ADV151-P | SI | N | %Z056128 | [8 empty] | %Z056128 | DI |  | 70CRB04 | [5 empty] | TBF01 | 55 | 56
[5 empty] | 70CRB01 | FCS0704 | 5 | 6 | 29 | ADV151-P | SI | N | %Z056129 | [8 empty] | %Z056129 | DI |  | 70CRB04 | [5 empty] | TBF01 | 57 | 58
[5 empty] | 70CRB01 | FCS0704 | 5 | 6 | 30 | ADV151-P | SI | N | %Z056130 | [8 empty] | %Z056130 | DI |  | 70CRB04 | [5 empty] | TBF01 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 5 | 6 | 31 | ADV151-P | SI | N | %Z056131 | [8 empty] | %Z056131 | DI |  | 70CRB04 | [5 empty] | TBF01 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 5 | 6 | 32 | ADV151-P | SI | N | %Z056132 | [8 empty] | %Z056132 | DI |  | 70CRB04 | [5 empty] | TBF01 | 63 | 64
|  | 70LCC30CL001H | 4#低加水位高 | 4# LP heater level H | 70CRB01 | FCS0704 | 5 | 7 | 1 | ADV151-P | SI | N | %Z057101 | [8 empty] | %Z057101 | DI |  | 70CRB04 | [5 empty] | TBF02 | 1 | 2 |  |  | 70LCC30CL001 | NO | DI | [8 empty] | SCS | D |  | K0204-012
|  | 70LCC30CL002HH | 4#低加水位高高 | 4# LP heater level HH | 70CRB01 | FCS0704 | 5 | 7 | 2 | ADV151-P | SI | N | %Z057102 | [8 empty] | %Z057102 | DI |  | 70CRB04 | [5 empty] | TBF02 | 3 | 4 |  |  | 70LCC30CL002 | NO | DI | [8 empty] | SCS | D |  | K0204-012
|  | 70LCC10CL001H | 6#低加水位高 | 6# LP heater level H | 70CRB01 | FCS0704 | 5 | 7 | 3 | ADV151-P | SI | N | %Z057103 | [8 empty] | %Z057103 | DI |  | 70CRB04 | [5 empty] | TBF02 | 5 | 6 |  |  | 70LCC10CL001 | NO | DI | [8 empty] | SCS | D |  | K0204-012
|  | 70LCC10CL002HH | 6#低加水位高高 | 6# LP heater level HH | 70CRB01 | FCS0704 | 5 | 7 | 4 | ADV151-P | SI | N | %Z057104 | [8 empty] | %Z057104 | DI |  | 70CRB04 | [5 empty] | TBF02 | 7 | 8 |  |  | 70LCC10CL002 | NO | DI | [8 empty] | SCS | D |  | K0204-012
|  | 70LBS30AA001XB01 | 4#抽汽电动阀全开状态 | 4# extraction steam MOV full opened status | 70CRB01 | FCS0704 | 5 | 7 | 5 | ADV151-P | SI | N | %Z057105 | [8 empty] | %Z057105 | DI |  | 70CRB04 | [5 empty] | TBF02 | 9 | 10 |  |  | 70LBS30AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS30AA001XB11 | 4#抽汽电动阀全关状态 | 4# extraction steam MOV full closed status | 70CRB01 | FCS0704 | 5 | 7 | 6 | ADV151-P | SI | N | %Z057106 | [8 empty] | %Z057106 | DI |  | 70CRB04 | [5 empty] | TBF02 | 11 | 12 |  |  | 70LBS30AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS30AA001XB31 | 4#抽汽电动阀故障 | 4# extraction steam MOV fault | 70CRB01 | FCS0704 | 5 | 7 | 7 | ADV151-P | SI | N | %Z057107 | [8 empty] | %Z057107 | DI |  | 70CRB04 | [5 empty] | TBF02 | 13 | 14 |  |  | 70LBS30AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70MAL47AA051XB01 | 4#抽汽逆止阀前疏水阀全开状态 | Drain valve before 4# extraction steam check valve full opened status | 70CRB01 | FCS0704 | 5 | 7 | 8 | ADV151-P | SI | N | %Z057108 | [8 empty] | %Z057108 | DI |  | 70CRB04 | [5 empty] | TBF02 | 15 | 16 |  |  | 70MAL47AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL47AA051XB11 | 4#抽汽逆止阀前疏水阀全关状态 | Drain valve before 4# extraction steam check valve full closed status | 70CRB01 | FCS0704 | 5 | 7 | 9 | ADV151-P | SI | N | %Z057109 | [8 empty] | %Z057109 | DI |  | 70CRB04 | [5 empty] | TBF02 | 17 | 18 |  |  | 70MAL47AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70LBS20AA001XB01 | 5#抽汽电动阀全开状态 | 5# extraction steam MOV full opened status | 70CRB01 | FCS0704 | 5 | 7 | 10 | ADV151-P | SI | N | %Z057110 | [8 empty] | %Z057110 | DI |  | 70CRB04 | [5 empty] | TBF02 | 19 | 20 |  |  | 70LBS20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS20AA001XB11 | 5#抽汽电动阀全关状态 | 5# extraction steam MOV full closed status | 70CRB01 | FCS0704 | 5 | 7 | 11 | ADV151-P | SI | N | %Z057111 | [8 empty] | %Z057111 | DI |  | 70CRB04 | [5 empty] | TBF02 | 21 | 22 |  |  | 70LBS20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS20AA001XB31 | 5#抽汽电动阀故障 | 5# extraction steam MOV fault | 70CRB01 | FCS0704 | 5 | 7 | 12 | ADV151-P | SI | N | %Z057112 | [8 empty] | %Z057112 | DI |  | 70CRB04 | [5 empty] | TBF02 | 23 | 24 |  |  | 70LBS20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70MAL49AA051XB01 | 5#抽汽逆止阀前疏水阀全开状态 | Drain valve before 5# extraction steam check valve full opened status | 70CRB01 | FCS0704 | 5 | 7 | 13 | ADV151-P | SI | N | %Z057113 | [8 empty] | %Z057113 | DI |  | 70CRB04 | [5 empty] | TBF02 | 25 | 26 |  |  | 70MAL49AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL49AA051XB11 | 5#抽汽逆止阀前疏水阀全关状态 | Drain valve before 5# extraction steam check valve full closed status | 70CRB01 | FCS0704 | 5 | 7 | 14 | ADV151-P | SI | N | %Z057114 | [8 empty] | %Z057114 | DI |  | 70CRB04 | [5 empty] | TBF02 | 27 | 28 |  |  | 70MAL49AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70LBQ20AA203XB01 | #1级非调整抽汽逆止阀全开状态 | #1 non-regulated extraction steam check valve full opened status | 70CRB01 | FCS0704 | 5 | 7 | 15 | ADV151-P | SI | N | %Z057115 | [8 empty] | %Z057115 | DI |  | 70CRB04 | [5 empty] | TBF02 | 29 | 30 |  |  | 70LBQ20AA203 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA203XB11 | #1级非调整抽汽逆止阀全关状态 | #1 non-regulated extraction steam check valve full closed status | 70CRB01 | FCS0704 | 5 | 7 | 16 | ADV151-P | SI | N | %Z057116 | [8 empty] | %Z057116 | DI |  | 70CRB04 | [5 empty] | TBF02 | 31 | 32 |  |  | 70LBQ20AA203 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA404XB01 | #1级非调整抽汽逆止阀后疏水阀1全开状态 | Drain valve 1 after #1 non-regulated extraction steam check valve full opened status | 70CRB01 | FCS0704 | 5 | 7 | 17 | ADV151-P | SI | N | %Z057117 | [8 empty] | %Z057117 | DI |  | 70CRB04 | [5 empty] | TBF02 | 33 | 34 |  |  | 70LBQ20AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA404XB11 | #1级非调整抽汽逆止阀后疏水阀1全关状态 | Drain valve 1 after #1 non-regulated extraction steam check valve full closed status | 70CRB01 | FCS0704 | 5 | 7 | 18 | ADV151-P | SI | N | %Z057118 | [8 empty] | %Z057118 | DI |  | 70CRB04 | [5 empty] | TBF02 | 35 | 36 |  |  | 70LBQ20AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA418XB01 | #1级非调整抽汽减温减压(C)后疏水阀全开状态 | Drain valve after #1 non-regulated extraction steam temperature and pressure reduction(C) full opened status | 70CRB01 | FCS0704 | 5 | 7 | 19 | ADV151-P | SI | N | %Z057119 | [8 empty] | %Z057119 | DI |  | 70CRB04 | [5 empty] | TBF02 | 37 | 38 |  |  | 70LBQ20AA418 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LBQ20AA418XB11 | #1级非调整抽汽减温减压(C)后疏水阀全关状态 | Drain valve after #1 non-regulated extraction steam temperature and pressure reduction(C) full closed status | 70CRB01 | FCS0704 | 5 | 7 | 20 | ADV151-P | SI | N | %Z057120 | [8 empty] | %Z057120 | DI |  | 70CRB04 | [5 empty] | TBF02 | 39 | 40 |  |  | 70LBQ20AA418 | NO | DI | [8 empty] | SCS | D |  | K0204-005
|  | 70LAB80AA001XB01 | 7#机组至8#机组给水电动阀全开状态 | 7# unit to 8# unit feedwater MOV full opened status | 70CRB01 | FCS0704 | 5 | 7 | 21 | ADV151-P | SI | N | %Z057121 | [8 empty] | %Z057121 | DI |  | 70CRB04 | [5 empty] | TBF02 | 41 | 42 |  |  | 70LAB80AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB80AA001XB11 | 7#机组至8#机组给水电动阀全关状态 | 7# unit to 8# unit feedwater MOV full closed status | 70CRB01 | FCS0704 | 5 | 7 | 22 | ADV151-P | SI | N | %Z057122 | [8 empty] | %Z057122 | DI |  | 70CRB04 | [5 empty] | TBF02 | 43 | 44 |  |  | 70LAB80AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB80AA001XB31 | 7#机组至8#机组给水电动阀故障 | 7# unit to 8# unit feedwater MOV fault | 70CRB01 | FCS0704 | 5 | 7 | 23 | ADV151-P | SI | N | %Z057123 | [8 empty] | %Z057123 | DI |  | 70CRB04 | [5 empty] | TBF02 | 45 | 46 |  |  | 70LAB80AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LBG10AA402XB01 | 辅助蒸汽母管疏水阀全开状态 | Auxiliary steam main pipe drain valve full opened status | 70CRB01 | FCS0704 | 5 | 7 | 24 | ADV151-P | SI | N | %Z057124 | [8 empty] | %Z057124 | DI |  | 70CRB04 | [5 empty] | TBF02 | 47 | 48 |  |  | 70LBG10AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-010
|  | 70LBG10AA402XB11 | 辅助蒸汽母管疏水阀全关状态 | Auxiliary steam main pipe drain valve full closed status | 70CRB01 | FCS0704 | 5 | 7 | 25 | ADV151-P | SI | N | %Z057125 | [8 empty] | %Z057125 | DI |  | 70CRB04 | [5 empty] | TBF02 | 49 | 50 |  |  | 70LBG10AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-010
[5 empty] | 70CRB01 | FCS0704 | 5 | 7 | 26 | ADV151-P | SI | N | %Z057126 | [8 empty] | %Z057126 | DI |  | 70CRB04 | [5 empty] | TBF02 | 51 | 52
[5 empty] | 70CRB01 | FCS0704 | 5 | 7 | 27 | ADV151-P | SI | N | %Z057127 | [8 empty] | %Z057127 | DI |  | 70CRB04 | [5 empty] | TBF02 | 53 | 54
[5 empty] | 70CRB01 | FCS0704 | 5 | 7 | 28 | ADV151-P | SI | N | %Z057128 | [8 empty] | %Z057128 | DI |  | 70CRB04 | [5 empty] | TBF02 | 55 | 56
[5 empty] | 70CRB01 | FCS0704 | 5 | 7 | 29 | ADV151-P | SI | N | %Z057129 | [8 empty] | %Z057129 | DI |  | 70CRB04 | [5 empty] | TBF02 | 57 | 58
[5 empty] | 70CRB01 | FCS0704 | 5 | 7 | 30 | ADV151-P | SI | N | %Z057130 | [8 empty] | %Z057130 | DI |  | 70CRB04 | [5 empty] | TBF02 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 5 | 7 | 31 | ADV151-P | SI | N | %Z057131 | [8 empty] | %Z057131 | DI |  | 70CRB04 | [5 empty] | TBF02 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 5 | 7 | 32 | ADV151-P | SI | N | %Z057132 | [8 empty] | %Z057132 | DI |  | 70CRB04 | [5 empty] | TBF02 | 63 | 64
|  | 70LBR20AA201XB01 | #2级调整抽汽逆止阀全开状态 | #2 regulated extraction steam check valve full opened status | 70CRB01 | FCS0704 | 6 | 5 | 1 | ADV151-P | SI | N | %Z065101 | [8 empty] | %Z065101 | DI |  | 70CRB04 | [5 empty] | TBG01 | 1 | 2 |  |  | 70LBR20AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA201XB11 | #2级调整抽汽逆止阀全关状态 | #2 regulated extraction steam check valve full closed status | 70CRB01 | FCS0704 | 6 | 5 | 2 | ADV151-P | SI | N | %Z065102 | [8 empty] | %Z065102 | DI |  | 70CRB04 | [5 empty] | TBG01 | 3 | 4 |  |  | 70LBR20AA201 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA001XB01 | #2级调整抽汽电动阀全开状态 | #2 regulated extraction steam MOV full opened status | 70CRB01 | FCS0704 | 6 | 5 | 3 | ADV151-P | SI | N | %Z065103 | [8 empty] | %Z065103 | DI |  | 70CRB04 | [5 empty] | TBG01 | 5 | 6 |  |  | 70LBR20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA001XB11 | #2级调整抽汽电动阀全关状态 | #2 regulated extraction steam MOV full closed status | 70CRB01 | FCS0704 | 6 | 5 | 4 | ADV151-P | SI | N | %Z065104 | [8 empty] | %Z065104 | DI |  | 70CRB04 | [5 empty] | TBG01 | 7 | 8 |  |  | 70LBR20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA001XB31 | #2级调整抽汽电动阀故障 | #2 regulated extraction steam MOV fault | 70CRB01 | FCS0704 | 6 | 5 | 5 | ADV151-P | SI | N | %Z065105 | [8 empty] | %Z065105 | DI |  | 70CRB04 | [5 empty] | TBG01 | 9 | 10 |  |  | 70LBR20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70MAL45AA051XB01 | #2级调整抽汽逆止阀前和各插管母管疏水阀全开状态 | Drain valve before #2 adjusting extraction steam check valve and intubation pipe full opened status | 70CRB01 | FCS0704 | 6 | 5 | 6 | ADV151-P | SI | N | %Z065106 | [8 empty] | %Z065106 | DI |  | 70CRB04 | [5 empty] | TBG01 | 11 | 12 |  |  | 70MAL45AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL45AA051XB11 | #2级调整抽汽逆止阀前和各插管母管疏水阀全关状态 | Drain valve before #2 adjusting extraction steam check valve and intubation pipe full closed status | 70CRB01 | FCS0704 | 6 | 5 | 7 | ADV151-P | SI | N | %Z065107 | [8 empty] | %Z065107 | DI |  | 70CRB04 | [5 empty] | TBG01 | 13 | 14 |  |  | 70MAL45AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70LBA20AA402XB01 | 减温减压器A前疏水阀全开状态 | Drain valve before desuperheater A full opened status | 70CRB01 | FCS0704 | 6 | 5 | 8 | ADV151-P | SI | N | %Z065108 | [8 empty] | %Z065108 | DI |  | 70CRB04 | [5 empty] | TBG01 | 15 | 16 |  |  | 70LBA20AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA20AA402XB11 | 减温减压器A前疏水阀全关状态 | Drain valve before desuperheater A full closed status | 70CRB01 | FCS0704 | 6 | 5 | 9 | ADV151-P | SI | N | %Z065109 | [8 empty] | %Z065109 | DI |  | 70CRB04 | [5 empty] | TBG01 | 17 | 18 |  |  | 70LBA20AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA20AA001XB01 | 减温减压器A前电动阀全开状态 | Desuperheater A front MOV full opened status | 70CRB01 | FCS0704 | 6 | 5 | 10 | ADV151-P | SI | N | %Z065110 | [8 empty] | %Z065110 | DI |  | 70CRB04 | [5 empty] | TBG01 | 19 | 20 |  |  | 70LBA20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA20AA001XB11 | 减温减压器A前电动阀全关状态 | Desuperheater A front MOV full closed status | 70CRB01 | FCS0704 | 6 | 5 | 11 | ADV151-P | SI | N | %Z065111 | [8 empty] | %Z065111 | DI |  | 70CRB04 | [5 empty] | TBG01 | 21 | 22 |  |  | 70LBA20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA20AA001XB31 | 减温减压器A前电动阀故障 | Desuperheater A front MOV fault | 70CRB01 | FCS0704 | 6 | 5 | 12 | ADV151-P | SI | N | %Z065112 | [8 empty] | %Z065112 | DI |  | 70CRB04 | [5 empty] | TBG01 | 23 | 24 |  |  | 70LBA20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70MAW10AA001XB01 | 汽封母管供汽电动阀全开状态 | Gland seal main steam MOV full opened status | 70CRB01 | FCS0704 | 6 | 5 | 13 | ADV151-P | SI | N | %Z065113 | [8 empty] | %Z065113 | DI |  | 70CRB04 | [5 empty] | TBG01 | 25 | 26 |  |  | 70MAW10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AA001XB11 | 汽封母管供汽电动阀全关状态 | Gland seal main steam MOV full closed status | 70CRB01 | FCS0704 | 6 | 5 | 14 | ADV151-P | SI | N | %Z065114 | [8 empty] | %Z065114 | DI |  | 70CRB04 | [5 empty] | TBG01 | 27 | 28 |  |  | 70MAW10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AA001XB31 | 汽封母管供汽电动阀故障 | Gland seal main steam MOV fault | 70CRB01 | FCS0704 | 6 | 5 | 15 | ADV151-P | SI | N | %Z065115 | [8 empty] | %Z065115 | DI |  | 70CRB04 | [5 empty] | TBG01 | 29 | 30 |  |  | 70MAW10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AN001XB01 | 1#汽封冷却器风机运行 | 1# gland seal fan running | 70CRB01 | FCS0704 | 6 | 5 | 16 | ADV151-P | SI | N | %Z065116 | [8 empty] | %Z065116 | DI |  | 70CRB04 | [5 empty] | TBG01 | 31 | 32 |  |  | 70MAW10AN001 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AN001XB11 | 1#汽封冷却器风机停止 | 1# gland seal fan stopped | 70CRB01 | FCS0704 | 6 | 5 | 17 | ADV151-P | SI | N | %Z065117 | [8 empty] | %Z065117 | DI |  | 70CRB04 | [5 empty] | TBG01 | 33 | 34 |  |  | 70MAW10AN001 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AN001XB21 | 1#汽封冷却器风机远方控制允许 | 1# gland seal fan remote control permitted | 70CRB01 | FCS0704 | 6 | 5 | 18 | ADV151-P | SI | N | %Z065118 | [8 empty] | %Z065118 | DI |  | 70CRB04 | [5 empty] | TBG01 | 35 | 36 |  |  | 70MAW10AN001 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AN001XB31 | 1#汽封冷却器风机控制电源消失 | 1# gland seal fan control circuit broken | 70CRB01 | FCS0704 | 6 | 5 | 19 | ADV151-P | SI | N | %Z065119 | [8 empty] | %Z065119 | DI |  | 70CRB04 | [5 empty] | TBG01 | 37 | 38 |  |  | 70MAW10AN001 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AN001XB32 | 1#汽封冷却器风机故障输出 | 1# gland seal fan fault output | 70CRB01 | FCS0704 | 6 | 5 | 20 | ADV151-P | SI | N | %Z065120 | [8 empty] | %Z065120 | DI |  | 70CRB04 | [5 empty] | TBG01 | 39 | 40 |  |  | 70MAW10AN001 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAL46AA501XB01 | 蒸汽室疏水阀全开状态 | Steam chamber drain valve full opened status | 70CRB01 | FCS0704 | 6 | 5 | 21 | ADV151-P | SI | N | %Z065121 | [8 empty] | %Z065121 | DI |  | 70CRB04 | [5 empty] | TBG01 | 41 | 42 |  |  | 70MAL46AA501 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL46AA501XB11 | 蒸汽室疏水阀全关状态 | Steam chamber drain valve full closed status | 70CRB01 | FCS0704 | 6 | 5 | 22 | ADV151-P | SI | N | %Z065122 | [8 empty] | %Z065122 | DI |  | 70CRB04 | [5 empty] | TBG01 | 43 | 44 |  |  | 70MAL46AA501 | NO | DI | [8 empty] | SCS | D |  | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 6 | 5 | 23 | ADV151-P | SI | N | %Z065123 | [8 empty] | %Z065123 | DI |  | 70CRB04 | [5 empty] | TBG01 | 45 | 46
[5 empty] | 70CRB01 | FCS0704 | 6 | 5 | 24 | ADV151-P | SI | N | %Z065124 | [8 empty] | %Z065124 | DI |  | 70CRB04 | [5 empty] | TBG01 | 47 | 48
[5 empty] | 70CRB01 | FCS0704 | 6 | 5 | 25 | ADV151-P | SI | N | %Z065125 | [8 empty] | %Z065125 | DI |  | 70CRB04 | [5 empty] | TBG01 | 49 | 50
[5 empty] | 70CRB01 | FCS0704 | 6 | 5 | 26 | ADV151-P | SI | N | %Z065126 | [8 empty] | %Z065126 | DI |  | 70CRB04 | [5 empty] | TBG01 | 51 | 52
[5 empty] | 70CRB01 | FCS0704 | 6 | 5 | 27 | ADV151-P | SI | N | %Z065127 | [8 empty] | %Z065127 | DI |  | 70CRB04 | [5 empty] | TBG01 | 53 | 54
[5 empty] | 70CRB01 | FCS0704 | 6 | 5 | 28 | ADV151-P | SI | N | %Z065128 | [8 empty] | %Z065128 | DI |  | 70CRB04 | [5 empty] | TBG01 | 55 | 56
[5 empty] | 70CRB01 | FCS0704 | 6 | 5 | 29 | ADV151-P | SI | N | %Z065129 | [8 empty] | %Z065129 | DI |  | 70CRB04 | [5 empty] | TBG01 | 57 | 58
[5 empty] | 70CRB01 | FCS0704 | 6 | 5 | 30 | ADV151-P | SI | N | %Z065130 | [8 empty] | %Z065130 | DI |  | 70CRB04 | [5 empty] | TBG01 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 6 | 5 | 31 | ADV151-P | SI | N | %Z065131 | [8 empty] | %Z065131 | DI |  | 70CRB04 | [5 empty] | TBG01 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 6 | 5 | 32 | ADV151-P | SI | N | %Z065132 | [8 empty] | %Z065132 | DI |  | 70CRB04 | [5 empty] | TBG01 | 63 | 64
|  | 70LAB70AA001XB01 | 2#高加出口给水电动阀全开状态 | 2# HP heater outlet feedwater MOV full opened status | 70CRB01 | FCS0704 | 6 | 6 | 1 | ADV151-P | SI | N | %Z066101 | [8 empty] | %Z066101 | DI |  | 70CRB04 | [5 empty] | TBG02 | 1 | 2 |  |  | 70LAB70AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB70AA001XB11 | 2#高加出口给水电动阀全关状态 | 2# HP heater outlet feedwater MOV full closed status | 70CRB01 | FCS0704 | 6 | 6 | 2 | ADV151-P | SI | N | %Z066102 | [8 empty] | %Z066102 | DI |  | 70CRB04 | [5 empty] | TBG02 | 3 | 4 |  |  | 70LAB70AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB70AA001XB31 | 2#高加出口给水电动阀故障 | 2# HP heater outlet feedwater MOV fault | 70CRB01 | FCS0704 | 6 | 6 | 3 | ADV151-P | SI | N | %Z066103 | [8 empty] | %Z066103 | DI |  | 70CRB04 | [5 empty] | TBG02 | 5 | 6 |  |  | 70LAB70AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAD20AA005XB01 | 2#高加危急疏水电动阀全开状态 | 2# HP heater emergency drain water MOV full opened status | 70CRB01 | FCS0704 | 6 | 6 | 4 | ADV151-P | SI | N | %Z066104 | [8 empty] | %Z066104 | DI |  | 70CRB04 | [5 empty] | TBG02 | 7 | 8 |  |  | 70LAD20AA005 | NO | DI | [8 empty] | SCS | D |  | K0204-011
|  | 70LAD20AA005XB11 | 2#高加危急疏水电动阀全关状态 | 2# HP heater emergency drain water MOV full closed status | 70CRB01 | FCS0704 | 6 | 6 | 5 | ADV151-P | SI | N | %Z066105 | [8 empty] | %Z066105 | DI |  | 70CRB04 | [5 empty] | TBG02 | 9 | 10 |  |  | 70LAD20AA005 | NO | DI | [8 empty] | SCS | D |  | K0204-011
|  | 70LAD20AA005XB31 | 2#高加危急疏水电动阀故障 | 2# HP heater emergency drain water MOV fault | 70CRB01 | FCS0704 | 6 | 6 | 6 | ADV151-P | SI | N | %Z066106 | [8 empty] | %Z066106 | DI |  | 70CRB04 | [5 empty] | TBG02 | 11 | 12 |  |  | 70LAD20AA005 | NO | DI | [8 empty] | SCS | D |  | K0204-011
|  | 70LBS10AA404XB01 | 6#抽汽电动阀前疏水阀全开状态 | Drain valve before 6# extraction steam regulating MOV full opened status | 70CRB01 | FCS0704 | 6 | 6 | 7 | ADV151-P | SI | N | %Z066107 | [8 empty] | %Z066107 | DI |  | 70CRB04 | [5 empty] | TBG02 | 13 | 14 |  |  | 70LBS10AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS10AA404XB11 | 6#抽汽电动阀前疏水阀全关状态 | Drain valve before 6# extraction steam regulating MOV full closed status | 70CRB01 | FCS0704 | 6 | 6 | 8 | ADV151-P | SI | N | %Z066108 | [8 empty] | %Z066108 | DI |  | 70CRB04 | [5 empty] | TBG02 | 15 | 16 |  |  | 70LBS10AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS10AA402XB01 | 6#抽汽电动阀后疏水阀全开状态 | Drain valve after 6# extraction steam regulating MOV full opened status | 70CRB01 | FCS0704 | 6 | 6 | 9 | ADV151-P | SI | N | %Z066109 | [8 empty] | %Z066109 | DI |  | 70CRB04 | [5 empty] | TBG02 | 17 | 18 |  |  | 70LBS10AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS10AA402XB11 | 6#抽汽电动阀后疏水阀全关状态 | Drain valve after 6# extraction steam regulating MOV full closed status | 70CRB01 | FCS0704 | 6 | 6 | 10 | ADV151-P | SI | N | %Z066110 | [8 empty] | %Z066110 | DI |  | 70CRB04 | [5 empty] | TBG02 | 19 | 20 |  |  | 70LBS10AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBR20AA414XB01 | #2级调整抽汽逆止阀后疏水阀全开状态 | Drain valve after #2 regulated extraction steam check valve full opened status | 70CRB01 | FCS0704 | 6 | 6 | 11 | ADV151-P | SI | N | %Z066111 | [8 empty] | %Z066111 | DI |  | 70CRB04 | [5 empty] | TBG02 | 21 | 22 |  |  | 70LBR20AA414 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA414XB11 | #2级调整抽汽逆止阀后疏水阀全关状态 | Drain valve after #2 regulated extraction steam check valve full closed status | 70CRB01 | FCS0704 | 6 | 6 | 12 | ADV151-P | SI | N | %Z066112 | [8 empty] | %Z066112 | DI |  | 70CRB04 | [5 empty] | TBG02 | 23 | 24 |  |  | 70LBR20AA414 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA404XB01 | #2级调整抽汽电动阀后疏水阀全开状态 | Drain valve after #2 regulated extraction steam MOV full opened status | 70CRB01 | FCS0704 | 6 | 6 | 13 | ADV151-P | SI | N | %Z066113 | [8 empty] | %Z066113 | DI |  | 70CRB04 | [5 empty] | TBG02 | 25 | 26 |  |  | 70LBR20AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70LBR20AA404XB11 | #2级调整抽汽电动阀后疏水阀全关状态 | Drain valve after #2 regulated extraction steam MOV full closed status | 70CRB01 | FCS0704 | 6 | 6 | 14 | ADV151-P | SI | N | %Z066114 | [8 empty] | %Z066114 | DI |  | 70CRB04 | [5 empty] | TBG02 | 27 | 28 |  |  | 70LBR20AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-002
|  | 70MAL19AA051XB01 | 调节级前疏水阀(左)全开状态 | Drain valve before djusting stage(left) full opened status | 70CRB01 | FCS0704 | 6 | 6 | 15 | ADV151-P | SI | N | %Z066115 | [8 empty] | %Z066115 | DI |  | 70CRB04 | [5 empty] | TBG02 | 29 | 30 |  |  | 70MAL19AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL19AA051XB11 | 调节级前疏水阀(左)全关状态 | Drain valve before djusting stage(left) full closed status | 70CRB01 | FCS0704 | 6 | 6 | 16 | ADV151-P | SI | N | %Z066116 | [8 empty] | %Z066116 | DI |  | 70CRB04 | [5 empty] | TBG02 | 31 | 32 |  |  | 70MAL19AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL22AA051XB01 | 调节级后疏水阀全开状态 | Drain valve after djusting stage full opened status | 70CRB01 | FCS0704 | 6 | 6 | 17 | ADV151-P | SI | N | %Z066117 | [8 empty] | %Z066117 | DI |  | 70CRB04 | [5 empty] | TBG02 | 33 | 34 |  |  | 70MAL22AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL22AA051XB11 | 调节级后疏水阀全关状态 | Drain valve after djusting stage full closed status | 70CRB01 | FCS0704 | 6 | 6 | 18 | ADV151-P | SI | N | %Z066118 | [8 empty] | %Z066118 | DI |  | 70CRB04 | [5 empty] | TBG02 | 35 | 36 |  |  | 70MAL22AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 19 | ADV151-P | SI | N | %Z066119 | [8 empty] | %Z066119 | DI |  | 70CRB04 | [5 empty] | TBG02 | 37 | 38
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 20 | ADV151-P | SI | N | %Z066120 | [8 empty] | %Z066120 | DI |  | 70CRB04 | [5 empty] | TBG02 | 39 | 40
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 21 | ADV151-P | SI | N | %Z066121 | [8 empty] | %Z066121 | DI |  | 70CRB04 | [5 empty] | TBG02 | 41 | 42
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 22 | ADV151-P | SI | N | %Z066122 | [8 empty] | %Z066122 | DI |  | 70CRB04 | [5 empty] | TBG02 | 43 | 44
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 23 | ADV151-P | SI | N | %Z066123 | [8 empty] | %Z066123 | DI |  | 70CRB04 | [5 empty] | TBG02 | 45 | 46
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 24 | ADV151-P | SI | N | %Z066124 | [8 empty] | %Z066124 | DI |  | 70CRB04 | [5 empty] | TBG02 | 47 | 48
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 25 | ADV151-P | SI | N | %Z066125 | [8 empty] | %Z066125 | DI |  | 70CRB04 | [5 empty] | TBG02 | 49 | 50
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 26 | ADV151-P | SI | N | %Z066126 | [8 empty] | %Z066126 | DI |  | 70CRB04 | [5 empty] | TBG02 | 51 | 52
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 27 | ADV151-P | SI | N | %Z066127 | [8 empty] | %Z066127 | DI |  | 70CRB04 | [5 empty] | TBG02 | 53 | 54
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 28 | ADV151-P | SI | N | %Z066128 | [8 empty] | %Z066128 | DI |  | 70CRB04 | [5 empty] | TBG02 | 55 | 56
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 29 | ADV151-P | SI | N | %Z066129 | [8 empty] | %Z066129 | DI |  | 70CRB04 | [5 empty] | TBG02 | 57 | 58
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 30 | ADV151-P | SI | N | %Z066130 | [8 empty] | %Z066130 | DI |  | 70CRB04 | [5 empty] | TBG02 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 31 | ADV151-P | SI | N | %Z066131 | [8 empty] | %Z066131 | DI |  | 70CRB04 | [5 empty] | TBG02 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 6 | 6 | 32 | ADV151-P | SI | N | %Z066132 | [8 empty] | %Z066132 | DI |  | 70CRB04 | [5 empty] | TBG02 | 63 | 64
|  | 70LCC20CL001H | 5#低加水位高 | 5# LP heater level H | 70CRB01 | FCS0704 | 6 | 7 | 1 | ADV151-P | SI | N | %Z067101 | [8 empty] | %Z067101 | DI |  | 70CRB04 | [5 empty] | TBG03 | 1 | 2 |  |  | 70LCC20CL001 | NO | DI | [8 empty] | SCS | D |  | K0204-012
|  | 70LCC20CL002HH | 5#低加水位高高 | 5# LP heater level HH | 70CRB01 | FCS0704 | 6 | 7 | 2 | ADV151-P | SI | N | %Z067102 | [8 empty] | %Z067102 | DI |  | 70CRB04 | [5 empty] | TBG03 | 3 | 4 |  |  | 70LCC20CL002 | NO | DI | [8 empty] | SCS | D |  | K0204-012
|  | 70LBS10AA001XB01 | 6#抽汽电动阀全开状态 | 6# extraction steam MOV full opened status | 70CRB01 | FCS0704 | 6 | 7 | 3 | ADV151-P | SI | N | %Z067103 | [8 empty] | %Z067103 | DI |  | 70CRB04 | [5 empty] | TBG03 | 5 | 6 |  |  | 70LBS10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS10AA001XB11 | 6#抽汽电动阀全关状态 | 6# extraction steam MOV full closed status | 70CRB01 | FCS0704 | 6 | 7 | 4 | ADV151-P | SI | N | %Z067104 | [8 empty] | %Z067104 | DI |  | 70CRB04 | [5 empty] | TBG03 | 7 | 8 |  |  | 70LBS10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBS10AA001XB31 | 6#抽汽电动阀故障 | 6# extraction steam MOV fault | 70CRB01 | FCS0704 | 6 | 7 | 5 | ADV151-P | SI | N | %Z067105 | [8 empty] | %Z067105 | DI |  | 70CRB04 | [5 empty] | TBG03 | 9 | 10 |  |  | 70LBS10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-004
|  | 70LBA20AA404XB01 | 减温减压器B前疏水阀全开状态 | Drain valve before desuperheater B full opened status | 70CRB01 | FCS0704 | 6 | 7 | 6 | ADV151-P | SI | N | %Z067106 | [8 empty] | %Z067106 | DI |  | 70CRB04 | [5 empty] | TBG03 | 11 | 12 |  |  | 70LBA20AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA20AA404XB11 | 减温减压器B前疏水阀全关状态 | Drain valve before desuperheater B full closed status | 70CRB01 | FCS0704 | 6 | 7 | 7 | ADV151-P | SI | N | %Z067107 | [8 empty] | %Z067107 | DI |  | 70CRB04 | [5 empty] | TBG03 | 13 | 14 |  |  | 70LBA20AA404 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA20AA002XB01 | 减温减压器B前电动阀全开状态 | Desuperheater B front MOV full opened status | 70CRB01 | FCS0704 | 6 | 7 | 8 | ADV151-P | SI | N | %Z067108 | [8 empty] | %Z067108 | DI |  | 70CRB04 | [5 empty] | TBG03 | 15 | 16 |  |  | 70LBA20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA20AA002XB11 | 减温减压器B前电动阀全关状态 | Desuperheater B front MOV full closed status | 70CRB01 | FCS0704 | 6 | 7 | 9 | ADV151-P | SI | N | %Z067109 | [8 empty] | %Z067109 | DI |  | 70CRB04 | [5 empty] | TBG03 | 17 | 18 |  |  | 70LBA20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70LBA20AA002XB31 | 减温减压器B前电动阀故障 | Desuperheater B front MOV fault | 70CRB01 | FCS0704 | 6 | 7 | 10 | ADV151-P | SI | N | %Z067110 | [8 empty] | %Z067110 | DI |  | 70CRB04 | [5 empty] | TBG03 | 19 | 20 |  |  | 70LBA20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-001
|  | 70MAW10AN002XB01 | 2#汽封冷却器风机运行 | 2# gland seal fan running | 70CRB01 | FCS0704 | 6 | 7 | 11 | ADV151-P | SI | N | %Z067111 | [8 empty] | %Z067111 | DI |  | 70CRB04 | [5 empty] | TBG03 | 21 | 22 |  |  | 70MAW10AN002 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AN002XB11 | 2#汽封冷却器风机停止 | 2# gland seal fan stopped | 70CRB01 | FCS0704 | 6 | 7 | 12 | ADV151-P | SI | N | %Z067112 | [8 empty] | %Z067112 | DI |  | 70CRB04 | [5 empty] | TBG03 | 23 | 24 |  |  | 70MAW10AN002 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AN002XB21 | 2#汽封冷却器风机远方控制允许 | 2# gland seal fan remote control permitted | 70CRB01 | FCS0704 | 6 | 7 | 13 | ADV151-P | SI | N | %Z067113 | [8 empty] | %Z067113 | DI |  | 70CRB04 | [5 empty] | TBG03 | 25 | 26 |  |  | 70MAW10AN002 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AN002XB31 | 2#汽封冷却器风机控制电源消失 | 2# gland seal fan control circuit broken | 70CRB01 | FCS0704 | 6 | 7 | 14 | ADV151-P | SI | N | %Z067114 | [8 empty] | %Z067114 | DI |  | 70CRB04 | [5 empty] | TBG03 | 27 | 28 |  |  | 70MAW10AN002 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW10AN002XB32 | 2#汽封冷却器风机故障输出 | 2# gland seal fan fault output | 70CRB01 | FCS0704 | 6 | 7 | 15 | ADV151-P | SI | N | %Z067115 | [8 empty] | %Z067115 | DI |  | 70CRB04 | [5 empty] | TBG03 | 29 | 30 |  |  | 70MAW10AN002 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW40AA001XB01 | 汽封母管疏水阀全开状态 | Gland seal main drain valve full opened status | 70CRB01 | FCS0704 | 6 | 7 | 16 | ADV151-P | SI | N | %Z067116 | [8 empty] | %Z067116 | DI |  | 70CRB04 | [5 empty] | TBG03 | 31 | 32 |  |  | 70MAW40AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAW40AA001XB11 | 汽封母管疏水阀全关状态 | Gland seal main drain valve full closed status | 70CRB01 | FCS0704 | 6 | 7 | 17 | ADV151-P | SI | N | %Z067117 | [8 empty] | %Z067117 | DI |  | 70CRB04 | [5 empty] | TBG03 | 33 | 34 |  |  | 70MAW40AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-016
|  | 70MAL21AA051XB01 | 调节级前疏水阀(右)全开状态 | Drain valve before djusting stage(right) full opened status | 70CRB01 | FCS0704 | 6 | 7 | 18 | ADV151-P | SI | N | %Z067118 | [8 empty] | %Z067118 | DI |  | 70CRB04 | [5 empty] | TBG03 | 35 | 36 |  |  | 70MAL21AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL21AA051XB11 | 调节级前疏水阀(右)全关状态 | Drain valve before djusting stage(right) full closed status | 70CRB01 | FCS0704 | 6 | 7 | 19 | ADV151-P | SI | N | %Z067119 | [8 empty] | %Z067119 | DI |  | 70CRB04 | [5 empty] | TBG03 | 37 | 38 |  |  | 70MAL21AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL14AA051XB01 | 主调门阀前疏水阀全开状态 | Drain valve before GV full opened status | 70CRB01 | FCS0704 | 6 | 7 | 20 | ADV151-P | SI | N | %Z067120 | [8 empty] | %Z067120 | DI |  | 70CRB04 | [5 empty] | TBG03 | 39 | 40 |  |  | 70MAL14AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
|  | 70MAL14AA051XB11 | 主调门阀前疏水阀全关状态 | Drain valve before GV full closed status | 70CRB01 | FCS0704 | 6 | 7 | 21 | ADV151-P | SI | N | %Z067121 | [8 empty] | %Z067121 | DI |  | 70CRB04 | [5 empty] | TBG03 | 41 | 42 |  |  | 70MAL14AA051 | NO | DI | [8 empty] | SCS | D |  | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 22 | ADV151-P | SI | N | %Z067122 | [8 empty] | %Z067122 | DI |  | 70CRB04 | [5 empty] | TBG03 | 43 | 44
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 23 | ADV151-P | SI | N | %Z067123 | [8 empty] | %Z067123 | DI |  | 70CRB04 | [5 empty] | TBG03 | 45 | 46
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 24 | ADV151-P | SI | N | %Z067124 | [8 empty] | %Z067124 | DI |  | 70CRB04 | [5 empty] | TBG03 | 47 | 48
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 25 | ADV151-P | SI | N | %Z067125 | [8 empty] | %Z067125 | DI |  | 70CRB04 | [5 empty] | TBG03 | 49 | 50
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 26 | ADV151-P | SI | N | %Z067126 | [8 empty] | %Z067126 | DI |  | 70CRB04 | [5 empty] | TBG03 | 51 | 52
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 27 | ADV151-P | SI | N | %Z067127 | [8 empty] | %Z067127 | DI |  | 70CRB04 | [5 empty] | TBG03 | 53 | 54
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 28 | ADV151-P | SI | N | %Z067128 | [8 empty] | %Z067128 | DI |  | 70CRB04 | [5 empty] | TBG03 | 55 | 56
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 29 | ADV151-P | SI | N | %Z067129 | [8 empty] | %Z067129 | DI |  | 70CRB04 | [5 empty] | TBG03 | 57 | 58
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 30 | ADV151-P | SI | N | %Z067130 | [8 empty] | %Z067130 | DI |  | 70CRB04 | [5 empty] | TBG03 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 31 | ADV151-P | SI | N | %Z067131 | [8 empty] | %Z067131 | DI |  | 70CRB04 | [5 empty] | TBG03 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 6 | 7 | 32 | ADV151-P | SI | N | %Z067132 | [8 empty] | %Z067132 | DI |  | 70CRB04 | [5 empty] | TBG03 | 63 | 64
|  | 70MAV21AP021YB01 | 1#主油泵启动指令1 | 1# main oil pump start command 1 | 70CRB01 | FCS0704 | 2 | 8 | 1 | ADV551-P | SO | N | %Z028101 | [8 empty] | %Z028101 | DO |  | 70CRB03 | [5 empty] | TBG03 | 1 | 2 |  |  | 70MAV21AP021 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70MAV21AP021YB11 | 1#主油泵停止指令 | 1# main oil pump stop command | 70CRB01 | FCS0704 | 2 | 8 | 2 | ADV551-P | SO | N | %Z028102 | [8 empty] | %Z028102 | DO |  | 70CRB03 | [5 empty] | TBG03 | 3 | 4 |  |  | 70MAV21AP021 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | A0LBA10AA001YB01 | 主蒸汽联络管电动阀打开指令 | Main steam contact pipe MOV open command | 70CRB01 | FCS0704 | 2 | 8 | 3 | ADV551-P | SO | N | %Z028103 | [8 empty] | %Z028103 | DO |  | 70CRB03 | [5 empty] | TBG03 | 5 | 6 |  |  | A0LBA10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | A0LBA10AA001YB11 | 主蒸汽联络管电动阀关闭指令 | Main steam contact pipe MOV close command | 70CRB01 | FCS0704 | 2 | 8 | 4 | ADV551-P | SO | N | %Z028104 | [8 empty] | %Z028104 | DO |  | 70CRB03 | [5 empty] | TBG03 | 7 | 8 |  |  | A0LBA10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | A0LBA10AA402YB01 | 主蒸汽联络管疏水阀打开/关闭指令 | Main steam contact pipe drain valve open/close command | 70CRB01 | FCS0704 | 2 | 8 | 5 | ADV551-P | SO | N | %Z028105 | [8 empty] | %Z028105 | DO |  | 70CRB03 | [5 empty] | TBG03 | 9 | 10 |  |  | A0LBA10AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | 70LBA10AA002YB01 | 主蒸汽电动阀打开指令 | Main steam MOV open command | 70CRB01 | FCS0704 | 2 | 8 | 6 | ADV551-P | SO | N | %Z028106 | [8 empty] | %Z028106 | DO |  | 70CRB03 | [5 empty] | TBG03 | 11 | 12 |  |  | 70LBA10AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | 70LBA10AA002YB11 | 主蒸汽电动阀关闭指令 | Main steam MOV close command | 70CRB01 | FCS0704 | 2 | 8 | 7 | ADV551-P | SO | N | %Z028107 | [8 empty] | %Z028107 | DO |  | 70CRB03 | [5 empty] | TBG03 | 13 | 14 |  |  | 70LBA10AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | 70LBA10AA406YB01 | 主蒸汽电动阀前疏水阀打开/关闭指令 | Drain valve before main steam MOV open/close command | 70CRB01 | FCS0704 | 2 | 8 | 8 | ADV551-P | SO | N | %Z028108 | [8 empty] | %Z028108 | DO |  | 70CRB03 | [5 empty] | TBG03 | 15 | 16 |  |  | 70LBA10AA406 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | 70MAX01AP001YB01 | 1# EH油泵启动指令 | 1# EH oil pump start command | 70CRB01 | FCS0704 | 2 | 8 | 9 | ADV551-P | SO | N | %Z028109 | [8 empty] | %Z028109 | DO |  | 70CRB03 | [5 empty] | TBG03 | 17 | 18 |  |  | 70MAX01GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP001YB11 | 1# EH油泵停止指令 | 1# EH oil pump stop command | 70CRB01 | FCS0704 | 2 | 8 | 10 | ADV551-P | SO | N | %Z028110 | [8 empty] | %Z028110 | DO |  | 70CRB03 | [5 empty] | TBG03 | 19 | 20 |  |  | 70MAX01GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP011YB01 | 1# EH油循环泵启动指令 | 1# EH oil circulating pump start command | 70CRB01 | FCS0704 | 2 | 8 | 11 | ADV551-P | SO | N | %Z028111 | [8 empty] | %Z028111 | DO |  | 70CRB03 | [5 empty] | TBG03 | 21 | 22 |  |  | 70MAX01GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP011YB11 | 1# EH油循环泵停止指令 | 1# EH oil circulating pump stop command | 70CRB01 | FCS0704 | 2 | 8 | 12 | ADV551-P | SO | N | %Z028112 | [8 empty] | %Z028112 | DO |  | 70CRB03 | [5 empty] | TBG03 | 23 | 24 |  |  | 70MAX01GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AH001YB01 | EH油箱电加热器启动指令 | EH oil tank heater start command | 70CRB01 | FCS0704 | 2 | 8 | 13 | ADV551-P | SO | N | %Z028113 | [8 empty] | %Z028113 | DO |  | 70CRB03 | [5 empty] | TBG03 | 25 | 26 |  |  | 70MAX01GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AH001YB11 | EH油箱电加热器停止指令 | EH oil tank heater stop command | 70CRB01 | FCS0704 | 2 | 8 | 14 | ADV551-P | SO | N | %Z028114 | [8 empty] | %Z028114 | DO |  | 70CRB03 | [5 empty] | TBG03 | 27 | 28 |  |  | 70MAX01GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAV51AA012YB01 | 盘车装置入口电磁阀打开/关闭指令 | Turning gear inlet SV open/close command | 70CRB01 | FCS0704 | 2 | 8 | 15 | ADV551-P | SO | N | %Z028115 | [8 empty] | %Z028115 | DO |  | 70CRB03 | [5 empty] | TBG03 | 29 | 30 |  |  | 70MAV51AA012 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-007
[5 empty] | 70CRB01 | FCS0704 | 2 | 8 | 16 | ADV551-P | SO | N | %Z028116 | [8 empty] | %Z028116 | DO |  | 70CRB03 | [5 empty] | TBG03 | 31 | 32
|  | 70CJJ01XB02 | 遥控功率请求 | Remote control request | 70CRB01 | FCS0704 | 2 | 8 | 17 | ADV551-P | SO | N | %Z028117 | [8 empty] | %Z028117 | DO |  | 70CRB03 | [5 empty] | TBG03 | 33 | 34 |  |  | 70CJJ01 | NO | DO | [8 empty] | SCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
|  | 70CJJ01XB03 | 投入孤网运行模式 | Into the isolated network operation mode | 70CRB01 | FCS0704 | 2 | 8 | 18 | ADV551-P | SO | N | %Z028118 | [8 empty] | %Z028118 | DO |  | 70CRB03 | [5 empty] | TBG03 | 35 | 36 |  |  | 70CJJ01 | NO | DO | [8 empty] | SCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
|  | 70CJJ01XB05 | 快速降负荷 | Rapid load shedding | 70CRB01 | FCS0704 | 2 | 8 | 19 | ADV551-P | SO | N | %Z028119 | [8 empty] | %Z028119 | DO |  | 70CRB03 | [5 empty] | TBG03 | 37 | 38 |  |  | 70CJJ01 | NO | DO | [8 empty] | SCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
|  | 70LBQ10AA201YB01 | 1#抽汽逆止阀打开/关闭指令 | 1# extraction steam check valve open/close command | 70CRB01 | FCS0704 | 2 | 8 | 20 | ADV551-P | SO | N | %Z028120 | [8 empty] | %Z028120 | DO |  | 70CRB03 | [5 empty] | TBG03 | 39 | 40 |  |  | 70LBQ10AA201 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBQ10AA402YB01 | 1#抽汽逆止阀后疏水阀打开/关闭指令 | Drain valve after 1# extraction steam check valve open/close command | 70CRB01 | FCS0704 | 2 | 8 | 21 | ADV551-P | SO | N | %Z028121 | [8 empty] | %Z028121 | DO |  | 70CRB03 | [5 empty] | TBG03 | 41 | 42 |  |  | 70LBQ10AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBQ10AA001YB01 | 1#抽汽电动阀打开指令 | 1# extraction steam MOV open command | 70CRB01 | FCS0704 | 2 | 8 | 22 | ADV551-P | SO | N | %Z028122 | [8 empty] | %Z028122 | DO |  | 70CRB03 | [5 empty] | TBG03 | 43 | 44 |  |  | 70LBQ10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBQ10AA001YB11 | 1#抽汽电动阀关闭指令 | 1# extraction steam MOV close command | 70CRB01 | FCS0704 | 2 | 8 | 23 | ADV551-P | SO | N | %Z028123 | [8 empty] | %Z028123 | DO |  | 70CRB03 | [5 empty] | TBG03 | 45 | 46 |  |  | 70LBQ10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70MAL41AA051YB01 | 1#抽汽逆止阀前疏水阀打开/关闭指令 | Drain valve before 1# extraction steam check valve open/close command | 70CRB01 | FCS0704 | 2 | 8 | 24 | ADV551-P | SO | N | %Z028124 | [8 empty] | %Z028124 | DO |  | 70CRB03 | [5 empty] | TBG03 | 47 | 48 |  |  | 70MAL41AA051 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 2 | 8 | 25 | ADV551-P | SO | N | %Z028125 | [8 empty] | %Z028125 | DO |  | 70CRB03 | [5 empty] | TBG03 | 49 | 50
[5 empty] | 70CRB01 | FCS0704 | 2 | 8 | 26 | ADV551-P | SO | N | %Z028126 | [8 empty] | %Z028126 | DO |  | 70CRB03 | [5 empty] | TBG03 | 51 | 52
[5 empty] | 70CRB01 | FCS0704 | 2 | 8 | 27 | ADV551-P | SO | N | %Z028127 | [8 empty] | %Z028127 | DO |  | 70CRB03 | [5 empty] | TBG03 | 53 | 54
[5 empty] | 70CRB01 | FCS0704 | 2 | 8 | 28 | ADV551-P | SO | N | %Z028128 | [8 empty] | %Z028128 | DO |  | 70CRB03 | [5 empty] | TBG03 | 55 | 56
[5 empty] | 70CRB01 | FCS0704 | 2 | 8 | 29 | ADV551-P | SO | N | %Z028129 | [8 empty] | %Z028129 | DO |  | 70CRB03 | [5 empty] | TBG03 | 57 | 58
[5 empty] | 70CRB01 | FCS0704 | 2 | 8 | 30 | ADV551-P | SO | N | %Z028130 | [8 empty] | %Z028130 | DO |  | 70CRB03 | [5 empty] | TBG03 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 2 | 8 | 31 | ADV551-P | SO | N | %Z028131 | [8 empty] | %Z028131 | DO |  | 70CRB03 | [5 empty] | TBG03 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 2 | 8 | 32 | ADV551-P | SO | N | %Z028132 | [8 empty] | %Z028132 | DO |  | 70CRB03 | [5 empty] | TBG03 | 63 | 64
|  | 70MAV21AP022YB01 | 2#主油泵启动指令1 | 2# main oil pump start command 1 | 70CRB01 | FCS0704 | 3 | 8 | 1 | ADV551-P | SO | N | %Z038101 | [8 empty] | %Z038101 | DO |  | 70CRB04 | [5 empty] | TBB03 | 1 | 2 |  |  | 70MAV21AP021 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70MAV21AP022YB11 | 2#主油泵停止指令 | 2# main oil pump stop command | 70CRB01 | FCS0704 | 3 | 8 | 2 | ADV551-P | SO | N | %Z038102 | [8 empty] | %Z038102 | DO |  | 70CRB04 | [5 empty] | TBB03 | 3 | 4 |  |  | 70MAV21AP021 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70MAV32AP001YB01 | 2#顶轴油泵启动指令 | 2# jacking oil pump start command | 70CRB01 | FCS0704 | 3 | 8 | 3 | ADV551-P | SO | N | %Z038103 | [8 empty] | %Z038103 | DO |  | 70CRB04 | [5 empty] | TBB03 | 5 | 6 |  |  | 70MAV32AP001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70MAV32AP001YB11 | 2#顶轴油泵停止指令 | 2# jacking oil pump stop command | 70CRB01 | FCS0704 | 3 | 8 | 4 | ADV551-P | SO | N | %Z038104 | [8 empty] | %Z038104 | DO |  | 70CRB04 | [5 empty] | TBB03 | 7 | 8 |  |  | 70MAV32AP001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70MAV82AN002YB01 | 2#排烟风机启动指令 | 2# exhaust smoke fan start command | 70CRB01 | FCS0704 | 3 | 8 | 5 | ADV551-P | SO | N | %Z038105 | [8 empty] | %Z038105 | DO |  | 70CRB04 | [5 empty] | TBB03 | 9 | 10 |  |  | 70MAV82AN002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70MAV82AN002YB11 | 2#排烟风机停止指令 | 2# exhaust smoke fan stop command | 70CRB01 | FCS0704 | 3 | 8 | 6 | ADV551-P | SO | N | %Z038106 | [8 empty] | %Z038106 | DO |  | 70CRB04 | [5 empty] | TBB03 | 11 | 12 |  |  | 70MAV82AN002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70MAX01AP002YB01 | 2# EH油泵启动指令 | 2# EH oil pump start command | 70CRB01 | FCS0704 | 3 | 8 | 7 | ADV551-P | SO | N | %Z038107 | [8 empty] | %Z038107 | DO |  | 70CRB04 | [5 empty] | TBB03 | 13 | 14 |  |  | 70MAX01GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP002YB11 | 2# EH油泵停止指令 | 2# EH oil pump stop command | 70CRB01 | FCS0704 | 3 | 8 | 8 | ADV551-P | SO | N | %Z038108 | [8 empty] | %Z038108 | DO |  | 70CRB04 | [5 empty] | TBB03 | 15 | 16 |  |  | 70MAX01GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP012YB01 | 2# EH油循环泵启动指令 | 2# EH oil circulating pump start command | 70CRB01 | FCS0704 | 3 | 8 | 9 | ADV551-P | SO | N | %Z038109 | [8 empty] | %Z038109 | DO |  | 70CRB04 | [5 empty] | TBB03 | 17 | 18 |  |  | 70MAX01GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
|  | 70MAX01AP012YB11 | 2# EH油循环泵停止指令 | 2# EH oil circulating pump stop command | 70CRB01 | FCS0704 | 3 | 8 | 10 | ADV551-P | SO | N | %Z038110 | [8 empty] | %Z038110 | DO |  | 70CRB04 | [5 empty] | TBB03 | 19 | 20 |  |  | 70MAX01GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
[5 empty] | 70CRB01 | FCS0704 | 3 | 8 | 11 | ADV551-P | SO | N | %Z038111 | [8 empty] | %Z038111 | DO |  | 70CRB04 | [5 empty] | TBB03 | 21 | 22
[5 empty] | 70CRB01 | FCS0704 | 3 | 8 | 12 | ADV551-P | SO | N | %Z038112 | [8 empty] | %Z038112 | DO |  | 70CRB04 | [5 empty] | TBB03 | 23 | 24
[5 empty] | 70CRB01 | FCS0704 | 3 | 8 | 13 | ADV551-P | SO | N | %Z038113 | [8 empty] | %Z038113 | DO |  | 70CRB04 | [5 empty] | TBB03 | 25 | 26
[5 empty] | 70CRB01 | FCS0704 | 3 | 8 | 14 | ADV551-P | SO | N | %Z038114 | [8 empty] | %Z038114 | DO |  | 70CRB04 | [5 empty] | TBB03 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 3 | 8 | 15 | ADV551-P | SO | N | %Z038115 | [8 empty] | %Z038115 | DO |  | 70CRB04 | [5 empty] | TBB03 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 3 | 8 | 16 | ADV551-P | SO | N | %Z038116 | [8 empty] | %Z038116 | DO |  | 70CRB04 | [5 empty] | TBB03 | 31 | 32
|  | 70MAV21AA321YB01 | 交流泵切换试验电磁阀打开/关闭指令 | AC pump xwitch test solenoid valve open/close command | 70CRB01 | FCS0704 | 3 | 8 | 17 | ADV551-P | SO | N | %Z038117 | [8 empty] | %Z038117 | DO |  | 70CRB04 | [5 empty] | TBB03 | 33 | 34 |  |  | 70MAV01GC001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV42AA322YB01 | 母管油压低试验电磁阀（直流）打开/关闭指令 | Main pressure low test solenoid valve(DC) open/close command | 70CRB01 | FCS0704 | 3 | 8 | 18 | ADV551-P | SO | N | %Z038118 | [8 empty] | %Z038118 | DO |  | 70CRB04 | [5 empty] | TBB03 | 35 | 36 |  |  | 70MAV01GC001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70MAV42AA329YB01 | 母管油压低试验电磁阀（交流）打开/关闭指令 | Main pressure low test solenoid valve(AC) open/close command | 70CRB01 | FCS0704 | 3 | 8 | 19 | ADV551-P | SO | N | %Z038119 | [8 empty] | %Z038119 | DO |  | 70CRB04 | [5 empty] | TBB03 | 37 | 38 |  |  | 70MAV01GC001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005 | 润滑油接线盒R | Lube oil junction box R
|  | 70LBR20AA002YB01 | 主蒸汽低压旁路管道电动阀打开指令 | Main steam LP bypass pipe MOV open command | 70CRB01 | FCS0704 | 3 | 8 | 20 | ADV551-P | SO | N | %Z038120 | [8 empty] | %Z038120 | DO |  | 70CRB04 | [5 empty] | TBB03 | 39 | 40 |  |  | 70LBR20AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-002
|  | 70LBR20AA002YB11 | 主蒸汽低压旁路管道电动阀关闭指令 | Main steam LP bypass pipe MOV close command | 70CRB01 | FCS0704 | 3 | 8 | 21 | ADV551-P | SO | N | %Z038121 | [8 empty] | %Z038121 | DO |  | 70CRB04 | [5 empty] | TBB03 | 41 | 42 |  |  | 70LBR20AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-002
|  | 70LBR20AA402YB01 | 主蒸汽低压旁路管道电动阀后疏水阀打开/关闭指令 | Drain valve after main steam LP bypass pipe MOV open/close command | 70CRB01 | FCS0704 | 3 | 8 | 22 | ADV551-P | SO | N | %Z038122 | [8 empty] | %Z038122 | DO |  | 70CRB04 | [5 empty] | TBB03 | 43 | 44 |  |  | 70LBR20AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-002
|  | 70LBQ20AA003YB01 | 主蒸汽中压旁路管道电动阀打开指令 | Main steam MP bypass pipe MOV open command | 70CRB01 | FCS0704 | 3 | 8 | 23 | ADV551-P | SO | N | %Z038123 | [8 empty] | %Z038123 | DO |  | 70CRB04 | [5 empty] | TBB03 | 45 | 46 |  |  | 70LBQ20AA003 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA003YB11 | 主蒸汽中压旁路管道电动阀关闭指令 | Main steam MP bypass pipe MOV close command | 70CRB01 | FCS0704 | 3 | 8 | 24 | ADV551-P | SO | N | %Z038124 | [8 empty] | %Z038124 | DO |  | 70CRB04 | [5 empty] | TBB03 | 47 | 48 |  |  | 70LBQ20AA003 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBR20AA416YB01 | 主蒸汽中压旁路管道电动阀后疏水阀打开/关闭指令 | Drain valve after main steam MP bypass pipe MOV open/close command | 70CRB01 | FCS0704 | 3 | 8 | 25 | ADV551-P | SO | N | %Z038125 | [8 empty] | %Z038125 | DO |  | 70CRB04 | [5 empty] | TBB03 | 49 | 50 |  |  | 70LBR20AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA201YB01 | 2#抽汽逆止阀打开/关闭指令 | 2# extraction steam check valve open/close command | 70CRB01 | FCS0704 | 3 | 8 | 26 | ADV551-P | SO | N | %Z038126 | [8 empty] | %Z038126 | DO |  | 70CRB04 | [5 empty] | TBB03 | 51 | 52 |  |  | 70LBQ20AA201 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA402YB01 | 2#抽汽电动阀前疏水阀打开/关闭指令 | 2# extraction steam MOV front drain vlave open/close command | 70CRB01 | FCS0704 | 3 | 8 | 27 | ADV551-P | SO | N | %Z038127 | [8 empty] | %Z038127 | DO |  | 70CRB04 | [5 empty] | TBB03 | 53 | 54 |  |  | 70LBQ20AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA001YB01 | 2#抽汽电动阀打开指令 | 2# extraction steam MOV open command | 70CRB01 | FCS0704 | 3 | 8 | 28 | ADV551-P | SO | N | %Z038128 | [8 empty] | %Z038128 | DO |  | 70CRB04 | [5 empty] | TBB03 | 55 | 56 |  |  | 70LBQ20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA001YB11 | 2#抽汽电动阀关闭指令 | 2# extraction steam MOV close command | 70CRB01 | FCS0704 | 3 | 8 | 29 | ADV551-P | SO | N | %Z038129 | [8 empty] | %Z038129 | DO |  | 70CRB04 | [5 empty] | TBB03 | 57 | 58 |  |  | 70LBQ20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70MAL43AA051YB01 | 2#抽汽和#1级非调整抽汽逆止阀前疏水阀打开/关闭指令 | Drain valve before 2# extraction steam and #1 non-adjusting extraction steam check valve open/close command | 70CRB01 | FCS0704 | 3 | 8 | 30 | ADV551-P | SO | N | %Z038130 | [8 empty] | %Z038130 | DO |  | 70CRB04 | [5 empty] | TBB03 | 59 | 60 |  |  | 70MAL43AA051 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 3 | 8 | 31 | ADV551-P | SO | N | %Z038131 | [8 empty] | %Z038131 | DO |  | 70CRB04 | [5 empty] | TBB03 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 3 | 8 | 32 | ADV551-P | SO | N | %Z038132 | [8 empty] | %Z038132 | DO |  | 70CRB04 | [5 empty] | TBB03 | 63 | 64
|  | 70MAV24AP001YB01 | 直流油泵启动指令1 | DC oil pump start command 1 | 70CRB01 | FCS0704 | 4 | 8 | 1 | ADV551-P | SO | N | %Z048101 | [8 empty] | %Z048101 | DO |  | 70CRB04 | [5 empty] | TBF04 | 1 | 2 |  | 220VDC | 70MAV24AP001 | NO | DO | [8 empty] | SCS | U | 220VDC | K0203-005
|  | 70MAV24AP001YB11 | 直流油泵停止指令 | DC oil pump stop command | 70CRB01 | FCS0704 | 4 | 8 | 2 | ADV551-P | SO | N | %Z048102 | [8 empty] | %Z048102 | DO |  | 70CRB04 | [5 empty] | TBF04 | 3 | 4 |  | 220VDC | 70MAV24AP001 | NO | DO | [8 empty] | SCS | U | 220VDC | K0203-005
|  | 70MAV31AP001YB01 | 1#顶轴油泵启动指令 | 1# jacking oil pump start command | 70CRB01 | FCS0704 | 4 | 8 | 3 | ADV551-P | SO | N | %Z048103 | [8 empty] | %Z048103 | DO |  | 70CRB04 | [5 empty] | TBF04 | 5 | 6 |  |  | 70MAV31AP001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70MAV31AP001YB11 | 1#顶轴油泵停止指令 | 1# jacking oil pump stop command | 70CRB01 | FCS0704 | 4 | 8 | 4 | ADV551-P | SO | N | %Z048104 | [8 empty] | %Z048104 | DO |  | 70CRB04 | [5 empty] | TBF04 | 7 | 8 |  |  | 70MAV31AP001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70MAV82AN001YB01 | 1#排烟风机启动指令 | 1# exhaust smoke fan start command | 70CRB01 | FCS0704 | 4 | 8 | 5 | ADV551-P | SO | N | %Z048105 | [8 empty] | %Z048105 | DO |  | 70CRB04 | [5 empty] | TBF04 | 9 | 10 |  |  | 70MAV82AN001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70MAV82AN001YB11 | 1#排烟风机停止指令 | 1# exhaust smoke fan stop command | 70CRB01 | FCS0704 | 4 | 8 | 6 | ADV551-P | SO | N | %Z048106 | [8 empty] | %Z048106 | DO |  | 70CRB04 | [5 empty] | TBF04 | 11 | 12 |  |  | 70MAV82AN001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0203-005
|  | 70LBR10AA201YB01 | 3#抽汽逆止阀1打开/关闭指令 | 3# extraction steam check valve 1 open/close command | 70CRB01 | FCS0704 | 4 | 8 | 7 | ADV551-P | SO | N | %Z048107 | [8 empty] | %Z048107 | DO |  | 70CRB04 | [5 empty] | TBF04 | 13 | 14 |  |  | 70LBR10AA201 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBR10AA404YB01 | 3#抽汽逆止阀2后疏水阀1打开/关闭指令 | Drain valve 1 after 3# extraction steam check valve 2 open/close command | 70CRB01 | FCS0704 | 4 | 8 | 8 | ADV551-P | SO | N | %Z048108 | [8 empty] | %Z048108 | DO |  | 70CRB04 | [5 empty] | TBF04 | 15 | 16 |  |  | 70LBR10AA404 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBR10AA406YB01 | 3#抽汽电动调节阀后疏水阀1打开/关闭指令 | Drain valve 1 after 3# extraction steam regulating MOV open/close command | 70CRB01 | FCS0704 | 4 | 8 | 9 | ADV551-P | SO | N | %Z048109 | [8 empty] | %Z048109 | DO |  | 70CRB04 | [5 empty] | TBF04 | 17 | 18 |  |  | 70LBR10AA406 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBR20AA003YB01 | 低压联箱启动排汽电动阀打开指令 | LP steam header start exhaust MOV open command | 70CRB01 | FCS0704 | 4 | 8 | 10 | ADV551-P | SO | N | %Z048110 | [8 empty] | %Z048110 | DO |  | 70CRB04 | [5 empty] | TBF04 | 19 | 20 |  |  | 70LBR20AA003 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-002
|  | 70LBR20AA003YB11 | 低压联箱启动排汽电动阀关闭指令 | LP steam header start exhaust MOV close command | 70CRB01 | FCS0704 | 4 | 8 | 11 | ADV551-P | SO | N | %Z048111 | [8 empty] | %Z048111 | DO |  | 70CRB04 | [5 empty] | TBF04 | 21 | 22 |  |  | 70LBR20AA003 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-002
|  | 70LBA10AA404YB01 | 汽机(左)进汽管道疏水阀打开/关闭指令 | Turbine(left) main steam inlet pipe drain valve open/close command | 70CRB01 | FCS0704 | 4 | 8 | 12 | ADV551-P | SO | N | %Z048112 | [8 empty] | %Z048112 | DO |  | 70CRB04 | [5 empty] | TBF04 | 23 | 24 |  |  | 70LBA10AA404 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
[5 empty] | 70CRB01 | FCS0704 | 4 | 8 | 13 | ADV551-P | SO | N | %Z048113 | [8 empty] | %Z048113 | DO |  | 70CRB04 | [5 empty] | TBF04 | 25 | 26
[5 empty] | 70CRB01 | FCS0704 | 4 | 8 | 14 | ADV551-P | SO | N | %Z048114 | [8 empty] | %Z048114 | DO |  | 70CRB04 | [5 empty] | TBF04 | 27 | 28
[5 empty] | 70CRB01 | FCS0704 | 4 | 8 | 15 | ADV551-P | SO | N | %Z048115 | [8 empty] | %Z048115 | DO |  | 70CRB04 | [5 empty] | TBF04 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 4 | 8 | 16 | ADV551-P | SO | N | %Z048116 | [8 empty] | %Z048116 | DO |  | 70CRB04 | [5 empty] | TBF04 | 31 | 32
|  | 70LBR10AA202YB01 | 3#抽汽逆止阀2打开/关闭指令 | 3# extraction steam check valve 2 open/close command | 70CRB01 | FCS0704 | 4 | 8 | 17 | ADV551-P | SO | N | %Z048117 | [8 empty] | %Z048117 | DO |  | 70CRB04 | [5 empty] | TBF04 | 33 | 34 |  |  | 70LBR10AA202 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBR10AA410YB01 | 3#抽汽逆止阀2后疏水阀2打开/关闭指令 | Drain valve 2 after 3# extraction steam check valve 2 open/close command | 70CRB01 | FCS0704 | 4 | 8 | 18 | ADV551-P | SO | N | %Z048118 | [8 empty] | %Z048118 | DO |  | 70CRB04 | [5 empty] | TBF04 | 35 | 36 |  |  | 70LBR10AA410 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBR10AA001YB01 | 3#抽汽电动阀打开指令 | 3# extraction steam MOV open command | 70CRB01 | FCS0704 | 4 | 8 | 19 | ADV551-P | SO | N | %Z048119 | [8 empty] | %Z048119 | DO |  | 70CRB04 | [5 empty] | TBF04 | 37 | 38 |  |  | 70LBR10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBR10AA001YB11 | 3#抽汽电动阀关闭指令 | 3# extraction steam MOV close command | 70CRB01 | FCS0704 | 4 | 8 | 20 | ADV551-P | SO | N | %Z048120 | [8 empty] | %Z048120 | DO |  | 70CRB04 | [5 empty] | TBF04 | 39 | 40 |  |  | 70LBR10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBR10AA412YB01 | 3#抽汽电动阀后旁路疏水阀打开/关闭指令 | Bypass drain valve after 3# extraction steam MOV open/close command | 70CRB01 | FCS0704 | 4 | 8 | 21 | ADV551-P | SO | N | %Z048121 | [8 empty] | %Z048121 | DO |  | 70CRB04 | [5 empty] | TBF04 | 41 | 42 |  |  | 70LBR10AA412 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBR10AA408YB01 | 3#抽汽电动调节阀后疏水阀2打开/关闭指令 | Drain valve 2 after 3# extraction steam regulating MOV open/close command | 70CRB01 | FCS0704 | 4 | 8 | 22 | ADV551-P | SO | N | %Z048122 | [8 empty] | %Z048122 | DO |  | 70CRB04 | [5 empty] | TBF04 | 43 | 44 |  |  | 70LBR10AA408 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBQ20AA004YB01 | 中压联箱启动排汽电动阀打开指令 | MP steam header start exhaust MOV open command | 70CRB01 | FCS0704 | 4 | 8 | 23 | ADV551-P | SO | N | %Z048123 | [8 empty] | %Z048123 | DO |  | 70CRB04 | [5 empty] | TBF04 | 45 | 46 |  |  | 70LBQ20AA004 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA004YB11 | 中压联箱启动排汽电动阀关闭指令 | MP steam header start exhaust MOV close command | 70CRB01 | FCS0704 | 4 | 8 | 24 | ADV551-P | SO | N | %Z048124 | [8 empty] | %Z048124 | DO |  | 70CRB04 | [5 empty] | TBF04 | 47 | 48 |  |  | 70LBQ20AA004 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBA10AA402YB01 | 汽机(右)进汽管道疏水阀打开/关闭指令 | Turbine(right) main steam inlet pipe drain valve open/close command | 70CRB01 | FCS0704 | 4 | 8 | 25 | ADV551-P | SO | N | %Z048125 | [8 empty] | %Z048125 | DO |  | 70CRB04 | [5 empty] | TBF04 | 49 | 50 |  |  | 70LBA10AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | 70MAL21AA051YB01 | 调节级前疏水阀(右)打开/关闭指令 | Drain valve before djusting stage(right) open/close command | 70CRB01 | FCS0704 | 4 | 8 | 26 | ADV551-P | SO | N | %Z048126 | [8 empty] | %Z048126 | DO |  | 70CRB04 | [5 empty] | TBF04 | 51 | 52 |  |  | 70MAL21AA051 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-017
|  | 70MAL22AA051YB01 | 调节级后疏水阀打开/关闭指令 | Drain valve after djusting stage open/close command | 70CRB01 | FCS0704 | 4 | 8 | 27 | ADV551-P | SO | N | %Z048127 | [8 empty] | %Z048127 | DO |  | 70CRB04 | [5 empty] | TBF04 | 53 | 54 |  |  | 70MAL22AA051 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-017
|  | 70MAL14AA051YB01 | 主调门阀前疏水阀打开/关闭指令 | Drain valve before GV open/close command | 70CRB01 | FCS0704 | 4 | 8 | 28 | ADV551-P | SO | N | %Z048128 | [8 empty] | %Z048128 | DO |  | 70CRB04 | [5 empty] | TBF04 | 55 | 56 |  |  | 70MAL14AA051 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-017
|  | 70MAL46AA501YB01 | 蒸汽室疏水阀打开/关闭指令 | Steam chamber drain valve open/close command | 70CRB01 | FCS0704 | 4 | 8 | 29 | ADV551-P | SO | N | %Z048129 | [8 empty] | %Z048129 | DO |  | 70CRB04 | [5 empty] | TBF04 | 57 | 58 |  |  | 70MAL46AA501 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 4 | 8 | 30 | ADV551-P | SO | N | %Z048130 | [8 empty] | %Z048130 | DO |  | 70CRB04 | [5 empty] | TBF04 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 4 | 8 | 31 | ADV551-P | SO | N | %Z048131 | [8 empty] | %Z048131 | DO |  | 70CRB04 | [5 empty] | TBF04 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 4 | 8 | 32 | ADV551-P | SO | N | %Z048132 | [8 empty] | %Z048132 | DO |  | 70CRB04 | [5 empty] | TBF04 | 63 | 64
|  | 70LAB50AA001YB01 | 1#高加入口给水电动阀打开指令 | 1# HP heater inlet feedwater MOV open command | 70CRB01 | FCS0704 | 5 | 8 | 1 | ADV551-P | SO | N | %Z058101 | [8 empty] | %Z058101 | DO |  | 70CRB04 | [5 empty] | TBF03 | 1 | 2 |  |  | 70LAB50AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAB50AA001YB11 | 1#高加入口给水电动阀关闭指令 | 1# HP heater inlet feedwater MOV close command | 70CRB01 | FCS0704 | 5 | 8 | 2 | ADV551-P | SO | N | %Z058102 | [8 empty] | %Z058102 | DO |  | 70CRB04 | [5 empty] | TBF03 | 3 | 4 |  |  | 70LAB50AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAD10AA005YB01 | 1#高加危急疏水电动阀打开指令 | 1# HP heater emergency drain water MOV open command | 70CRB01 | FCS0704 | 5 | 8 | 3 | ADV551-P | SO | N | %Z058103 | [8 empty] | %Z058103 | DO |  | 70CRB04 | [5 empty] | TBF03 | 5 | 6 |  |  | 70LAD10AA005 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-011
|  | 70LAD10AA005YB11 | 1#高加危急疏水电动阀关闭指令 | 1# HP heater emergency drain water MOV close command | 70CRB01 | FCS0704 | 5 | 8 | 4 | ADV551-P | SO | N | %Z058104 | [8 empty] | %Z058104 | DO |  | 70CRB04 | [5 empty] | TBF03 | 7 | 8 |  |  | 70LAD10AA005 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-011
|  | 70LBS20AA201YB01 | 5#抽汽逆止阀打开/关闭指令 | 5# extraction steam check valve open/close command | 70CRB01 | FCS0704 | 5 | 8 | 5 | ADV551-P | SO | N | %Z058105 | [8 empty] | %Z058105 | DO |  | 70CRB04 | [5 empty] | TBF03 | 9 | 10 |  |  | 70LBS20AA201 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBS20AA402YB01 | 5#抽汽逆止阀后疏水阀打开/关闭指令 | Drain valve after 5# extraction steam check valve open/close command | 70CRB01 | FCS0704 | 5 | 8 | 6 | ADV551-P | SO | N | %Z058106 | [8 empty] | %Z058106 | DO |  | 70CRB04 | [5 empty] | TBF03 | 11 | 12 |  |  | 70LBS20AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBS20AA001YB01 | 5#抽汽电动阀打开指令 | 5# extraction steam MOV open command | 70CRB01 | FCS0704 | 5 | 8 | 7 | ADV551-P | SO | N | %Z058107 | [8 empty] | %Z058107 | DO |  | 70CRB04 | [5 empty] | TBF03 | 13 | 14 |  |  | 70LBS20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBS20AA001YB11 | 5#抽汽电动阀关闭指令 | 5# extraction steam MOV close command | 70CRB01 | FCS0704 | 5 | 8 | 8 | ADV551-P | SO | N | %Z058108 | [8 empty] | %Z058108 | DO |  | 70CRB04 | [5 empty] | TBF03 | 15 | 16 |  |  | 70LBS20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70MAL49AA051YB01 | 5#抽汽逆止阀前疏水阀打开/关闭指令 | Drain valve before 5# extraction steam check valve open/close command | 70CRB01 | FCS0704 | 5 | 8 | 9 | ADV551-P | SO | N | %Z058109 | [8 empty] | %Z058109 | DO |  | 70CRB04 | [5 empty] | TBF03 | 17 | 18 |  |  | 70MAL49AA051 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-017
|  | 70LAB80AA001YB01 | 7#机组至8#机组给水电动阀打开指令 | 7# unit to 8# unit feedwater MOV open command | 70CRB01 | FCS0704 | 5 | 8 | 10 | ADV551-P | SO | N | %Z058110 | [8 empty] | %Z058110 | DO |  | 70CRB04 | [5 empty] | TBF03 | 19 | 20 |  |  | 70LAB80AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAB80AA001YB11 | 7#机组至8#机组给水电动阀关闭指令 | 7# unit to 8# unit feedwater MOV close command | 70CRB01 | FCS0704 | 5 | 8 | 11 | ADV551-P | SO | N | %Z058111 | [8 empty] | %Z058111 | DO |  | 70CRB04 | [5 empty] | TBF03 | 21 | 22 |  |  | 70LAB80AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LBG10AA402YB01 | 辅助蒸汽母管疏水阀打开/关闭指令 | Auxiliary steam main pipe drain valve open/close command | 70CRB01 | FCS0704 | 5 | 8 | 12 | ADV551-P | SO | N | %Z058112 | [8 empty] | %Z058112 | DO |  | 70CRB04 | [5 empty] | TBF03 | 23 | 24 |  |  | 70LBG10AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-010
|  | 70LBG10AA001YB01 | 辅助蒸汽母管电动阀打开指令 | Auxiliary steam main pipe MOV open command | 70CRB01 | FCS0704 | 5 | 8 | 13 | ADV551-P | SO | N | %Z058113 | [8 empty] | %Z058113 | DO |  | 70CRB04 | [5 empty] | TBF03 | 25 | 26 |  |  | 70LBG10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-010
|  | 70LBG10AA001YB11 | 辅助蒸汽母管电动阀关闭指令 | Auxiliary steam main pipe MOV close command | 70CRB01 | FCS0704 | 5 | 8 | 14 | ADV551-P | SO | N | %Z058114 | [8 empty] | %Z058114 | DO |  | 70CRB04 | [5 empty] | TBF03 | 27 | 28 |  |  | 70LBG10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-010
[5 empty] | 70CRB01 | FCS0704 | 5 | 8 | 15 | ADV551-P | SO | N | %Z058115 | [8 empty] | %Z058115 | DO |  | 70CRB04 | [5 empty] | TBF03 | 29 | 30
[5 empty] | 70CRB01 | FCS0704 | 5 | 8 | 16 | ADV551-P | SO | N | %Z058116 | [8 empty] | %Z058116 | DO |  | 70CRB04 | [5 empty] | TBF03 | 31 | 32
|  | 70LBS30AA201YB01 | 4#抽汽逆止阀打开/关闭指令 | 4# extraction steam check valve open/close command | 70CRB01 | FCS0704 | 5 | 8 | 17 | ADV551-P | SO | N | %Z058117 | [8 empty] | %Z058117 | DO |  | 70CRB04 | [5 empty] | TBF03 | 33 | 34 |  |  | 70LBS30AA201 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBS30AA402YB01 | 4#抽汽电动调节阀后疏水阀打开/关闭指令 | Drain valve after 4# extraction steam regulating MOV open/close command | 70CRB01 | FCS0704 | 5 | 8 | 18 | ADV551-P | SO | N | %Z058118 | [8 empty] | %Z058118 | DO |  | 70CRB04 | [5 empty] | TBF03 | 35 | 36 |  |  | 70LBS30AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBS30AA001YB01 | 4#抽汽电动阀打开指令 | 4# extraction steam MOV open command | 70CRB01 | FCS0704 | 5 | 8 | 19 | ADV551-P | SO | N | %Z058119 | [8 empty] | %Z058119 | DO |  | 70CRB04 | [5 empty] | TBF03 | 37 | 38 |  |  | 70LBS30AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBS30AA001YB11 | 4#抽汽电动阀关闭指令 | 4# extraction steam MOV close command | 70CRB01 | FCS0704 | 5 | 8 | 20 | ADV551-P | SO | N | %Z058120 | [8 empty] | %Z058120 | DO |  | 70CRB04 | [5 empty] | TBF03 | 39 | 40 |  |  | 70LBS30AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70MAL47AA051YB01 | 4#抽汽逆止阀前疏水阀打开/关闭指令 | Drain valve before 4# extraction steam check valve open/close command | 70CRB01 | FCS0704 | 5 | 8 | 21 | ADV551-P | SO | N | %Z058121 | [8 empty] | %Z058121 | DO |  | 70CRB04 | [5 empty] | TBF03 | 41 | 42 |  |  | 70MAL47AA051 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-017
|  | 70LBQ20AA203YB01 | #1级非调整抽汽逆止阀打开/关闭指令 | #1 non-regulated extraction steam check valve open/close command | 70CRB01 | FCS0704 | 5 | 8 | 22 | ADV551-P | SO | N | %Z058122 | [8 empty] | %Z058122 | DO |  | 70CRB04 | [5 empty] | TBF03 | 43 | 44 |  |  | 70LBQ20AA203 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA404YB01 | #1级非调整抽汽逆止阀后疏水阀1打开/关闭指令 | Drain valve 1 after #1 non-regulated extraction steam check valve open/close command | 70CRB01 | FCS0704 | 5 | 8 | 23 | ADV551-P | SO | N | %Z058123 | [8 empty] | %Z058123 | DO |  | 70CRB04 | [5 empty] | TBF03 | 45 | 46 |  |  | 70LBQ20AA404 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA406YB01 | #1级非调整抽汽逆止阀后疏水阀2打开/关闭指令 | Drain valve 2 after #1 non-regulated extraction steam check valve open/close command | 70CRB01 | FCS0704 | 5 | 8 | 24 | ADV551-P | SO | N | %Z058124 | [8 empty] | %Z058124 | DO |  | 70CRB04 | [5 empty] | TBF03 | 47 | 48 |  |  | 70LBQ20AA406 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA418YB01 | #1级非调整抽汽减温减压(C)后疏水阀打开/关闭指令 | Drain valve after #1 non-regulated extraction steam temperature and pressure reduction(C) open/close command | 70CRB01 | FCS0704 | 5 | 8 | 25 | ADV551-P | SO | N | %Z058125 | [8 empty] | %Z058125 | DO |  | 70CRB04 | [5 empty] | TBF03 | 49 | 50 |  |  | 70LBQ20AA418 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA002YB01 | #1级非调整抽汽电动阀打开指令 | #1 non-regulated extraction steam MOV open command | 70CRB01 | FCS0704 | 5 | 8 | 26 | ADV551-P | SO | N | %Z058126 | [8 empty] | %Z058126 | DO |  | 70CRB04 | [5 empty] | TBF03 | 51 | 52 |  |  | 70LBQ20AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70LBQ20AA002YB11 | #1级非调整抽汽电动阀关闭指令 | #1 non-regulated extraction steam MOV close command | 70CRB01 | FCS0704 | 5 | 8 | 27 | ADV551-P | SO | N | %Z058127 | [8 empty] | %Z058127 | DO |  | 70CRB04 | [5 empty] | TBF03 | 53 | 54 |  |  | 70LBQ20AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-005
|  | 70MAW10AN002YB01 | 2#汽封冷却器风机启动指令 | 2# gland seal fan start command | 70CRB01 | FCS0704 | 5 | 8 | 28 | ADV551-P | SO | N | %Z058128 | [8 empty] | %Z058128 | DO |  | 70CRB04 | [5 empty] | TBF03 | 55 | 56 |  |  | 70MAW10AN002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-016
|  | 70MAW10AN002YB11 | 2#汽封冷却器风机停止指令 | 2# gland seal fan stop command | 70CRB01 | FCS0704 | 5 | 8 | 29 | ADV551-P | SO | N | %Z058129 | [8 empty] | %Z058129 | DO |  | 70CRB04 | [5 empty] | TBF03 | 57 | 58 |  |  | 70MAW10AN002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-016
[5 empty] | 70CRB01 | FCS0704 | 5 | 8 | 30 | ADV551-P | SO | N | %Z058130 | [8 empty] | %Z058130 | DO |  | 70CRB04 | [5 empty] | TBF03 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 5 | 8 | 31 | ADV551-P | SO | N | %Z058131 | [8 empty] | %Z058131 | DO |  | 70CRB04 | [5 empty] | TBF03 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 5 | 8 | 32 | ADV551-P | SO | N | %Z058132 | [8 empty] | %Z058132 | DO |  | 70CRB04 | [5 empty] | TBF03 | 63 | 64
|  | 70LAB70AA001YB01 | 2#高加出口给水电动阀打开指令 | 2# HP heater outlet feedwater MOV open command | 70CRB01 | FCS0704 | 6 | 8 | 1 | ADV551-P | SO | N | %Z068101 | [8 empty] | %Z068101 | DO |  | 70CRB04 | [5 empty] | TBG04 | 1 | 2 |  |  | 70LAB70AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAB70AA001YB11 | 2#高加出口给水电动阀关闭指令 | 2# HP heater outlet feedwater MOV close command | 70CRB01 | FCS0704 | 6 | 8 | 2 | ADV551-P | SO | N | %Z068102 | [8 empty] | %Z068102 | DO |  | 70CRB04 | [5 empty] | TBG04 | 3 | 4 |  |  | 70LAB70AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAD20AA005YB01 | 2#高加危急疏水电动阀打开指令 | 2# HP heater emergency drain water MOV open command | 70CRB01 | FCS0704 | 6 | 8 | 3 | ADV551-P | SO | N | %Z068103 | [8 empty] | %Z068103 | DO |  | 70CRB04 | [5 empty] | TBG04 | 5 | 6 |  |  | 70LAD20AA005 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-011
|  | 70LAD20AA005YB11 | 2#高加危急疏水电动阀关闭指令 | 2# HP heater emergency drain water MOV close command | 70CRB01 | FCS0704 | 6 | 8 | 4 | ADV551-P | SO | N | %Z068104 | [8 empty] | %Z068104 | DO |  | 70CRB04 | [5 empty] | TBG04 | 7 | 8 |  |  | 70LAD20AA005 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-011
|  | 70LAB51AA001YB01 | 高加给水旁路电动阀打开指令 | HP feedwater bypass MOV open command | 70CRB01 | FCS0704 | 6 | 8 | 5 | ADV551-P | SO | N | %Z068105 | [8 empty] | %Z068105 | DO |  | 70CRB04 | [5 empty] | TBG04 | 9 | 10 |  |  | 70LAB51AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAB51AA001YB11 | 高加给水旁路电动阀关闭指令 | HP feedwater bypass MOV close command | 70CRB01 | FCS0704 | 6 | 8 | 6 | ADV551-P | SO | N | %Z068106 | [8 empty] | %Z068106 | DO |  | 70CRB04 | [5 empty] | TBG04 | 11 | 12 |  |  | 70LAB51AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LBA20AA402YB01 | 减温减压器A前疏水阀打开/关闭指令 | Drain valve before desuperheater A open/close command | 70CRB01 | FCS0704 | 6 | 8 | 7 | ADV551-P | SO | N | %Z068107 | [8 empty] | %Z068107 | DO |  | 70CRB04 | [5 empty] | TBG04 | 13 | 14 |  |  | 70LBA20AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | 70LBA20AA001YB01 | 减温减压器A前电动阀打开指令 | Desuperheater A front MOV open command | 70CRB01 | FCS0704 | 6 | 8 | 8 | ADV551-P | SO | N | %Z068108 | [8 empty] | %Z068108 | DO |  | 70CRB04 | [5 empty] | TBG04 | 15 | 16 |  |  | 70LBA20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | 70LBA20AA001YB11 | 减温减压器A前电动阀关闭指令 | Desuperheater A front MOV close command | 70CRB01 | FCS0704 | 6 | 8 | 9 | ADV551-P | SO | N | %Z068109 | [8 empty] | %Z068109 | DO |  | 70CRB04 | [5 empty] | TBG04 | 17 | 18 |  |  | 70LBA20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | 70MAW10AA001YB01 | 汽封母管供汽电动阀打开指令 | Gland seal main steam MOV open command | 70CRB01 | FCS0704 | 6 | 8 | 10 | ADV551-P | SO | N | %Z068110 | [8 empty] | %Z068110 | DO |  | 70CRB04 | [5 empty] | TBG04 | 19 | 20 |  |  | 70MAW10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-016
|  | 70MAW10AA001YB11 | 汽封母管供汽电动阀关闭指令 | Gland seal main steam MOV close command | 70CRB01 | FCS0704 | 6 | 8 | 11 | ADV551-P | SO | N | %Z068111 | [8 empty] | %Z068111 | DO |  | 70CRB04 | [5 empty] | TBG04 | 21 | 22 |  |  | 70MAW10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-016
|  | 70MAW10AN001YB01 | 1#汽封冷却器风机启动指令 | 1# gland seal fan start command | 70CRB01 | FCS0704 | 6 | 8 | 12 | ADV551-P | SO | N | %Z068112 | [8 empty] | %Z068112 | DO |  | 70CRB04 | [5 empty] | TBG04 | 23 | 24 |  |  | 70MAW10AN001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-016
|  | 70MAW10AN001YB11 | 1#汽封冷却器风机停止指令 | 1# gland seal fan stop command | 70CRB01 | FCS0704 | 6 | 8 | 13 | ADV551-P | SO | N | %Z068113 | [8 empty] | %Z068113 | DO |  | 70CRB04 | [5 empty] | TBG04 | 25 | 26 |  |  | 70MAW10AN001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-016
|  | 70MAW40AA001YB01 | 汽封母管疏水阀打开/关闭指令 | Gland seal main drain valve open/close command | 70CRB01 | FCS0704 | 6 | 8 | 14 | ADV551-P | SO | N | %Z068114 | [8 empty] | %Z068114 | DO |  | 70CRB04 | [5 empty] | TBG04 | 27 | 28 |  |  | 70MAW40AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-016
|  | 70MAL19AA051YB01 | 调节级前疏水阀(左)打开/关闭指令 | Drain valve before djusting stage(left) open/close command | 70CRB01 | FCS0704 | 6 | 8 | 15 | ADV551-P | SO | N | %Z068115 | [8 empty] | %Z068115 | DO |  | 70CRB04 | [5 empty] | TBG04 | 29 | 30 |  |  | 70MAL19AA051 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-017
[5 empty] | 70CRB01 | FCS0704 | 6 | 8 | 16 | ADV551-P | SO | N | %Z068116 | [8 empty] | %Z068116 | DO |  | 70CRB04 | [5 empty] | TBG04 | 31 | 32
|  | 70LBS10AA404YB01 | 6#抽汽电动阀前疏水阀打开/关闭指令 | Drain valve before 6# extraction steam regulating MOV open/close command | 70CRB01 | FCS0704 | 6 | 8 | 17 | ADV551-P | SO | N | %Z068117 | [8 empty] | %Z068117 | DO |  | 70CRB04 | [5 empty] | TBG04 | 33 | 34 |  |  | 70LBS10AA404 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBS10AA402YB01 | 6#抽汽电动阀后疏水阀打开/关闭指令 | Drain valve after 6# extraction steam regulating MOV open/close command | 70CRB01 | FCS0704 | 6 | 8 | 18 | ADV551-P | SO | N | %Z068118 | [8 empty] | %Z068118 | DO |  | 70CRB04 | [5 empty] | TBG04 | 35 | 36 |  |  | 70LBS10AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBS10AA001YB01 | 6#抽汽电动阀打开指令 | 6# extraction steam MOV open command | 70CRB01 | FCS0704 | 6 | 8 | 19 | ADV551-P | SO | N | %Z068119 | [8 empty] | %Z068119 | DO |  | 70CRB04 | [5 empty] | TBG04 | 37 | 38 |  |  | 70LBS10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBS10AA001YB11 | 6#抽汽电动阀关闭指令 | 6# extraction steam MOV close command | 70CRB01 | FCS0704 | 6 | 8 | 20 | ADV551-P | SO | N | %Z068120 | [8 empty] | %Z068120 | DO |  | 70CRB04 | [5 empty] | TBG04 | 39 | 40 |  |  | 70LBS10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-004
|  | 70LBR20AA001YB01 | #2级调整抽汽电动阀打开指令 | #2 regulated extraction steam MOV open command | 70CRB01 | FCS0704 | 6 | 8 | 21 | ADV551-P | SO | N | %Z068121 | [8 empty] | %Z068121 | DO |  | 70CRB04 | [5 empty] | TBG04 | 41 | 42 |  |  | 70LBR20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-002
|  | 70LBR20AA001YB11 | #2级调整抽汽电动阀关闭指令 | #2 regulated extraction steam MOV close command | 70CRB01 | FCS0704 | 6 | 8 | 22 | ADV551-P | SO | N | %Z068122 | [8 empty] | %Z068122 | DO |  | 70CRB04 | [5 empty] | TBG04 | 43 | 44 |  |  | 70LBR20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-002
|  | 70LBR20AA414YB01 | #2级调整抽汽逆止阀后疏水阀打开/关闭指令 | Drain valve after #2 regulated extraction steam check valve open/close command | 70CRB01 | FCS0704 | 6 | 8 | 23 | ADV551-P | SO | N | %Z068123 | [8 empty] | %Z068123 | DO |  | 70CRB04 | [5 empty] | TBG04 | 45 | 46 |  |  | 70LBR20AA414 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-002
|  | 70LBR20AA404YB01 | #2级调整抽汽电动阀后疏水阀打开/关闭指令 | Drain valve after #2 regulated extraction steam MOV open/close command | 70CRB01 | FCS0704 | 6 | 8 | 24 | ADV551-P | SO | N | %Z068124 | [8 empty] | %Z068124 | DO |  | 70CRB04 | [5 empty] | TBG04 | 47 | 48 |  |  | 70LBR20AA404 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-002
|  | 70MAL45AA051YB01 | #2级调整抽汽逆止阀前和各插管母管疏水阀打开/关闭指令 | Drain valve before #2 adjusting extraction steam check valve and intubation pipe open/close command | 70CRB01 | FCS0704 | 6 | 8 | 25 | ADV551-P | SO | N | %Z068125 | [8 empty] | %Z068125 | DO |  | 70CRB04 | [5 empty] | TBG04 | 49 | 50 |  |  | 70MAL45AA051 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-017
|  | 70LBR20AA201YB01 | #2级调整抽汽逆止阀打开/关闭指令 | #2 regulated extraction steam check valve open/close command | 70CRB01 | FCS0704 | 6 | 8 | 26 | ADV551-P | SO | N | %Z068126 | [8 empty] | %Z068126 | DO |  | 70CRB04 | [5 empty] | TBG04 | 51 | 52 |  |  | 70LBR20AA201 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-002
|  | 70LBA20AA404YB01 | 减温减压器B前疏水阀打开/关闭指令 | Drain valve before desuperheater B open/close command | 70CRB01 | FCS0704 | 6 | 8 | 27 | ADV551-P | SO | N | %Z068127 | [8 empty] | %Z068127 | DO |  | 70CRB04 | [5 empty] | TBG04 | 53 | 54 |  |  | 70LBA20AA404 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | 70LBA20AA002YB01 | 减温减压器B前电动阀打开指令 | Desuperheater B front MOV open command | 70CRB01 | FCS0704 | 6 | 8 | 28 | ADV551-P | SO | N | %Z068128 | [8 empty] | %Z068128 | DO |  | 70CRB04 | [5 empty] | TBG04 | 55 | 56 |  |  | 70LBA20AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
|  | 70LBA20AA002YB11 | 减温减压器B前电动阀关闭指令 | Desuperheater B front MOV close command | 70CRB01 | FCS0704 | 6 | 8 | 29 | ADV551-P | SO | N | %Z068129 | [8 empty] | %Z068129 | DO |  | 70CRB04 | [5 empty] | TBG04 | 57 | 58 |  |  | 70LBA20AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-001
[5 empty] | 70CRB01 | FCS0704 | 6 | 8 | 30 | ADV551-P | SO | N | %Z068130 | [8 empty] | %Z068130 | DO |  | 70CRB04 | [5 empty] | TBG04 | 59 | 60
[5 empty] | 70CRB01 | FCS0704 | 6 | 8 | 31 | ADV551-P | SO | N | %Z068131 | [8 empty] | %Z068131 | DO |  | 70CRB04 | [5 empty] | TBG04 | 61 | 62
[5 empty] | 70CRB01 | FCS0704 | 6 | 8 | 32 | ADV551-P | SO | N | %Z068132 | [8 empty] | %Z068132 | DO |  | 70CRB04 | [5 empty] | TBG04 | 63 | 64
Note on AD1: 作者: Surge arrester(SA) model

## DCS_IO_DB_FCS0705
AREA | PID_SHT | PID_TAG | COMMENT(Chinese) | COMMENT | FCS_COMP_NAME | FCS | NODE | SLOT | TERMINAL | MODULE | SIGNAL | DUPLEX | DIOTAG | LOOP | DCS_TAG | TYPNO | DRAWNO | TGCOMM | ENG_LO | ENG_HI | ENG_UNITS | IOADDR_SYSTAG | IO_TYPE | Wire_Type | MRP_COMP_Name | BoardModel | Board_No | Board_TB_No | Board_TB_No | Board_TB_No | TBNo. | TB A or (+) | TB B or (-) | TB C | Remarks | Source | Type | I/O | HHH | HH | H | L | LL | LLL | LOG | SOE | DCS Subfunction | Power Supply | Excitation Voltage | Drawing No. | Chinese Remark | English Remark
区域 |  | 测点编号 | 测点中文名称 | 测点英文名称 | 控制柜机柜名 | 控制器编号 | 节点编号 | 插槽编号 | 通道编号 | 卡见类型 | 信号类型 | 冗余 | 通道编号 | 回路 | DCS测点编号 | 类型 | DR图号 | 注释 | 下限 | 上限 | 单位 | 系统地址 | IO类型 | 线制 | 接线柜柜号 | 端子板类型 | 端子板编号 | 端子编号 | 端子编号 | 端子编号 | 端子编号 | 端子A编号 | 端子B编号 | 端子C编号 | 备注 | 信号来源 | 信号制 | 信号类别 | 报警 | [5 empty] | 记录 |  | DCS 子功能 | 供电方 | 励磁电压 | 图号 | 中文备注 | 英文备注
|  | 70LAB50CP101 | 电动给水泵出口母管压力 | Electrical feedwater pump outlet main pipe pressure | 70CRB02 | FCS0705 | 1 | 1 | 1 | AAI143-H | 4~20mA | N | %Z011101 | [5 empty] | 0 | 24 | MPa | %Z011101 | AI |  | 70CRB02 | [5 empty] | TBF01 | 1 | 2 |  |  | 70LAB50CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-006
|  | 70LAB50CT101 | 电动给水泵出口母管温度 | Electrical feedwater pump outlet main pipe temp. | 70CRB02 | FCS0705 | 1 | 1 | 2 | AAI143-H | 4~20mA | N | %Z011102 | [5 empty] | 0 | 200 | ℃ | %Z011102 | AI |  | 70CRB02 | [5 empty] | TBF01 | 3 | 4 |  |  | 70LAB50CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-006
|  | 70LCA30CP101 | 凝结水泵出口母管压力 | Condensate pump outlet main pipe pressure | 70CRB02 | FCS0705 | 1 | 1 | 3 | AAI143-H | 4~20mA | N | %Z011103 | [5 empty] | 0 | 2.5 | MPa | %Z011103 | AI |  | 70CRB02 | [5 empty] | TBF01 | 5 | 6 |  |  | 70LCA30CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-008
|  | 70LCA30CT101 | 凝结水泵出口母管温度 | Condensate pump outlet main pipe temperature | 70CRB02 | FCS0705 | 1 | 1 | 4 | AAI143-H | 4~20mA | N | %Z011104 | [5 empty] | 0 | 200 | ℃ | %Z011104 | AI |  | 70CRB02 | [5 empty] | TBF01 | 7 | 8 |  |  | 70LCA30CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-008
|  | 70MAG10CL101 | 凝汽器热井水位 | Condenser hot well level | 70CRB02 | FCS0705 | 1 | 1 | 5 | AAI143-H | 4~20mA | N | %Z011105 | [5 empty] | 0 | 1.5 | m | %Z011105 | AI |  | 70CRB02 | [5 empty] | TBF01 | 9 | 10 |  |  | 70MAG10CL101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-008
|  | 70LCA10CT101 | 凝汽器出口水温 | Condenser outlet water temperature | 70CRB02 | FCS0705 | 1 | 1 | 6 | AAI143-H | 4~20mA | N | %Z011106 | [5 empty] | 0 | 200 | ℃ | %Z011106 | AI |  | 70CRB02 | [5 empty] | TBF01 | 11 | 12 |  |  | 70LCA10CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-008
|  | 70GHC10CP101 | 除盐水母管压力 | Demineralized water pressure | 70CRB02 | FCS0705 | 1 | 1 | 7 | AAI143-H | 4~20mA | N | %Z011107 | [5 empty] | 0 | 2.2 | MPa | %Z011107 | AI |  | 70CRB02 | [5 empty] | TBF01 | 13 | 142 |  |  | 70GHC10CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-015
|  | 70LBR10CP102 | 除氧器进汽压力 | Deaerator inlet steam pressure | 70CRB02 | FCS0705 | 1 | 1 | 8 | AAI143-H | 4~20mA | N | %Z011108 | [5 empty] | 0 | 1.6 | MPa | %Z011108 | AI |  | 70CRB02 | [5 empty] | TBF01 | 15 | 16 |  |  | 70LBR10CP102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-004
|  | 70LBR10CT109 | 除氧器进汽温度 | Deaerator inlet steam temperature | 70CRB02 | FCS0705 | 1 | 1 | 9 | AAI143-H | 4~20mA | N | %Z011109 | [5 empty] | 0 | 300 | ℃ | %Z011109 | AI |  | 70CRB02 | [5 empty] | TBF01 | 17 | 18 |  |  | 70LBR10CT109 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-004
|  | 70LAA10CT101 | 除氧器水箱温度 | Deaerator water tank temperature | 70CRB02 | FCS0705 | 1 | 1 | 10 | AAI143-H | 4~20mA | N | %Z011110 | [5 empty] | 0 | 300 | ℃ | %Z011110 | AI |  | 70CRB02 | [5 empty] | TBF01 | 19 | 20 |  |  | 70LAA10CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-008
|  | 70LAA10CL104 | 除氧器水箱液位 | Deaerator water tank level | 70CRB02 | FCS0705 | 1 | 1 | 11 | AAI143-H | 4~20mA | N | %Z011111 | [5 empty] | 0 | 2.8 | m | %Z011111 | AI |  | 70CRB02 | [5 empty] | TBF01 | 21 | 22 |  |  | 70LAA10CL104 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-008
[5 empty] | 70CRB02 | FCS0705 | 1 | 1 | 12 | AAI143-H | 4~20mA | N | %Z011112 | [8 empty] | %Z011112 | AI |  | 70CRB02 | [5 empty] | TBF01 | 23 | 24
[5 empty] | 70CRB02 | FCS0705 | 1 | 1 | 13 | AAI143-H | 4~20mA | N | %Z011113 | [8 empty] | %Z011113 | AI |  | 70CRB02 | [5 empty] | TBF01 | 25 | 26
[5 empty] | 70CRB02 | FCS0705 | 1 | 1 | 14 | AAI143-H | 4~20mA | N | %Z011114 | [8 empty] | %Z011114 | AI |  | 70CRB02 | [5 empty] | TBF01 | 27 | 28
[5 empty] | 70CRB02 | FCS0705 | 1 | 1 | 15 | AAI143-H | 4~20mA | N | %Z011115 | [8 empty] | %Z011115 | AI |  | 70CRB02 | [5 empty] | TBF01 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 1 | 1 | 16 | AAI143-H | 4~20mA | N | %Z011116 | [8 empty] | %Z011116 | AI |  | 70CRB02 | [5 empty] | TBF01 | 31 | 32
|  | 70LAB20CP101 | 电动给水泵A入口压力 | Electrical feedwater pump A inlet pressure | 70CRB02 | FCS0705 | 2 | 1 | 1 | AAI143-H | 4~20mA | N | %Z021101 | [5 empty] | 0 | 1 | MPa | %Z021101 | AI |  | 70CRB02 | [5 empty] | TBF02 | 1 | 2 |  |  | 70LAB20CP101 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB20CT113 | 电动给水泵A入口温度 | Electrical feedwater pump A inlet temp. | 70CRB02 | FCS0705 | 2 | 1 | 2 | AAI143-H | 4~20mA | N | %Z021102 | [5 empty] | 0 | 200 | ℃ | %Z021102 | AI |  | 70CRB02 | [5 empty] | TBF02 | 3 | 4 |  |  | 70LAB20CT113 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB20CP102 | 电动给水泵A出口压力 | Electrical feedwater pump A outlet pressure | 70CRB02 | FCS0705 | 2 | 1 | 3 | AAI143-H | 4~20mA | N | %Z021103 | [5 empty] | 0 | 24 | MPa | %Z021103 | AI |  | 70CRB02 | [5 empty] | TBF02 | 5 | 6 |  |  | 70LAB20CP102 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB20CP121 | 电动给水泵A液力耦合器工作油出油压力 | Electrical feedwater pump A coupler work oil outlet pressure | 70CRB02 | FCS0705 | 2 | 1 | 4 | AAI143-H | 4~20mA | N | %Z021104 | [5 empty] | 0 | 0.6 | MPa | %Z021104 | AI |  | 70CRB02 | [5 empty] | TBF02 | 7 | 8 |  |  | 70LAB20CP121 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20CP122 | 电动给水泵A液力耦合器滤清器出口油压 | Electrical feedwater pump A coupler percolator outlet oil pressure | 70CRB02 | FCS0705 | 2 | 1 | 5 | AAI143-H | 4~20mA | N | %Z021105 | [5 empty] | 0 | 0.6 | MPa | %Z021105 | AI |  | 70CRB02 | [5 empty] | TBF02 | 9 | 10 |  |  | 70LAB20CP122 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20CP123 | 电动给水泵A液力耦合器直流润滑油泵出口压力 | Electrical feedwater pump A coupler DC lube oil pump outlet pressure | 70CRB02 | FCS0705 | 2 | 1 | 6 | AAI143-H | 4~20mA | N | %Z021106 | [5 empty] | 0 | 0.6 | MPa | %Z021106 | AI |  | 70CRB02 | [5 empty] | TBF02 | 11 | 12 |  |  | 70LAB20CP123 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-007
|  | 70MAG10CL102 | 凝汽器热井水位1 | Condenser hot well level 1 | 70CRB02 | FCS0705 | 2 | 1 | 7 | AAI143-H | 4~20mA | N | %Z021107 | [5 empty] | 0 | 1.5 | m | %Z021107 | AI |  | 70CRB02 | [5 empty] | TBF02 | 13 | 142 |  |  | 70MAG10CL102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-008
|  | 70LCA30CF101 | 除氧器进水流量1 | Deaerator inlet water flow 1 | 70CRB02 | FCS0705 | 2 | 1 | 8 | AAI143-H | 4~20mA | N | %Z021108 | [5 empty] | 57 | 207 | t/h | %Z021108 | AI |  | 70CRB02 | [5 empty] | TBF02 | 15 | 16 |  |  | 70LCA30CF101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-008
|  | 70LAA10CL101 | 除氧器水箱液位1 | Deaerator water tank level 1 | 70CRB02 | FCS0705 | 2 | 1 | 9 | AAI143-H | 4~20mA | N | %Z021109 | [5 empty] | 0 | 2.8 | m | %Z021109 | AI |  | 70CRB02 | [5 empty] | TBF02 | 17 | 18 |  |  | 70LAA10CL101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-008
|  | 70LAA10CL103 | 除氧器水箱液位3 | Deaerator water tank level 3 | 70CRB02 | FCS0705 | 2 | 1 | 10 | AAI143-H | 4~20mA | N | %Z021110 | [5 empty] | 0 | 2.8 | m | %Z021110 | AI |  | 70CRB02 | [5 empty] | TBF02 | 19 | 20 |  |  | 70LAA10CL103 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-008
|  | 70QCD11CL101 | 1#氨溶液箱液位 | 1# ammonia solution tank level | 70CRB02 | FCS0705 | 2 | 1 | 11 | AAI143-H | 4~20mA | N | %Z021111 | [5 empty] | 0 |  | m | %Z021111 | AI |  | 70CRB02 | [5 empty] | TBF02 | 21 | 22 |  |  | 70QCD10GH001 | 4~20mA | AI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCA11CL101 | 1#联氨溶液箱液位 | 1# hydrazine solution tank level | 70CRB02 | FCS0705 | 2 | 1 | 12 | AAI143-H | 4~20mA | N | %Z021112 | [5 empty] | 0 |  | m | %Z021112 | AI |  | 70CRB02 | [5 empty] | TBF02 | 23 | 24 |  |  | 70QCA10GH001 | 4~20mA | AI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCC11CL101 | 1#磷酸盐溶液箱液位 | 1# phosphate solution tank level | 70CRB02 | FCS0705 | 2 | 1 | 13 | AAI143-H | 4~20mA | N | %Z021113 | [5 empty] | 0 |  | m | %Z021113 | AI |  | 70CRB02 | [5 empty] | TBF02 | 25 | 26 |  |  | 70QCC10GH001 | 4~20mA | AI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
[5 empty] | 70CRB02 | FCS0705 | 2 | 1 | 14 | AAI143-H | 4~20mA | N | %Z021114 | [8 empty] | %Z021114 | AI |  | 70CRB02 | [5 empty] | TBF02 | 27 | 28
[5 empty] | 70CRB02 | FCS0705 | 2 | 1 | 15 | AAI143-H | 4~20mA | N | %Z021115 | [8 empty] | %Z021115 | AI |  | 70CRB02 | [5 empty] | TBF02 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 2 | 1 | 16 | AAI143-H | 4~20mA | N | %Z021116 | [8 empty] | %Z021116 | AI |  | 70CRB02 | [5 empty] | TBF02 | 31 | 32
|  | 70LAB20AP001XQ01 | 电动给水泵A断路器电流 | Electrical feedwater pump A current | 70CRB02 | FCS0705 | 2 | 2 | 1 | AAI143-H | 4~20mA | N | %Z022101 | [7 empty] | A | %Z022101 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 2 | 1 |  |  | 70LAB20AP001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB20CS121 | 电动给水泵A液力耦合器输出转速 | Electrical feedwater pump A coupler outlet speed | 70CRB02 | FCS0705 | 2 | 2 | 2 | AAI143-H | 4~20mA | N | %Z022102 | [8 empty] | %Z022102 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 4 | 3 |  |  | 70LAB20CS121 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-007
|  | 70LAB20AA121XQ11 | 电动给水泵A液力耦合器电动调节阀位置反馈 | Electrical feedwater pump A coupler regulating MOV position feedback | 70CRB02 | FCS0705 | 2 | 2 | 3 | AAI143-H | 4~20mA | N | %Z022103 | [5 empty] | 0 | 100 | % | %Z022103 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 6 | 5 |  |  | 70LAB20AA121 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-007
|  | 70LCB10AP001XQ01 | 凝结水泵A电流 | Condensate pump A current | 70CRB02 | FCS0705 | 2 | 2 | 4 | AAI143-H | 4~20mA | N | %Z022104 | [7 empty] | A | %Z022104 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 8 | 7 |  |  | 70LCB10AP001 | 4～20mA | AI | [8 empty] | DAS | U |  | K0204-008
|  | 70LCA30AA101XQ11 | 除氧器入口电动调节阀位置反馈 | Deaerator inlet regulating MOV position feedback | 70CRB02 | FCS0705 | 2 | 2 | 5 | AAI143-H | 4~20mA | N | %Z022105 | [5 empty] | 0 | 100 | % | %Z022105 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 10 | 9 |  |  | 70LCA30AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-008
|  | 70QCD11AP001XQ11 | 1#给水氨计量泵频率反馈 | 1# feed water ammonia metering pump frequency feedback | 70CRB02 | FCS0705 | 2 | 2 | 6 | AAI143-H | 4~20mA | N | %Z022106 | [5 empty] | 0 | 50 | Hz | %Z022106 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 12 | 11 |  |  | 70QCD10GH001 | 4~20mA | AI | [8 empty] | MCS | U |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCA11AP001XQ11 | 1#给水联氨计量泵频率反馈 | 1# feed water hydrazine metering pump frequency feedback | 70CRB02 | FCS0705 | 2 | 2 | 7 | AAI143-H | 4~20mA | N | %Z022107 | [5 empty] | 0 | 50 | Hz | %Z022107 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 14 | 13 |  |  | 70QCA10GH001 | 4~20mA | AI | [8 empty] | MCS | U |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QUH10CQ101 | 汽包炉水左/右侧取样水比导率 | The left /right side of boiler drum sampling specific conductivity | 70CRB02 | FCS0705 | 2 | 2 | 8 | AAI143-H | 4~20mA | N | %Z022108 | [5 empty] | 0.055 | 1000 | us/cm | %Z022108 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 16 | 15 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUH10CQ102 | 汽包炉水左/右侧取样水pH | The left /right side of boiler drum sampling pH | 70CRB02 | FCS0705 | 2 | 2 | 9 | AAI143-H | 4~20mA | N | %Z022109 | [5 empty] | 0 | 14 |  | %Z022109 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 18 | 17 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUA10CQ101 | 饱和蒸汽左/右侧取样水氢电导率 | The left /right side of saturated steam sampling cation conductivity | 70CRB02 | FCS0705 | 2 | 2 | 10 | AAI143-H | 4~20mA | N | %Z022110 | [5 empty] | 0.055 | 1000 | us/cm | %Z022110 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 20 | 19 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUA30CQ101 | 过热蒸汽取样水氢电导率 | Superheated steam sampling cation conductivity | 70CRB02 | FCS0705 | 2 | 2 | 11 | AAI143-H | 4~20mA | N | %Z022111 | [5 empty] | 0.055 | 1000 | us/cm | %Z022111 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 22 | 21 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUB20CQ101 | 省煤器入口给水取样水氢电导率 | Economizer inlet feedwater sampling cation conductivity | 70CRB02 | FCS0705 | 2 | 2 | 12 | AAI143-H | 4~20mA | N | %Z022112 | [5 empty] | 0.055 | 1000 | us/cm | %Z022112 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 24 | 23 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUB20CQ102 | 省煤器入口给水取样水比导率 | Economizer inlet feedwater sampling specific conductivity | 70CRB02 | FCS0705 | 2 | 2 | 13 | AAI143-H | 4~20mA | N | %Z022113 | [5 empty] | 0.055 | 1000 | us/cm | %Z022113 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 26 | 25 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUB20CQ103 | 省煤器入口给水取样水pH | Economizer inlet feedwater sampling pH | 70CRB02 | FCS0705 | 2 | 2 | 14 | AAI143-H | 4~20mA | N | %Z022114 | [5 empty] | 0 | 14 |  | %Z022114 | AI | 4W | 70CRB02 | [5 empty] | TBF03 | 28 | 27 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
[5 empty] | 70CRB02 | FCS0705 | 2 | 2 | 15 | AAI143-H | 4~20mA | N | %Z022115 | [8 empty] | %Z022115 | AI |  | 70CRB02 | [5 empty] | TBF03 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 2 | 2 | 16 | AAI143-H | 4~20mA | N | %Z022116 | [8 empty] | %Z022116 | AI |  | 70CRB02 | [5 empty] | TBF03 | 31 | 32
|  | 70LAB10CP101 | 电动给水泵B入口压力 | Electrical feedwater pump B inlet pressure | 70CRB02 | FCS0705 | 3 | 1 | 1 | AAI143-H | 4~20mA | N | %Z031101 | [5 empty] | 0 | 1 | MPa | %Z031101 | AI |  | 70CRB02 | [5 empty] | TBF04 | 1 | 2 |  |  | 70LAB10CP101 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB10CT113 | 电动给水泵B入口温度 | Electrical feedwater pump B inlet temp. | 70CRB02 | FCS0705 | 3 | 1 | 2 | AAI143-H | 4~20mA | N | %Z031102 | [5 empty] | 0 | 200 | ℃ | %Z031102 | AI |  | 70CRB02 | [5 empty] | TBF04 | 3 | 4 |  |  | 70LAB10CT113 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB10CP102 | 电动给水泵B出口压力 | Electrical feedwater pump B outlet pressure | 70CRB02 | FCS0705 | 3 | 1 | 3 | AAI143-H | 4~20mA | N | %Z031103 | [5 empty] | 0 | 24 | MPa | %Z031103 | AI |  | 70CRB02 | [5 empty] | TBF04 | 5 | 6 |  |  | 70LAB10CP102 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-006
|  | 70LAB10CP121 | 电动给水泵B液力耦合器工作油出油压力 | Electrical feedwater pump Bcoupler work oil outlet pressure | 70CRB02 | FCS0705 | 3 | 1 | 4 | AAI143-H | 4~20mA | N | %Z031104 | [5 empty] | 0 | 0.6 | MPa | %Z031104 | AI |  | 70CRB02 | [5 empty] | TBF04 | 7 | 8 |  |  | 70LAB10CP121 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10CP122 | 电动给水泵B液力耦合器滤清器出口油压 | Electrical feedwater pump Bcoupler percolator outlet oil pressure | 70CRB02 | FCS0705 | 3 | 1 | 5 | AAI143-H | 4~20mA | N | %Z031105 | [5 empty] | 0 | 0.6 | MPa | %Z031105 | AI |  | 70CRB02 | [5 empty] | TBF04 | 9 | 10 |  |  | 70LAB10CP122 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10CP123 | 电动给水泵B液力耦合器直流润滑油泵出口压力 | Electrical feedwater pump Bcoupler DC lube oil pump outlet pressure | 70CRB02 | FCS0705 | 3 | 1 | 6 | AAI143-H | 4~20mA | N | %Z031106 | [5 empty] | 0 | 0.6 | MPa | %Z031106 | AI |  | 70CRB02 | [5 empty] | TBF04 | 11 | 12 |  |  | 70LAB10CP123 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-007
|  | 70MAG10CL103 | 凝汽器热井水位2 | Condenser hot well level 2 | 70CRB02 | FCS0705 | 3 | 1 | 7 | AAI143-H | 4~20mA | N | %Z031107 | [5 empty] | 0 | 1.5 | m | %Z031107 | AI |  | 70CRB02 | [5 empty] | TBF04 | 13 | 142 |  |  | 70MAG10CL103 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-008
|  | 70PAB20CT101 | A侧凝汽器循环水进水温度 | Inlet water temperature of condenser by side A | 70CRB02 | FCS0705 | 3 | 1 | 8 | AAI143-H | 4~20mA | N | %Z031108 | [5 empty] | 0 | 100 | ℃ | %Z031108 | AI |  | 70CRB02 | [5 empty] | TBF04 | 15 | 16 |  |  | 70PAB20CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-014
|  | 70PAB20CP101 | A侧凝汽器循环水进水压力 | Inlet water pressure of condenser by side A | 70CRB02 | FCS0705 | 3 | 1 | 9 | AAI143-H | 4~20mA | N | %Z031109 | [5 empty] | 0 | 0.25 | MPa | %Z031109 | AI |  | 70CRB02 | [5 empty] | TBF04 | 17 | 18 |  |  | 70PAB20CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-014
|  | 70PAB40CP101 | A侧凝汽器循环水出水压力 | Outlet water pressure of condenser by side A | 70CRB02 | FCS0705 | 3 | 1 | 10 | AAI143-H | 4~20mA | N | %Z031110 | [5 empty] | 0 | 0.25 | MPa | %Z031110 | AI |  | 70CRB02 | [5 empty] | TBF04 | 19 | 20 |  |  | 70PAB40CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-014
|  | 70PAB40CT101 | A侧凝汽器循环水出水温度 | Outlet water pressure of condenser by side A | 70CRB02 | FCS0705 | 3 | 1 | 11 | AAI143-H | 4~20mA | N | %Z031111 | [5 empty] | 0 | 100 | ℃ | %Z031111 | AI |  | 70CRB02 | [5 empty] | TBF04 | 21 | 22 |  |  | 70PAB40CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-014
[5 empty] | 70CRB02 | FCS0705 | 3 | 1 | 12 | AAI143-H | 4~20mA | N | %Z031112 | [8 empty] | %Z031112 | AI |  | 70CRB02 | [5 empty] | TBF04 | 23 | 24
[5 empty] | 70CRB02 | FCS0705 | 3 | 1 | 13 | AAI143-H | 4~20mA | N | %Z031113 | [8 empty] | %Z031113 | AI |  | 70CRB02 | [5 empty] | TBF04 | 25 | 26
[5 empty] | 70CRB02 | FCS0705 | 3 | 1 | 14 | AAI143-H | 4~20mA | N | %Z031114 | [8 empty] | %Z031114 | AI |  | 70CRB02 | [5 empty] | TBF04 | 27 | 28
[5 empty] | 70CRB02 | FCS0705 | 3 | 1 | 15 | AAI143-H | 4~20mA | N | %Z031115 | [8 empty] | %Z031115 | AI |  | 70CRB02 | [5 empty] | TBF04 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 3 | 1 | 16 | AAI143-H | 4~20mA | N | %Z031116 | [8 empty] | %Z031116 | AI |  | 70CRB02 | [5 empty] | TBF04 | 31 | 32
|  | 70LAB10AP001XQ01 | 电动给水泵B断路器电流 | Electrical feedwater pump B current | 70CRB02 | FCS0705 | 3 | 2 | 1 | AAI143-H | 4~20mA | N | %Z032101 | [7 empty] | A | %Z032101 | AI | 4W | 70CRB02 | [5 empty] | TBF05 | 2 | 1 |  |  | 70LAB10AP001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LAB10CS121 | 电动给水泵B液力耦合器输出转速 | Electrical feedwater pump Bcoupler outlet speed | 70CRB02 | FCS0705 | 3 | 2 | 2 | AAI143-H | 4~20mA | N | %Z032102 | [8 empty] | %Z032102 | AI | 4W | 70CRB02 | [5 empty] | TBF05 | 4 | 3 |  |  | 70LAB10CS121 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-007
|  | 70LAB10AA121XQ11 | 电动给水泵B液力耦合器电动调节阀位置反馈 | Electrical feedwater pump B coupler regulating MOV position feedback | 70CRB02 | FCS0705 | 3 | 2 | 3 | AAI143-H | 4~20mA | N | %Z032103 | [5 empty] | 0 | 100 | % | %Z032103 | AI | 4W | 70CRB02 | [5 empty] | TBF05 | 6 | 5 |  |  | 70LAB10AA121 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-007
|  | 70LCB10AP002XQ01 | 凝结水泵B电流 | Condensate pump B current | 70CRB02 | FCS0705 | 3 | 2 | 4 | AAI143-H | 4~20mA | N | %Z032104 | [7 empty] | A | %Z032104 | AI | 4W | 70CRB02 | [5 empty] | TBF05 | 8 | 7 |  |  | 70LCB10AP002 | 4～20mA | AI | [8 empty] | DAS | U |  | K0204-008
|  | 70MAG12CQ101 | 真空泵A漏气量 | Vacuum pump A leakage | 70CRB02 | FCS0705 | 3 | 2 | 5 | AAI143-H | 4~20mA | N | %Z032105 | [5 empty] | 0 | 240 | Kg/h | %Z032105 | AI | 4W | 70CRB02 | [5 empty] | TBF05 | 10 | 9 |  |  | 70MAG12CQ101 | 4~20mA | AI | [8 empty] | DAS | U |  | K0204-003
|  | 70MAG12AP001XQ01 | 真空泵A电流 | Vacuum pump A current | 70CRB02 | FCS0705 | 3 | 2 | 6 | AAI143-H | 4~20mA | N | %Z032106 | [5 empty] | 0 |  | A | %Z032106 | AI | 4W | 70CRB02 | [5 empty] | TBF05 | 12 | 11 |  |  | 70MAG12AP001 | 4～20mA | AI | [8 empty] | DAS | U |  | K0204-003
|  | 70MAG10CP101 | 凝汽器真空1 | Condenser vacuum pressure 1 | 70CRB02 | FCS0705 | 3 | 2 | 7 | AAI143-H | 4~20mA | N | %Z032107 | [5 empty] | 0 | 0.2 | MPa | %Z032107 | AI |  | 70CRB02 | [5 empty] | TBF05 | 13 | 142 |  |  | 70MAG10CP101 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG12CL101 | 真空泵A分离罐液位 | Vacuum pump A separator level | 70CRB02 | FCS0705 | 3 | 2 | 8 | AAI143-H | 4~20mA | N | %Z032108 | [5 empty] | 0 |  | mm | %Z032108 | AI |  | 70CRB02 | [5 empty] | TBF05 | 15 | 16 |  |  | 70MAG12GH002 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
|  | 70QUC10CQ101 | 凝结水泵出口取样水氢电导率 | Condensate pump outlet water sampling cation conductivity | 70CRB02 | FCS0705 | 3 | 2 | 9 | AAI143-H | 4~20mA | N | %Z032109 | [5 empty] | 0.055 | 1000 | us/cm | %Z032109 | AI | 4W | 70CRB02 | [5 empty] | TBF05 | 18 | 17 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUC10CQ102 | 凝结水泵出口取样水含氧量 | Condensate pump outlet water sampling dissolved oxygen | 70CRB02 | FCS0705 | 3 | 2 | 10 | AAI143-H | 4~20mA | N | %Z032110 | [5 empty] | 0.01 | 300 | ppb | %Z032110 | AI | 4W | 70CRB02 | [5 empty] | TBF05 | 20 | 19 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUB30CQ101 | 除氧器出口给水取样水含氧量 | Deaerator outlet feedwater sampling dissolved oxygen | 70CRB02 | FCS0705 | 3 | 2 | 11 | AAI143-H | 4~20mA | N | %Z032111 | [5 empty] | 0.01 | 300 | ppb | %Z032111 | AI | 4W | 70CRB02 | [5 empty] | TBF05 | 22 | 21 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUH10CP101 | 除盐水冷却水进水压力 | Demineralized cooling water inlet water pressure | 70CRB02 | FCS0705 | 3 | 2 | 12 | AAI143-H | 4~20mA | N | %Z032112 | [5 empty] | 0 | 1.6 | Mpa | %Z032112 | AI |  | 70CRB02 | [5 empty] | TBF05 | 23 | 24 |  |  | 70QUH10GH001 | 4~20mA | AI | [8 empty] | DAS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
[5 empty] | 70CRB02 | FCS0705 | 3 | 2 | 13 | AAI143-H | 4~20mA | N | %Z032113 | [8 empty] | %Z032113 | AI |  | 70CRB02 | [5 empty] | TBF05 | 25 | 26
[5 empty] | 70CRB02 | FCS0705 | 3 | 2 | 14 | AAI143-H | 4~20mA | N | %Z032114 | [8 empty] | %Z032114 | AI |  | 70CRB02 | [5 empty] | TBF05 | 27 | 28
[5 empty] | 70CRB02 | FCS0705 | 3 | 2 | 15 | AAI143-H | 4~20mA | N | %Z032115 | [8 empty] | %Z032115 | AI |  | 70CRB02 | [5 empty] | TBF05 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 3 | 2 | 16 | AAI143-H | 4~20mA | N | %Z032116 | [8 empty] | %Z032116 | AI |  | 70CRB02 | [5 empty] | TBF05 | 31 | 32
|  | 70MAG10CL104 | 凝汽器热井水位3 | Condenser hot well level 3 | 70CRB02 | FCS0705 | 4 | 1 | 1 | AAI143-H | 4~20mA | N | %Z041101 | [5 empty] | 0 | 1.5 | m | %Z041101 | AI |  | 70CRB02 | [5 empty] | TBF06 | 1 | 2 |  |  | 70MAG10CL104 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-008
|  | 70GHC50CF101 | 凝汽器补水流量 | Condensate make-up water flow | 70CRB02 | FCS0705 | 4 | 1 | 2 | AAI143-H | 4~20mA | N | %Z041102 | [5 empty] | 0 | 12 | t/h | %Z041102 | AI |  | 70CRB02 | [5 empty] | TBF06 | 3 | 4 |  |  | 70GHC50CF101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-015
|  | 70PAB10CT101 | B侧凝汽器循环水进水温度 | Inlet water temperature of condenser by side B | 70CRB02 | FCS0705 | 4 | 1 | 3 | AAI143-H | 4~20mA | N | %Z041103 | [5 empty] | 0 | 100 | ℃ | %Z041103 | AI |  | 70CRB02 | [5 empty] | TBF06 | 5 | 6 |  |  | 70PAB10CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-014
|  | 70PAB10CP101 | B侧凝汽器循环水进水压力 | Inlet water pressure of condenser by side B | 70CRB02 | FCS0705 | 4 | 1 | 4 | AAI143-H | 4~20mA | N | %Z041104 | [5 empty] | 0 | 0.25 | MPa | %Z041104 | AI |  | 70CRB02 | [5 empty] | TBF06 | 7 | 8 |  |  | 70PAB10CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-014
|  | 70PAB30CP101 | B侧凝汽器循环水出水压力 | Outlet water pressure of condenser by side B | 70CRB02 | FCS0705 | 4 | 1 | 5 | AAI143-H | 4~20mA | N | %Z041105 | [5 empty] | 0 | 0.25 | MPa | %Z041105 | AI |  | 70CRB02 | [5 empty] | TBF06 | 9 | 10 |  |  | 70PAB30CP101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-014
|  | 70PAB30CT101 | B侧凝汽器循环水出水温度 | Outlet water pressure of condenser by side B | 70CRB02 | FCS0705 | 4 | 1 | 6 | AAI143-H | 4~20mA | N | %Z041106 | [5 empty] | 0 | 100 | ℃ | %Z041106 | AI |  | 70CRB02 | [5 empty] | TBF06 | 11 | 12 |  |  | 70PAB30CT101 | 4~20mA | AI | [8 empty] | DAS | D |  | K0204-014
|  | 70LCA30CF102 | 除氧器进水流量2 | Deaerator inlet water flow 2 | 70CRB02 | FCS0705 | 4 | 1 | 7 | AAI143-H | 4~20mA | N | %Z041107 | [5 empty] | 57 | 207 | t/h | %Z041107 | AI |  | 70CRB02 | [5 empty] | TBF06 | 13 | 142 |  |  | 70LCA30CF102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-008
|  | 70LAA10CL102 | 除氧器水箱液位2 | Deaerator water tank level 2 | 70CRB02 | FCS0705 | 4 | 1 | 8 | AAI143-H | 4~20mA | N | %Z041108 | [5 empty] | 0 | 2.8 | m | %Z041108 | AI |  | 70CRB02 | [5 empty] | TBF06 | 15 | 16 |  |  | 70LAA10CL102 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-008
|  | 70GHC10CF101 | 除氧器补水流量 | Deaerator make-up water flow | 70CRB02 | FCS0705 | 4 | 1 | 9 | AAI143-H | 4~20mA | N | %Z041109 | [5 empty] | 0 | 200 | t/h | %Z041109 | AI |  | 70CRB02 | [5 empty] | TBF06 | 17 | 18 |  |  | 70GHC10CF101 | 4~20mA | AI | [8 empty] | MCS | D |  | K0204-015
|  | 70QCD12CL101 | 2#氨溶液箱液位 | 2# ammonia solution tank level | 70CRB02 | FCS0705 | 4 | 1 | 10 | AAI143-H | 4~20mA | N | %Z041110 | [5 empty] | 0 |  | m | %Z041110 | AI |  | 70CRB02 | [5 empty] | TBF06 | 19 | 20 |  |  | 70QCD10GH001 | 4~20mA | AI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCA12CL101 | 2#联氨溶液箱液位 | 2# hydrazine solution tank level | 70CRB02 | FCS0705 | 4 | 1 | 11 | AAI143-H | 4~20mA | N | %Z041111 | [5 empty] | 0 |  | m | %Z041111 | AI |  | 70CRB02 | [5 empty] | TBF06 | 21 | 22 |  |  | 70QCA10GH001 | 4~20mA | AI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCC12CL101 | 2#磷酸盐溶液箱液位 | 2# phosphate solution tank level | 70CRB02 | FCS0705 | 4 | 1 | 12 | AAI143-H | 4~20mA | N | %Z041112 | [5 empty] | 0 |  | m | %Z041112 | AI |  | 70CRB02 | [5 empty] | TBF06 | 23 | 24 |  |  | 70QCC10GH001 | 4~20mA | AI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
[5 empty] | 70CRB02 | FCS0705 | 4 | 1 | 13 | AAI143-H | 4~20mA | N | %Z041113 | [8 empty] | %Z041113 | AI |  | 70CRB02 | [5 empty] | TBF06 | 25 | 26
[5 empty] | 70CRB02 | FCS0705 | 4 | 1 | 14 | AAI143-H | 4~20mA | N | %Z041114 | [8 empty] | %Z041114 | AI |  | 70CRB02 | [5 empty] | TBF06 | 27 | 28
[5 empty] | 70CRB02 | FCS0705 | 4 | 1 | 15 | AAI143-H | 4~20mA | N | %Z041115 | [8 empty] | %Z041115 | AI |  | 70CRB02 | [5 empty] | TBF06 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 4 | 1 | 16 | AAI143-H | 4~20mA | N | %Z041116 | [8 empty] | %Z041116 | AI |  | 70CRB02 | [5 empty] | TBF06 | 31 | 32
|  | 70LCB10AP003XQ01 | 凝结水泵C电流 | Condensate pump C current | 70CRB02 | FCS0705 | 4 | 2 | 1 | AAI143-H | 4~20mA | N | %Z042101 | [7 empty] | A | %Z042101 | AI | 4W | 70CRB02 | [5 empty] | TBF07 | 2 | 1 |  |  | 70LCB10AP003 | 4～20mA | AI | [8 empty] | DAS | U |  | K0204-008
|  | 70LCA40AA101XQ11 | 凝结水再循电动调节阀阀位反馈 | Condensate water recirculation regulating MOV position feedback | 70CRB02 | FCS0705 | 4 | 2 | 2 | AAI143-H | 4~20mA | N | %Z042102 | [5 empty] | 0 | 100 | % | %Z042102 | AI | 4W | 70CRB02 | [5 empty] | TBF07 | 4 | 3 |  |  | 70LCA40AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-008
|  | 70GHC50AA101XQ11 | 凝汽器补水电动调节阀位置反馈 | Condensate make-up water regulating MOV position feedback | 70CRB02 | FCS0705 | 4 | 2 | 3 | AAI143-H | 4~20mA | N | %Z042103 | [5 empty] | 0 | 100 | % | %Z042103 | AI | 4W | 70CRB02 | [5 empty] | TBF07 | 6 | 5 |  |  | 70GHC50AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-015
|  | 70GHC10AA101XQ11 | 除氧器补水电动调节阀位置反馈 | Deaerator make-up water regulating MOV position feedback | 70CRB02 | FCS0705 | 4 | 2 | 4 | AAI143-H | 4~20mA | N | %Z042104 | [5 empty] | 0 | 100 | % | %Z042104 | AI | 4W | 70CRB02 | [5 empty] | TBF07 | 8 | 7 |  |  | 70GHC10AA101 | 4~20mA | AI | [8 empty] | MCS | U |  | K0204-015
|  | 70QCD12AP001XQ11 | 2#给水氨计量泵频率反馈 | 2# feed water ammonia metering pump frequency feedback | 70CRB02 | FCS0705 | 4 | 2 | 5 | AAI143-H | 4~20mA | N | %Z042105 | [5 empty] | 0 | 50 | Hz | %Z042105 | AI | 4W | 70CRB02 | [5 empty] | TBF07 | 10 | 9 |  |  | 70QCD10GH001 | 4~20mA | AI | [8 empty] | MCS | U |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCA12AP001XQ11 | 2#给水联氨计量泵频率反馈 | 2# feed water hydrazine metering pump frequency feedback | 70CRB02 | FCS0705 | 4 | 2 | 6 | AAI143-H | 4~20mA | N | %Z042106 | [5 empty] | 0 | 50 | Hz | %Z042106 | AI | 4W | 70CRB02 | [5 empty] | TBF07 | 12 | 11 |  |  | 70QCA10GH001 | 4~20mA | AI | [8 empty] | MCS | U |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70MAG11CQ101 | 真空泵B漏气量 | Vacuum pump B leakage | 70CRB02 | FCS0705 | 4 | 2 | 7 | AAI143-H | 4~20mA | N | %Z042107 | [5 empty] | 0 | 240 | Kg/h | %Z042107 | AI | 4W | 70CRB02 | [5 empty] | TBF07 | 14 | 13 |  |  | 70MAG11CQ101 | 4~20mA | AI | [8 empty] | DAS | U |  | K0204-003
|  | 70MAG11AP001XQ01 | 真空泵B电流 | Vacuum pump B current | 70CRB02 | FCS0705 | 4 | 2 | 8 | AAI143-H | 4~20mA | N | %Z042108 | [5 empty] | 0 |  | A | %Z042108 | AI | 4W | 70CRB02 | [5 empty] | TBF07 | 16 | 15 |  |  | 70MAG11AP001 | 4～20mA | AI | [8 empty] | DAS | U |  | K0204-003
|  | 70MAG10CP102 | 凝汽器真空2 | Condenser vacuum pressure 2 | 70CRB02 | FCS0705 | 4 | 2 | 9 | AAI143-H | 4~20mA | N | %Z042109 | [5 empty] | 0 | 0.2 | MPa | %Z042109 | AI |  | 70CRB02 | [5 empty] | TBF07 | 17 | 18 |  |  | 70MAG10CP102 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG11CL101 | 真空泵B分离罐液位 | Vacuum pump B separator level | 70CRB02 | FCS0705 | 4 | 2 | 10 | AAI143-H | 4~20mA | N | %Z042110 | [5 empty] | 0 |  | mm | %Z042110 | AI |  | 70CRB02 | [5 empty] | TBF07 | 19 | 20 |  |  | 70MAG11GH002 | 4~20mA | AI | [8 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
[5 empty] | 70CRB02 | FCS0705 | 4 | 2 | 11 | AAI143-H | 4~20mA | N | %Z042111 | [8 empty] | %Z042111 | AI |  | 70CRB02 | [5 empty] | TBF07 | 21 | 22
[5 empty] | 70CRB02 | FCS0705 | 4 | 2 | 12 | AAI143-H | 4~20mA | N | %Z042112 | [8 empty] | %Z042112 | AI |  | 70CRB02 | [5 empty] | TBF07 | 23 | 24
[5 empty] | 70CRB02 | FCS0705 | 4 | 2 | 13 | AAI143-H | 4~20mA | N | %Z042113 | [8 empty] | %Z042113 | AI |  | 70CRB02 | [5 empty] | TBF07 | 25 | 26
[5 empty] | 70CRB02 | FCS0705 | 4 | 2 | 14 | AAI143-H | 4~20mA | N | %Z042114 | [8 empty] | %Z042114 | AI |  | 70CRB02 | [5 empty] | TBF07 | 27 | 28
[5 empty] | 70CRB02 | FCS0705 | 4 | 2 | 15 | AAI143-H | 4~20mA | N | %Z042115 | [8 empty] | %Z042115 | AI |  | 70CRB02 | [5 empty] | TBF07 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 4 | 2 | 16 | AAI143-H | 4~20mA | N | %Z042116 | [8 empty] | %Z042116 | AI |  | 70CRB02 | [5 empty] | TBF07 | 31 | 32
|  | 70LAB20CT101 | 电动给水泵A电机定子线圈U向温度1 | Electrical feedwater pump A motor stator winding U temp.1 | 70CRB02 | FCS0705 | 2 | 3 | 1 | AAR181-S | PT100 | N | %Z023101 | [5 empty] | 0 | 100 | ℃ | %Z023101 | AI |  | 70CRB02 | [5 empty] | TBG02 | 1 | 2 | 3 |  | 70LAB20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
|  | 70LAB20CT103 | 电动给水泵A电机定子线圈V向温度1 | Electrical feedwater pump A motor stator winding V temp.1 | 70CRB02 | FCS0705 | 2 | 3 | 2 | AAR181-S | PT100 | N | %Z023102 | [5 empty] | 0 | 100 | ℃ | %Z023102 | AI |  | 70CRB02 | [5 empty] | TBG02 | 4 | 5 | 6 |  | 70LAB20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
|  | 70LAB20CT105 | 电动给水泵A电机定子线圈W向温度1 | Electrical feedwater pump A motor stator winding W temp.1 | 70CRB02 | FCS0705 | 2 | 3 | 3 | AAR181-S | PT100 | N | %Z023103 | [5 empty] | 0 | 100 | ℃ | %Z023103 | AI |  | 70CRB02 | [5 empty] | TBG02 | 7 | 8 | 9 |  | 70LAB20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
|  | 70LAB20CT107 | 电动给水泵A电机自由端轴承温度 | Electrical feedwater pump A motor free end bearing temp. | 70CRB02 | FCS0705 | 2 | 3 | 4 | AAR181-S | PT100 | N | %Z023104 | [5 empty] | 0 | 100 | ℃ | %Z023104 | AI |  | 70CRB02 | [5 empty] | TBG02 | 10 | 11 | 12 |  | 70LAB20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
|  | 70LAB20CT109 | 电动给水泵A自由端轴承温度 | Electrical feedwater pump A free end bearing temp. | 70CRB02 | FCS0705 | 2 | 3 | 5 | AAR181-S | PT100 | N | %Z023105 | [5 empty] | 0 | 100 | ℃ | %Z023105 | AI |  | 70CRB02 | [5 empty] | TBG02 | 13 | 14 | 15 |  | 70LAB20GH002 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A仪表接线箱 | Electrical feedwater pump A instrument junction box
|  | 70LAB20CT111 | 电动给水泵A自由端机封冲洗水温度 | Electrical feedwater pump A motor free end machine seal flushing water Temp. | 70CRB02 | FCS0705 | 2 | 3 | 6 | AAR181-S | PT100 | N | %Z023106 | [5 empty] | 0 | 200 | ℃ | %Z023106 | AI |  | 70CRB02 | [5 empty] | TBG02 | 16 | 17 | 18 |  | 70LAB20GH002 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A仪表接线箱 | Electrical feedwater pump A instrument junction box
|  | 70LAB20CT121 | 电动给水泵A液力耦合器1#轴瓦温度 | Electrical feedwater pump A coupler 1# bearing temperature | 70CRB02 | FCS0705 | 2 | 3 | 7 | AAR181-S | PT100 | N | %Z023107 | [5 empty] | 0 | 200 | ℃ | %Z023107 | AI |  | 70CRB02 | [5 empty] | TBG02 | 19 | 20 | 21 |  | 70LAB20CT121 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20CT123 | 电动给水泵A液力耦合器3#轴瓦温度 | Electrical feedwater pump A coupler 3# bearing temperature | 70CRB02 | FCS0705 | 2 | 3 | 8 | AAR181-S | PT100 | N | %Z023108 | [5 empty] | 0 | 200 | ℃ | %Z023108 | AI |  | 70CRB02 | [5 empty] | TBG02 | 22 | 23 | 24 |  | 70LAB20CT123 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20CT125 | 电动给水泵A液力耦合器5#轴瓦温度 | Electrical feedwater pump A coupler 5# bearing temperature | 70CRB02 | FCS0705 | 2 | 3 | 9 | AAR181-S | PT100 | N | %Z023109 | [5 empty] | 0 | 200 | ℃ | %Z023109 | AI |  | 70CRB02 | [5 empty] | TBG02 | 25 | 26 | 27 |  | 70LAB20CT125 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20CT127 | 电动给水泵A液力耦合器工作油出油温度 | Electrical feedwater pump A coupler work oil outlet temperature | 70CRB02 | FCS0705 | 2 | 3 | 10 | AAR181-S | PT100 | N | %Z023110 | [5 empty] | 0 | 100 | ℃ | %Z023110 | AI |  | 70CRB02 | [5 empty] | TBG02 | 28 | 29 | 30 |  | 70LAB20CT127 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20CT129 | 电动给水泵A液力耦合器直流润滑油泵出口温度 | Electrical feedwater pump A coupler DC lube oil pump outlet temperature | 70CRB02 | FCS0705 | 2 | 3 | 11 | AAR181-S | PT100 | N | %Z023111 | [5 empty] | 0 | 100 | ℃ | %Z023111 | AI |  | 70CRB02 | [5 empty] | TBG02 | 31 | 32 | 33 |  | 70LAB20CT129 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
[5 empty] | 70CRB02 | FCS0705 | 2 | 3 | 12 | AAR181-S | PT100 | N | %Z023112 | [8 empty] | %Z023112 | AI |  | 70CRB02 | [5 empty] | TBG02 | 34 | 35 | 36
|  | 70LAB20CT102 | 电动给水泵A电机定子线圈U向温度2 | Electrical feedwater pump A motor stator winding U temp.2 | 70CRB02 | FCS0705 | 2 | 4 | 1 | AAR181-S | PT100 | N | %Z024101 | [5 empty] | 0 | 100 | ℃ | %Z024101 | AI |  | 70CRB02 | [5 empty] | TBG03 | 1 | 2 | 3 |  | 70LAB20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
|  | 70LAB20CT104 | 电动给水泵A电机定子线圈V向温度2 | Electrical feedwater pump A motor stator winding V temp.2 | 70CRB02 | FCS0705 | 2 | 4 | 2 | AAR181-S | PT100 | N | %Z024102 | [5 empty] | 0 | 100 | ℃ | %Z024102 | AI |  | 70CRB02 | [5 empty] | TBG03 | 4 | 5 | 6 |  | 70LAB20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
|  | 70LAB20CT106 | 电动给水泵A电机定子线圈W向温度2 | Electrical feedwater pump A motor stator winding W temp.2 | 70CRB02 | FCS0705 | 2 | 4 | 3 | AAR181-S | PT100 | N | %Z024103 | [5 empty] | 0 | 100 | ℃ | %Z024103 | AI |  | 70CRB02 | [5 empty] | TBG03 | 7 | 8 | 9 |  | 70LAB20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
|  | 70LAB20CT108 | 电动给水泵A电机传动端轴承温度 | Electrical feedwater pump A motor drive end bearing Temp. | 70CRB02 | FCS0705 | 2 | 4 | 4 | AAR181-S | PT100 | N | %Z024104 | [5 empty] | 0 | 100 | ℃ | %Z024104 | AI |  | 70CRB02 | [5 empty] | TBG03 | 10 | 11 | 12 |  | 70LAB20GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
|  | 70LAB20CT110 | 电动给水泵A传动端轴承温度 | Electrical feedwater pump A drive end bearing temp. | 70CRB02 | FCS0705 | 2 | 4 | 5 | AAR181-S | PT100 | N | %Z024105 | [5 empty] | 0 | 100 | ℃ | %Z024105 | AI |  | 70CRB02 | [5 empty] | TBG03 | 13 | 14 | 15 |  | 70LAB20GH002 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A仪表接线箱 | Electrical feedwater pump A instrument junction box
|  | 70LAB20CT112 | 电动给水泵A传动端机封冲洗水温度 | Electrical feedwater pump A motor drive end machine seal flushing water Temp. | 70CRB02 | FCS0705 | 2 | 4 | 6 | AAR181-S | PT100 | N | %Z024106 | [5 empty] | 0 | 200 | ℃ | %Z024106 | AI |  | 70CRB02 | [5 empty] | TBG03 | 16 | 17 | 18 |  | 70LAB20GH002 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A仪表接线箱 | Electrical feedwater pump A instrument junction box
|  | 70LAB20CT122 | 电动给水泵A液力耦合器2#轴瓦温度 | Electrical feedwater pump A coupler 2# bearing temperature | 70CRB02 | FCS0705 | 2 | 4 | 7 | AAR181-S | PT100 | N | %Z024107 | [5 empty] | 0 | 200 | ℃ | %Z024107 | AI |  | 70CRB02 | [5 empty] | TBG03 | 19 | 20 | 21 |  | 70LAB20CT122 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20CT124 | 电动给水泵A液力耦合器4#轴瓦温度 | Electrical feedwater pump A coupler 4# bearing temperature | 70CRB02 | FCS0705 | 2 | 4 | 8 | AAR181-S | PT100 | N | %Z024108 | [5 empty] | 0 | 200 | ℃ | %Z024108 | AI |  | 70CRB02 | [5 empty] | TBG03 | 22 | 23 | 24 |  | 70LAB20CT124 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20CT126 | 电动给水泵A液力耦合器6#轴瓦温度 | Electrical feedwater pump A coupler 6# bearing temperature | 70CRB02 | FCS0705 | 2 | 4 | 9 | AAR181-S | PT100 | N | %Z024109 | [5 empty] | 0 | 200 | ℃ | %Z024109 | AI |  | 70CRB02 | [5 empty] | TBG03 | 25 | 26 | 27 |  | 70LAB20CT126 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20CT128 | 电动给水泵A液力耦合器工作油进油温度 | Electrical feedwater pump A coupler work oil inlet temperature | 70CRB02 | FCS0705 | 2 | 4 | 10 | AAR181-S | PT100 | N | %Z024110 | [5 empty] | 0 | 100 | ℃ | %Z024110 | AI |  | 70CRB02 | [5 empty] | TBG03 | 28 | 29 | 30 |  | 70LAB20CT128 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
[5 empty] | 70CRB02 | FCS0705 | 2 | 4 | 11 | AAR181-S | PT100 | N | %Z024111 | [8 empty] | %Z024111 | AI |  | 70CRB02 | [5 empty] | TBG03 | 31 | 32 | 33
[5 empty] | 70CRB02 | FCS0705 | 2 | 4 | 12 | AAR181-S | PT100 | N | %Z024112 | [8 empty] | %Z024112 | AI |  | 70CRB02 | [5 empty] | TBG03 | 34 | 35 | 36
|  | 70LAB10CT101 | 电动给水泵B电机定子线圈U向温度1 | Electrical feedwater pump B motor stator winding U temp.1 | 70CRB02 | FCS0705 | 3 | 3 | 1 | AAR181-S | PT100 | N | %Z033101 | [5 empty] | 0 | 100 | ℃ | %Z033101 | AI |  | 70CRB02 | [5 empty] | TBG04 | 1 | 2 | 3 |  | 70LAB10GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
|  | 70LAB10CT103 | 电动给水泵B电机定子线圈V向温度1 | Electrical feedwater pump B motor stator winding V temp.1 | 70CRB02 | FCS0705 | 3 | 3 | 2 | AAR181-S | PT100 | N | %Z033102 | [5 empty] | 0 | 100 | ℃ | %Z033102 | AI |  | 70CRB02 | [5 empty] | TBG04 | 4 | 5 | 6 |  | 70LAB10GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
|  | 70LAB10CT105 | 电动给水泵B电机定子线圈W向温度1 | Electrical feedwater pump B motor stator winding W temp.1 | 70CRB02 | FCS0705 | 3 | 3 | 3 | AAR181-S | PT100 | N | %Z033103 | [5 empty] | 0 | 100 | ℃ | %Z033103 | AI |  | 70CRB02 | [5 empty] | TBG04 | 7 | 8 | 9 |  | 70LAB10GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
|  | 70LAB10CT107 | 电动给水泵B电机自由端轴承温度 | Electrical feedwater pump B motor free end bearing temp. | 70CRB02 | FCS0705 | 3 | 3 | 4 | AAR181-S | PT100 | N | %Z033104 | [5 empty] | 0 | 100 | ℃ | %Z033104 | AI |  | 70CRB02 | [5 empty] | TBG04 | 10 | 11 | 12 |  | 70LAB10GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
|  | 70LAB10CT109 | 电动给水泵B自由端轴承温度 | Electrical feedwater pump B free end bearing temp. | 70CRB02 | FCS0705 | 3 | 3 | 5 | AAR181-S | PT100 | N | %Z033105 | [5 empty] | 0 | 100 | ℃ | %Z033105 | AI |  | 70CRB02 | [5 empty] | TBG04 | 13 | 14 | 15 |  | 70LAB10GH002 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B仪表接线箱 | Electrical feedwater pump B instrument junction box
|  | 70LAB10CT111 | 电动给水泵B自由端机封冲洗水温度 | Electrical feedwater pump B motor free end machine seal flushing water Temp. | 70CRB02 | FCS0705 | 3 | 3 | 6 | AAR181-S | PT100 | N | %Z033106 | [5 empty] | 0 | 200 | ℃ | %Z033106 | AI |  | 70CRB02 | [5 empty] | TBG04 | 16 | 17 | 18 |  | 70LAB10GH002 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B仪表接线箱 | Electrical feedwater pump B instrument junction box
|  | 70LAB10CT121 | 电动给水泵B液力耦合器1#轴瓦温度 | Electrical feedwater pump Bcoupler 1# bearing temperature | 70CRB02 | FCS0705 | 3 | 3 | 7 | AAR181-S | PT100 | N | %Z033107 | [5 empty] | 0 | 200 | ℃ | %Z033107 | AI |  | 70CRB02 | [5 empty] | TBG04 | 19 | 20 | 21 |  | 70LAB10CT121 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10CT123 | 电动给水泵B液力耦合器3#轴瓦温度 | Electrical feedwater pump Bcoupler 3# bearing temperature | 70CRB02 | FCS0705 | 3 | 3 | 8 | AAR181-S | PT100 | N | %Z033108 | [5 empty] | 0 | 200 | ℃ | %Z033108 | AI |  | 70CRB02 | [5 empty] | TBG04 | 22 | 23 | 24 |  | 70LAB10CT123 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10CT125 | 电动给水泵B液力耦合器5#轴瓦温度 | Electrical feedwater pump Bcoupler 5# bearing temperature | 70CRB02 | FCS0705 | 3 | 3 | 9 | AAR181-S | PT100 | N | %Z033109 | [5 empty] | 0 | 200 | ℃ | %Z033109 | AI |  | 70CRB02 | [5 empty] | TBG04 | 25 | 26 | 27 |  | 70LAB10CT125 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10CT127 | 电动给水泵B液力耦合器工作油出油温度 | Electrical feedwater pump Bcoupler work oil outlet temperature | 70CRB02 | FCS0705 | 3 | 3 | 10 | AAR181-S | PT100 | N | %Z033110 | [5 empty] | 0 | 100 | ℃ | %Z033110 | AI |  | 70CRB02 | [5 empty] | TBG04 | 28 | 29 | 30 |  | 70LAB10CT127 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10CT129 | 电动给水泵B液力耦合器直流润滑油泵出口温度 | Electrical feedwater pump Bcoupler DC lube oil pump outlet temperature | 70CRB02 | FCS0705 | 3 | 3 | 11 | AAR181-S | PT100 | N | %Z033111 | [5 empty] | 0 | 100 | ℃ | %Z033111 | AI |  | 70CRB02 | [5 empty] | TBG04 | 31 | 32 | 33 |  | 70LAB10CT129 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
[5 empty] | 70CRB02 | FCS0705 | 3 | 3 | 12 | AAR181-S | PT100 | N | %Z033112 | [8 empty] | %Z033112 | AI |  | 70CRB02 | [5 empty] | TBG04 | 34 | 35 | 36
|  | 70LAB10CT102 | 电动给水泵B电机定子线圈U向温度2 | Electrical feedwater pump B motor stator winding U temp.2 | 70CRB02 | FCS0705 | 3 | 4 | 1 | AAR181-S | PT100 | N | %Z034101 | [5 empty] | 0 | 100 | ℃ | %Z034101 | AI |  | 70CRB02 | [5 empty] | TBG05 | 1 | 2 | 3 |  | 70LAB10GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
|  | 70LAB10CT104 | 电动给水泵B电机定子线圈V向温度2 | Electrical feedwater pump B motor stator winding V temp.2 | 70CRB02 | FCS0705 | 3 | 4 | 2 | AAR181-S | PT100 | N | %Z034102 | [5 empty] | 0 | 100 | ℃ | %Z034102 | AI |  | 70CRB02 | [5 empty] | TBG05 | 4 | 5 | 6 |  | 70LAB10GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
|  | 70LAB10CT106 | 电动给水泵B电机定子线圈W向温度2 | Electrical feedwater pump B motor stator winding W temp.2 | 70CRB02 | FCS0705 | 3 | 4 | 3 | AAR181-S | PT100 | N | %Z034103 | [5 empty] | 0 | 100 | ℃ | %Z034103 | AI |  | 70CRB02 | [5 empty] | TBG05 | 7 | 8 | 9 |  | 70LAB10GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
|  | 70LAB10CT108 | 电动给水泵B电机传动端轴承温度 | Electrical feedwater pump B motor drive end bearing Temp. | 70CRB02 | FCS0705 | 3 | 4 | 4 | AAR181-S | PT100 | N | %Z034104 | [5 empty] | 0 | 100 | ℃ | %Z034104 | AI |  | 70CRB02 | [5 empty] | TBG05 | 10 | 11 | 12 |  | 70LAB10GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
|  | 70LAB10CT110 | 电动给水泵B传动端轴承温度 | Electrical feedwater pump B drive end bearing temp. | 70CRB02 | FCS0705 | 3 | 4 | 5 | AAR181-S | PT100 | N | %Z034105 | [5 empty] | 0 | 100 | ℃ | %Z034105 | AI |  | 70CRB02 | [5 empty] | TBG05 | 13 | 14 | 15 |  | 70LAB10GH002 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B仪表接线箱 | Electrical feedwater pump B instrument junction box
|  | 70LAB10CT112 | 电动给水泵B传动端机封冲洗水温度 | Electrical feedwater pump B motor drive end machine seal flushing water Temp. | 70CRB02 | FCS0705 | 3 | 4 | 6 | AAR181-S | PT100 | N | %Z034106 | [5 empty] | 0 | 200 | ℃ | %Z034106 | AI |  | 70CRB02 | [5 empty] | TBG05 | 16 | 17 | 18 |  | 70LAB10GH002 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B仪表接线箱 | Electrical feedwater pump B instrument junction box
|  | 70LAB10CT122 | 电动给水泵B液力耦合器2#轴瓦温度 | Electrical feedwater pump Bcoupler 2# bearing temperature | 70CRB02 | FCS0705 | 3 | 4 | 7 | AAR181-S | PT100 | N | %Z034107 | [5 empty] | 0 | 200 | ℃ | %Z034107 | AI |  | 70CRB02 | [5 empty] | TBG05 | 19 | 20 | 21 |  | 70LAB10CT122 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10CT124 | 电动给水泵B液力耦合器4#轴瓦温度 | Electrical feedwater pump Bcoupler 4# bearing temperature | 70CRB02 | FCS0705 | 3 | 4 | 8 | AAR181-S | PT100 | N | %Z034108 | [5 empty] | 0 | 200 | ℃ | %Z034108 | AI |  | 70CRB02 | [5 empty] | TBG05 | 22 | 23 | 24 |  | 70LAB10CT124 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10CT126 | 电动给水泵B液力耦合器6#轴瓦温度 | Electrical feedwater pump Bcoupler 6# bearing temperature | 70CRB02 | FCS0705 | 3 | 4 | 9 | AAR181-S | PT100 | N | %Z034109 | [5 empty] | 0 | 200 | ℃ | %Z034109 | AI |  | 70CRB02 | [5 empty] | TBG05 | 25 | 26 | 27 |  | 70LAB10CT126 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10CT128 | 电动给水泵B液力耦合器工作油进油温度 | Electrical feedwater pump Bcoupler work oil inlet temperature | 70CRB02 | FCS0705 | 3 | 4 | 10 | AAR181-S | PT100 | N | %Z034110 | [5 empty] | 0 | 100 | ℃ | %Z034110 | AI |  | 70CRB02 | [5 empty] | TBG05 | 28 | 29 | 30 |  | 70LAB10CT128 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-007
[5 empty] | 70CRB02 | FCS0705 | 3 | 4 | 11 | AAR181-S | PT100 | N | %Z034111 | [8 empty] | %Z034111 | AI |  | 70CRB02 | [5 empty] | TBG05 | 31 | 32 | 33
[5 empty] | 70CRB02 | FCS0705 | 3 | 4 | 12 | AAR181-S | PT100 | N | %Z034112 | [8 empty] | %Z034112 | AI |  | 70CRB02 | [5 empty] | TBG05 | 34 | 35 | 36
|  | 70LCB10CT101 | 凝结水泵A推力轴承金属温度1 | Condensate pump A radial bearing metal temperature 1 | 70CRB02 | FCS0705 | 4 | 3 | 1 | AAR181-S | PT100 | N | %Z043101 | [5 empty] | 0 | 100 | ℃ | %Z043101 | AI |  | 70CRB02 | [5 empty] | TBG06 | 1 | 2 | 3 |  | 70LCB10CT101 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10CT111 | 凝结水泵B推力轴承金属温度1 | Condensate pump B radial bearing metal temperature 1 | 70CRB02 | FCS0705 | 4 | 3 | 2 | AAR181-S | PT100 | N | %Z043102 | [5 empty] | 0 | 100 | ℃ | %Z043102 | AI |  | 70CRB02 | [5 empty] | TBG06 | 4 | 5 | 6 |  | 70LCB10CT111 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10CT121 | 凝结水泵C推力轴承金属温度1 | Condensate pump C radial bearing metal temperature 1 | 70CRB02 | FCS0705 | 4 | 3 | 3 | AAR181-S | PT100 | N | %Z043103 | [5 empty] | 0 | 100 | ℃ | %Z043103 | AI |  | 70CRB02 | [5 empty] | TBG06 | 7 | 8 | 9 |  | 70LCB10CT121 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-008
|  | 70MAG12CT101 | 真空泵A电机轴承温度1 | Vacuum pump A motor bearing temperature 1 | 70CRB02 | FCS0705 | 4 | 3 | 4 | AAR181-S | PT100 | N | %Z043104 | [5 empty] | 0 | 200 | ℃ | %Z043104 | AI |  | 70CRB02 | [5 empty] | TBG06 | 10 | 11 | 12 |  | 70MAG12GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-003 | 真空泵A电机接线盒 | Vacuum pump A motor JB
|  | 70MAG12CT103 | 真空泵A电机绕组温度1 | Vacuum pump A motor stator coil temperature 1 | 70CRB02 | FCS0705 | 4 | 3 | 5 | AAR181-S | PT100 | N | %Z043105 | [5 empty] | 0 | 200 | ℃ | %Z043105 | AI |  | 70CRB02 | [5 empty] | TBG06 | 13 | 14 | 15 |  | 70MAG12GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-003 | 真空泵A电机接线盒 | Vacuum pump A motor JB
|  | 70MAG11CT101 | 真空泵B电机轴承温度1 | Vacuum pump B motor bearing temperature 1 | 70CRB02 | FCS0705 | 4 | 3 | 6 | AAR181-S | PT100 | N | %Z043106 | [5 empty] | 0 | 200 | ℃ | %Z043106 | AI |  | 70CRB02 | [5 empty] | TBG06 | 16 | 17 | 18 |  | 70MAG11GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-003 | 真空泵B电机接线盒 | Vacuum pump B motor JB
|  | 70MAG11CT103 | 真空泵B电机绕组温度1 | Vacuum pump B motor stator coil temperature 1 | 70CRB02 | FCS0705 | 4 | 3 | 7 | AAR181-S | PT100 | N | %Z043107 | [5 empty] | 0 | 200 | ℃ | %Z043107 | AI |  | 70CRB02 | [5 empty] | TBG06 | 19 | 20 | 21 |  | 70MAG11GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-003 | 真空泵B电机接线盒 | Vacuum pump B motor JB
|  | 70MAG12CT105 | 真空泵A电机绕组温度3 | Vacuum pump A motor stator coil temperature 3 | 70CRB02 | FCS0705 | 4 | 3 | 8 | AAR181-S | PT100 | N | %Z043108 | [5 empty] | 0 | 200 | ℃ | %Z043108 | AI |  | 70CRB02 | [5 empty] | TBG06 | 22 | 23 | 24 |  | 70MAG12GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-003 | 真空泵A电机接线盒 | Vacuum pump A motor JB
[5 empty] | 70CRB02 | FCS0705 | 4 | 3 | 9 | AAR181-S | PT100 | N | %Z043109 | [8 empty] | %Z043109 | AI |  | 70CRB02 | [5 empty] | TBG06 | 25 | 26 | 27
[5 empty] | 70CRB02 | FCS0705 | 4 | 3 | 10 | AAR181-S | PT100 | N | %Z043110 | [8 empty] | %Z043110 | AI |  | 70CRB02 | [5 empty] | TBG06 | 28 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 4 | 3 | 11 | AAR181-S | PT100 | N | %Z043111 | [8 empty] | %Z043111 | AI |  | 70CRB02 | [5 empty] | TBG06 | 31 | 32 | 33
[5 empty] | 70CRB02 | FCS0705 | 4 | 3 | 12 | AAR181-S | PT100 | N | %Z043112 | [8 empty] | %Z043112 | AI |  | 70CRB02 | [5 empty] | TBG06 | 34 | 35 | 36
|  | 70LCB10CT102 | 凝结水泵A推力轴承金属温度2 | Condensate pump A radial bearing metal temperature 2 | 70CRB02 | FCS0705 | 4 | 4 | 1 | AAR181-S | PT100 | N | %Z044101 | [5 empty] | 0 | 100 | ℃ | %Z044101 | AI |  | 70CRB02 | [5 empty] | TBG07 | 1 | 2 | 3 |  | 70LCB10CT102 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10CT112 | 凝结水泵B推力轴承金属温度2 | Condensate pump B radial bearing metal temperature 2 | 70CRB02 | FCS0705 | 4 | 4 | 2 | AAR181-S | PT100 | N | %Z044102 | [5 empty] | 0 | 100 | ℃ | %Z044102 | AI |  | 70CRB02 | [5 empty] | TBG07 | 4 | 5 | 6 |  | 70LCB10CT112 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10CT122 | 凝结水泵C推力轴承金属温度2 | Condensate pump C radial bearing metal temperature 2 | 70CRB02 | FCS0705 | 4 | 4 | 3 | AAR181-S | PT100 | N | %Z044103 | [5 empty] | 0 | 100 | ℃ | %Z044103 | AI |  | 70CRB02 | [5 empty] | TBG07 | 7 | 8 | 9 |  | 70LCB10CT122 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-008
|  | 70MAG12CT102 | 真空泵A电机轴承温度2 | Vacuum pump A motor bearing temperature 2 | 70CRB02 | FCS0705 | 4 | 4 | 4 | AAR181-S | PT100 | N | %Z044104 | [5 empty] | 0 | 200 | ℃ | %Z044104 | AI |  | 70CRB02 | [5 empty] | TBG07 | 10 | 11 | 12 |  | 70MAG12GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-003 | 真空泵A电机接线盒 | Vacuum pump A motor JB
|  | 70MAG12CT104 | 真空泵A电机绕组温度2 | Vacuum pump A motor stator coil temperature 2 | 70CRB02 | FCS0705 | 4 | 4 | 5 | AAR181-S | PT100 | N | %Z044105 | [5 empty] | 0 | 200 | ℃ | %Z044105 | AI |  | 70CRB02 | [5 empty] | TBG07 | 13 | 14 | 15 |  | 70MAG12GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-003 | 真空泵A电机接线盒 | Vacuum pump A motor JB
|  | 70MAG11CT102 | 真空泵B电机轴承温度2 | Vacuum pump B motor bearing temperature 2 | 70CRB02 | FCS0705 | 4 | 4 | 6 | AAR181-S | PT100 | N | %Z044106 | [5 empty] | 0 | 200 | ℃ | %Z044106 | AI |  | 70CRB02 | [5 empty] | TBG07 | 16 | 17 | 18 |  | 70MAG11GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-003 | 真空泵B电机接线盒 | Vacuum pump B motor JB
|  | 70MAG11CT104 | 真空泵B电机绕组温度2 | Vacuum pump B motor stator coil temperature 2 | 70CRB02 | FCS0705 | 4 | 4 | 7 | AAR181-S | PT100 | N | %Z044107 | [5 empty] | 0 | 200 | ℃ | %Z044107 | AI |  | 70CRB02 | [5 empty] | TBG07 | 19 | 20 | 21 |  | 70MAG11GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-003 | 真空泵B电机接线盒 | Vacuum pump B motor JB
|  | 70MAG11CT105 | 真空泵B电机绕组温度3 | Vacuum pump B motor stator coil temperature 3 | 70CRB02 | FCS0705 | 4 | 4 | 8 | AAR181-S | PT100 | N | %Z044108 | [5 empty] | 0 | 200 | ℃ | %Z044108 | AI |  | 70CRB02 | [5 empty] | TBG07 | 22 | 23 | 24 |  | 70MAG11GH001 | PT100 | RTD | [8 empty] | SCS | D |  | K0204-003 | 真空泵B电机接线盒 | Vacuum pump B motor JB
[5 empty] | 70CRB02 | FCS0705 | 4 | 4 | 9 | AAR181-S | PT100 | N | %Z044109 | [8 empty] | %Z044109 | AI |  | 70CRB02 | [5 empty] | TBG07 | 25 | 26 | 27
[5 empty] | 70CRB02 | FCS0705 | 4 | 4 | 10 | AAR181-S | PT100 | N | %Z044110 | [8 empty] | %Z044110 | AI |  | 70CRB02 | [5 empty] | TBG07 | 28 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 4 | 4 | 11 | AAR181-S | PT100 | N | %Z044111 | [8 empty] | %Z044111 | AI |  | 70CRB02 | [5 empty] | TBG07 | 31 | 32 | 33
[5 empty] | 70CRB02 | FCS0705 | 4 | 4 | 12 | AAR181-S | PT100 | N | %Z044112 | [8 empty] | %Z044112 | AI |  | 70CRB02 | [5 empty] | TBG07 | 34 | 35 | 36
|  | 70LAB20AA121YQ01 | 电动给水泵A液力耦合器电动调节阀控制指令 | Electrical feedwater pump A coupler regulating MOV position command | 70CRB02 | FCS0705 | 1 | 2 | 1 | AAI543-H | 4~20mA | N | %Z012101 | [5 empty] | 0 | 100 | % | %Z012101 | AO |  | 70CRB02 | [5 empty] | TBG01 | 1 | 2 |  |  | 70LAB20AA121 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-007
|  | 70LAB10AA121YQ01 | 电动给水泵B液力耦合器电动调节阀控制指令 | Electrical feedwater pump B coupler regulating MOV position command | 70CRB02 | FCS0705 | 1 | 2 | 2 | AAI543-H | 4~20mA | N | %Z012102 | [5 empty] | 0 | 100 | % | %Z012102 | AO |  | 70CRB02 | [5 empty] | TBG01 | 3 | 4 |  |  | 70LAB10AA121 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-007
|  | 70LCA40AA101YQ01 | 凝结水再循电动调节阀控制指令 | Condensate water recirculation regulating MOV position command | 70CRB02 | FCS0705 | 1 | 2 | 3 | AAI543-H | 4~20mA | N | %Z012103 | [5 empty] | 0 | 100 | % | %Z012103 | AO |  | 70CRB02 | [5 empty] | TBG01 | 5 | 6 |  |  | 70LCA40AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-008
|  | 70LCA30AA101YQ01 | 除氧器入口电动调节阀控制指令 | Deaerator inlet regulating MOV position command | 70CRB02 | FCS0705 | 1 | 2 | 4 | AAI543-H | 4~20mA | N | %Z012104 | [5 empty] | 0 | 100 | % | %Z012104 | AO |  | 70CRB02 | [5 empty] | TBG01 | 7 | 8 |  |  | 70LCA30AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-008
|  | 70GHC50AA101YQ01 | 凝汽器补水电动调节阀控制指令 | Condensate make-up water regulating MOV position command | 70CRB02 | FCS0705 | 1 | 2 | 5 | AAI543-H | 4~20mA | N | %Z012105 | [5 empty] | 0 | 100 | % | %Z012105 | AO |  | 70CRB02 | [5 empty] | TBG01 | 9 | 10 |  |  | 70GHC50AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-015
|  | 70GHC10AA101YQ01 | 除氧器补水电动调节阀控制指令 | Deaerator make-up water regulating MOV position command | 70CRB02 | FCS0705 | 1 | 2 | 6 | AAI543-H | 4~20mA | N | %Z012106 | [5 empty] | 0 | 100 | % | %Z012106 | AO |  | 70CRB02 | [5 empty] | TBG01 | 11 | 12 |  |  | 70GHC10AA101 | 4~20mA | AO | [8 empty] | MCS | D |  | K0204-015
|  | 70QCD11AP001YQ01 | 1#给水氨计量泵频率给定 | 1# feed water ammonia metering pump frequency given | 70CRB02 | FCS0705 | 1 | 2 | 7 | AAI543-H | 4~20mA | N | %Z012107 | [5 empty] | 0 | 100 | Hz | %Z012107 | AO |  | 70CRB02 | [5 empty] | TBG01 | 13 | 14 |  |  | 70QCD10GH001 | 4~20mA | AO | [8 empty] | MCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD12AP001YQ01 | 2#给水氨计量泵频率给定 | 2# feed water ammonia metering pump frequency given | 70CRB02 | FCS0705 | 1 | 2 | 8 | AAI543-H | 4~20mA | N | %Z012108 | [5 empty] | 0 | 100 | Hz | %Z012108 | AO |  | 70CRB02 | [5 empty] | TBG01 | 15 | 16 |  |  | 70QCD10GH001 | 4~20mA | AO | [8 empty] | MCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCA11AP001YQ01 | 1#给水联氨计量泵频率给定 | 1# feed water hydrazine metering pump frequency given | 70CRB02 | FCS0705 | 1 | 2 | 9 | AAI543-H | 4~20mA | N | %Z012109 | [5 empty] | 0 | 100 | Hz | %Z012109 | AO |  | 70CRB02 | [5 empty] | TBG01 | 17 | 18 |  |  | 70QCA10GH001 | 4~20mA | AO | [8 empty] | MCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA12AP001YQ01 | 2#给水联氨计量泵频率给定 | 2# feed water hydrazine metering pump frequency given | 70CRB02 | FCS0705 | 1 | 2 | 10 | AAI543-H | 4~20mA | N | %Z012110 | [5 empty] | 0 | 100 | Hz | %Z012110 | AO |  | 70CRB02 | [5 empty] | TBG01 | 19 | 20 |  |  | 70QCA10GH001 | 4~20mA | AO | [8 empty] | MCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
[5 empty] | 70CRB02 | FCS0705 | 1 | 2 | 11 | AAI543-H | 4~20mA | N | %Z012111 | [8 empty] | %Z012111 | AO |  | 70CRB02 | [5 empty] | TBG01 | 21 | 22
[5 empty] | 70CRB02 | FCS0705 | 1 | 2 | 12 | AAI543-H | 4~20mA | N | %Z012112 | [8 empty] | %Z012112 | AO |  | 70CRB02 | [5 empty] | TBG01 | 23 | 24
[5 empty] | 70CRB02 | FCS0705 | 1 | 2 | 13 | AAI543-H | 4~20mA | N | %Z012113 | [8 empty] | %Z012113 | AO |  | 70CRB02 | [5 empty] | TBG01 | 25 | 26
[5 empty] | 70CRB02 | FCS0705 | 1 | 2 | 14 | AAI543-H | 4~20mA | N | %Z012114 | [8 empty] | %Z012114 | AO |  | 70CRB02 | [5 empty] | TBG01 | 27 | 28
[5 empty] | 70CRB02 | FCS0705 | 1 | 2 | 15 | AAI543-H | 4~20mA | N | %Z012115 | [8 empty] | %Z012115 | AO |  | 70CRB02 | [5 empty] | TBG01 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 1 | 2 | 16 | AAI543-H | 4~20mA | N | %Z012116 | [8 empty] | %Z012116 | AO |  | 70CRB02 | [5 empty] | TBG01 | 31 | 32
|  | 70MAG12AP001XB12 | 真空泵A停止(SOE) | Vacuum pump A stopped(SOE) | 70CRB02 | FCS0705 | 1 | 4 | 1 | ADV151-E | SI | N | %Z014101 | [8 empty] | %Z014101 | DI |  | 70CRB05 | [5 empty] | TBB01 | 1 | 2 |  |  | 70MAG12AP001 | NC | SOE | [8 empty] | SOE | D |  | K0204-003
|  | 70MAG11AP001XB12 | 真空泵B停止(SOE) | Vacuum pump B stopped(SOE) | 70CRB02 | FCS0705 | 1 | 4 | 2 | ADV151-E | SI | N | %Z014102 | [8 empty] | %Z014102 | DI |  | 70CRB05 | [5 empty] | TBB01 | 3 | 4 |  |  | 70MAG11AP001 | NC | SOE | [8 empty] | SOE | D |  | K0204-003
|  | 70LAB20AP001XB12 | 电动给水泵A断路器跳闸信号(SOE) | Electrical feedwater pump A breaker tripping(SOE) | 70CRB02 | FCS0705 | 1 | 4 | 3 | ADV151-E | SI | N | %Z014103 | [8 empty] | %Z014103 | DI |  | 70CRB05 | [5 empty] | TBB01 | 5 | 6 |  |  | 70LAB20AP001 | NO | SOE | [8 empty] | SOE | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB10AP001XB12 | 电动给水泵B断路器跳闸信号(SOE) | Electrical feedwater pump B breaker tripping(SOE) | 70CRB02 | FCS0705 | 1 | 4 | 4 | ADV151-E | SI | N | %Z014104 | [8 empty] | %Z014104 | DI |  | 70CRB05 | [5 empty] | TBB01 | 7 | 8 |  |  | 70LAB10AP001 | NO | SOE | [8 empty] | SOE | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LCB10AP001XB12 | 凝结水泵A停止(SOE) | Condensate pump A stopped (SOE) | 70CRB02 | FCS0705 | 1 | 4 | 5 | ADV151-E | SI | N | %Z014105 | [8 empty] | %Z014105 | DI |  | 70CRB05 | [5 empty] | TBB01 | 9 | 10 |  |  | 70LCB10AP001 | NC | SOE | [8 empty] | SOE | D |  | K0204-008
|  | 70LCB10AP002XB12 | 凝结水泵B停止(SOE) | Condensate pump B stopped (SOE) | 70CRB02 | FCS0705 | 1 | 4 | 6 | ADV151-E | SI | N | %Z014106 | [8 empty] | %Z014106 | DI |  | 70CRB05 | [5 empty] | TBB01 | 11 | 12 |  |  | 70LCB10AP002 | NC | SOE | [8 empty] | SOE | D |  | K0204-008
|  | 70LCB10AP003XB12 | 凝结水泵C停止(SOE) | Condensate pump C stopped (SOE) | 70CRB02 | FCS0705 | 1 | 4 | 7 | ADV151-E | SI | N | %Z014107 | [8 empty] | %Z014107 | DI |  | 70CRB05 | [5 empty] | TBB01 | 13 | 14 |  |  | 70LCB10AP003 | NC | SOE | [8 empty] | SOE | D |  | K0204-008
|  | 70MAV24AP001XB12 | 直流油泵停止(SOE) | DC oil pump stopped(SOE) | 70CRB02 | FCS0705 | 1 | 4 | 8 | ADV151-E | SI | N | %Z014108 | [8 empty] | %Z014108 | DI |  | 70CRB05 | [5 empty] | TBB01 | 15 | 16 |  |  | 70MAV24AP001 | NO | SOE | [7 empty] | √ | SOE | D |  | K0203-005
|  | 70MAV21AP021XB12 | 1#主油泵停止(SOE) | 1# main oil pump stopped(SOE) | 70CRB02 | FCS0705 | 1 | 4 | 9 | ADV151-E | SI | N | %Z014109 | [8 empty] | %Z014109 | DI |  | 70CRB05 | [5 empty] | TBB01 | 17 | 18 |  |  | 70MAV21AP021 | NO | SOE | [7 empty] | √ | SOE | D |  | K0203-005
|  | 70MAV21AP022XB12 | 2#主油泵停止(SOE) | 2# main oil pump stopped(SOE) | 70CRB02 | FCS0705 | 1 | 4 | 10 | ADV151-E | SI | N | %Z014110 | [8 empty] | %Z014110 | DI |  | 70CRB05 | [5 empty] | TBB01 | 19 | 20 |  |  | 70MAV21AP021 | NO | SOE | [7 empty] | √ | SOE | D |  | K0203-005
|  | 70CAA01YB01 | 真空低遮断 | Low acuum interruption | 70CRB02 | FCS0705 | 1 | 4 | 11 | ADV151-E | SI | N | %Z014111 | [8 empty] | %Z014111 | DI |  | 70CRB05 | [5 empty] | TBB01 | 21 | 22 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB02 | 润滑油压低遮断 | Lube oil pressure low trip | 70CRB02 | FCS0705 | 1 | 4 | 12 | ADV151-E | SI | N | %Z014112 | [8 empty] | %Z014112 | DI |  | 70CRB05 | [5 empty] | TBB01 | 23 | 24 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB03 | 机头停机按钮遮断 | Emergency stop of turbine head button trip | 70CRB02 | FCS0705 | 1 | 4 | 13 | ADV151-E | SI | N | %Z014113 | [8 empty] | %Z014113 | DI |  | 70CRB05 | [5 empty] | TBB01 | 25 | 26 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB04 | 操作台紧急停机按钮遮断 | Console emergency trip turbine button trip | 70CRB02 | FCS0705 | 1 | 4 | 14 | ADV151-E | SI | N | %Z014114 | [8 empty] | %Z014114 | DI |  | 70CRB05 | [5 empty] | TBB01 | 27 | 28 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB05 | 电超速遮断 | Electric overspeed trip | 70CRB02 | FCS0705 | 1 | 4 | 15 | ADV151-E | SI | N | %Z014115 | [8 empty] | %Z014115 | DI |  | 70CRB05 | [5 empty] | TBB01 | 29 | 30 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB06 | 排汽温度遮断 | Exhaust temperature trip | 70CRB02 | FCS0705 | 1 | 4 | 16 | ADV151-E | SI | N | %Z014116 | [8 empty] | %Z014116 | DI |  | 70CRB05 | [5 empty] | TBB01 | 31 | 32 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB07 | 相对振动大遮断 | Relative vibration H trip | 70CRB02 | FCS0705 | 1 | 4 | 17 | ADV151-E | SI | N | %Z014117 | [8 empty] | %Z014117 | DI |  | 70CRB05 | [5 empty] | TBB01 | 33 | 34 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB08 | 轴向位移大遮断 | Rotor position H trip | 70CRB02 | FCS0705 | 1 | 4 | 18 | ADV151-E | SI | N | %Z014118 | [8 empty] | %Z014118 | DI |  | 70CRB05 | [5 empty] | TBB01 | 35 | 36 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB09 | 差胀大遮断 | Differential expansion H trip | 70CRB02 | FCS0705 | 1 | 4 | 19 | ADV151-E | SI | N | %Z014119 | [8 empty] | %Z014119 | DI |  | 70CRB05 | [5 empty] | TBB01 | 37 | 38 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB10 | 画面手动遮断 | Manual trip | 70CRB02 | FCS0705 | 1 | 4 | 20 | ADV151-E | SI | N | %Z014120 | [8 empty] | %Z014120 | DI |  | 70CRB05 | [5 empty] | TBB01 | 39 | 40 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB11 | 轴瓦温度遮断 | Bearing temperature H trip | 70CRB02 | FCS0705 | 1 | 4 | 21 | ADV151-E | SI | N | %Z014121 | [8 empty] | %Z014121 | DI |  | 70CRB05 | [5 empty] | TBB01 | 41 | 42 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB12 | 遥控遮断1 | Remote trip 1 | 70CRB02 | FCS0705 | 1 | 4 | 22 | ADV151-E | SI | N | %Z014122 | [8 empty] | %Z014122 | DI |  | 70CRB05 | [5 empty] | TBB01 | 43 | 44 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB13 | 遥控遮断2 | Remote trip 2 | 70CRB02 | FCS0705 | 1 | 4 | 23 | ADV151-E | SI | N | %Z014123 | [8 empty] | %Z014123 | DI |  | 70CRB05 | [5 empty] | TBB01 | 45 | 46 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB14 | 遥控遮断3 | Remote trip 3 | 70CRB02 | FCS0705 | 1 | 4 | 24 | ADV151-E | SI | N | %Z014124 | [8 empty] | %Z014124 | DI |  | 70CRB05 | [5 empty] | TBB01 | 47 | 48 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB15 | 遥控遮断4 | Remote trip 4 | 70CRB02 | FCS0705 | 1 | 4 | 25 | ADV151-E | SI | N | %Z014125 | [8 empty] | %Z014125 | DI |  | 70CRB05 | [5 empty] | TBB01 | 49 | 50 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
|  | 70CAA01YB21 | 停机扩展至SOE | Trip expansion to SOE | 70CRB02 | FCS0705 | 1 | 4 | 26 | ADV151-E | SI | N | %Z014126 | [8 empty] | %Z014126 | DI |  | 70CRB05 | [5 empty] | TBB01 | 51 | 52 |  |  | 70CAA01 | NO | DI | [7 empty] | √ | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
[5 empty] | 70CRB02 | FCS0705 | 1 | 4 | 27 | ADV151-E | SI | N | %Z014127 | [8 empty] | %Z014127 | DI |  | 70CRB05 | [5 empty] | TBB01 | 53 | 54
[5 empty] | 70CRB02 | FCS0705 | 1 | 4 | 28 | ADV151-E | SI | N | %Z014128 | [8 empty] | %Z014128 | DI |  | 70CRB05 | [5 empty] | TBB01 | 55 | 56
[5 empty] | 70CRB02 | FCS0705 | 1 | 4 | 29 | ADV151-E | SI | N | %Z014129 | [8 empty] | %Z014129 | DI |  | 70CRB05 | [5 empty] | TBB01 | 57 | 58
[5 empty] | 70CRB02 | FCS0705 | 1 | 4 | 30 | ADV151-E | SI | N | %Z014130 | [8 empty] | %Z014130 | DI |  | 70CRB05 | [5 empty] | TBB01 | 59 | 60
[5 empty] | 70CRB02 | FCS0705 | 1 | 4 | 31 | ADV151-E | SI | N | %Z014131 | [8 empty] | %Z014131 | DI |  | 70CRB05 | [5 empty] | TBB01 | 61 | 62
[5 empty] | 70CRB02 | FCS0705 | 1 | 4 | 32 | ADV151-E | SI | N | %Z014132 | [8 empty] | %Z014132 | DI |  | 70CRB05 | [5 empty] | TBB01 | 63 | 64
|  | 70QUH10CT001H | 汽包炉水左/右侧取样水温度高 | The left /right side of boiler drum sampling Temp.H | 70CRB02 | FCS0705 | 1 | 3 | 1 | ADV151-P | SI | N | %Z013101 | [7 empty] | ℃ | %Z013101 | DI |  | 70CRB05 | [5 empty] | TBB02 | 1 | 2 |  |  | 70QUH10GH001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUA10CT001H | 饱和蒸汽左/右侧取样水温度高 | The left /right side of saturated steam sampling Temp.H | 70CRB02 | FCS0705 | 1 | 3 | 2 | ADV151-P | SI | N | %Z013102 | [7 empty] | ℃ | %Z013102 | DI |  | 70CRB05 | [5 empty] | TBB02 | 3 | 4 |  |  | 70QUH10GH001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUA30CT001H | 过热蒸汽取样水温度高 | Superheated steam sampling Temp.H | 70CRB02 | FCS0705 | 1 | 3 | 3 | ADV151-P | SI | N | %Z013103 | [7 empty] | ℃ | %Z013103 | DI |  | 70CRB05 | [5 empty] | TBB02 | 5 | 6 |  |  | 70QUH10GH001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUB20CT001H | 省煤器入口给水取样水温度高 | Economizer inlet feedwater sampling Temp.H | 70CRB02 | FCS0705 | 1 | 3 | 4 | ADV151-P | SI | N | %Z013104 | [7 empty] | ℃ | %Z013104 | DI |  | 70CRB05 | [5 empty] | TBB02 | 7 | 8 |  |  | 70QUH10GH001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUC10CT001H | 凝结水泵出口取样水温度高 | Condensate pump outlet water sampling Temp.H | 70CRB02 | FCS0705 | 1 | 3 | 5 | ADV151-P | SI | N | %Z013105 | [7 empty] | ℃ | %Z013105 | DI |  | 70CRB05 | [5 empty] | TBB02 | 9 | 10 |  |  | 70QUH10GH001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUB30CT001H | 除氧器出口给水取样水温度高 | Deaerator outlet feedwater sampling Temp.H | 70CRB02 | FCS0705 | 1 | 3 | 6 | ADV151-P | SI | N | %Z013106 | [7 empty] | ℃ | %Z013106 | DI |  | 70CRB05 | [5 empty] | TBB02 | 11 | 12 |  |  | 70QUH10GH001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUH10CF001L | 除盐水冷却水进水流量低 | Demineralized cooling water inlet water flow L | 70CRB02 | FCS0705 | 1 | 3 | 7 | ADV151-P | SI | N | %Z013107 | [7 empty] | mL/min | %Z013107 | DI |  | 70CRB05 | [5 empty] | TBB02 | 13 | 14 |  |  | 70QUH10GH001 | NC | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUP01AP001XB01 | 恒温箱压缩机运行 | Thermostat compressor running | 70CRB02 | FCS0705 | 1 | 3 | 8 | ADV151-P | SI | N | %Z013108 | [8 empty] | %Z013108 | DI |  | 70CRB05 | [5 empty] | TBB02 | 15 | 16 |  |  | 70QUH10GH001 | NO | DI | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUP01AP001XB31 | 恒温箱压缩机故障 | Thermostat compressor fault | 70CRB02 | FCS0705 | 1 | 3 | 9 | ADV151-P | SI | N | %Z013109 | [8 empty] | %Z013109 | DI |  | 70CRB05 | [5 empty] | TBB02 | 17 | 18 |  |  | 70QUH10GH001 | NO | DI | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUP01AP002XB01 | 恒温箱循环泵运行 | Thermostat cyclic pump running | 70CRB02 | FCS0705 | 1 | 3 | 10 | ADV151-P | SI | N | %Z013110 | [8 empty] | %Z013110 | DI |  | 70CRB05 | [5 empty] | TBB02 | 19 | 20 |  |  | 70QUH10GH001 | NO | DI | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
|  | 70QUP01AP002XB31 | 恒温箱循环泵故障 | Thermostat cyclic pump fault | 70CRB02 | FCS0705 | 1 | 3 | 11 | ADV151-P | SI | N | %Z013111 | [8 empty] | %Z013111 | DI |  | 70CRB05 | [5 empty] | TBB02 | 21 | 22 |  |  | 70QUH10GH001 | NO | DI | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 12 | ADV151-P | SI | N | %Z013112 | [8 empty] | %Z013112 | DI |  | 70CRB05 | [5 empty] | TBB02 | 23 | 24
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 13 | ADV151-P | SI | N | %Z013113 | [8 empty] | %Z013113 | DI |  | 70CRB05 | [5 empty] | TBB02 | 25 | 26
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 14 | ADV151-P | SI | N | %Z013114 | [8 empty] | %Z013114 | DI |  | 70CRB05 | [5 empty] | TBB02 | 27 | 28
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 15 | ADV151-P | SI | N | %Z013115 | [8 empty] | %Z013115 | DI |  | 70CRB05 | [5 empty] | TBB02 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 16 | ADV151-P | SI | N | %Z013116 | [8 empty] | %Z013116 | DI |  | 70CRB05 | [5 empty] | TBB02 | 31 | 32
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 17 | ADV151-P | SI | N | %Z013117 | [8 empty] | %Z013117 | DI |  | 70CRB05 | [5 empty] | TBB02 | 33 | 34
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 18 | ADV151-P | SI | N | %Z013118 | [8 empty] | %Z013118 | DI |  | 70CRB05 | [5 empty] | TBB02 | 35 | 36
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 19 | ADV151-P | SI | N | %Z013119 | [8 empty] | %Z013119 | DI |  | 70CRB05 | [5 empty] | TBB02 | 37 | 38
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 20 | ADV151-P | SI | N | %Z013120 | [8 empty] | %Z013120 | DI |  | 70CRB05 | [5 empty] | TBB02 | 39 | 40
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 21 | ADV151-P | SI | N | %Z013121 | [8 empty] | %Z013121 | DI |  | 70CRB05 | [5 empty] | TBB02 | 41 | 42
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 22 | ADV151-P | SI | N | %Z013122 | [8 empty] | %Z013122 | DI |  | 70CRB05 | [5 empty] | TBB02 | 43 | 44
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 23 | ADV151-P | SI | N | %Z013123 | [8 empty] | %Z013123 | DI |  | 70CRB05 | [5 empty] | TBB02 | 45 | 46
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 24 | ADV151-P | SI | N | %Z013124 | [8 empty] | %Z013124 | DI |  | 70CRB05 | [5 empty] | TBB02 | 47 | 48
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 25 | ADV151-P | SI | N | %Z013125 | [8 empty] | %Z013125 | DI |  | 70CRB05 | [5 empty] | TBB02 | 49 | 50
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 26 | ADV151-P | SI | N | %Z013126 | [8 empty] | %Z013126 | DI |  | 70CRB05 | [5 empty] | TBB02 | 51 | 52
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 27 | ADV151-P | SI | N | %Z013127 | [8 empty] | %Z013127 | DI |  | 70CRB05 | [5 empty] | TBB02 | 53 | 54
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 28 | ADV151-P | SI | N | %Z013128 | [8 empty] | %Z013128 | DI |  | 70CRB05 | [5 empty] | TBB02 | 55 | 56
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 29 | ADV151-P | SI | N | %Z013129 | [8 empty] | %Z013129 | DI |  | 70CRB05 | [5 empty] | TBB02 | 57 | 58
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 30 | ADV151-P | SI | N | %Z013130 | [8 empty] | %Z013130 | DI |  | 70CRB05 | [5 empty] | TBB02 | 59 | 60
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 31 | ADV151-P | SI | N | %Z013131 | [8 empty] | %Z013131 | DI |  | 70CRB05 | [5 empty] | TBB02 | 61 | 62
[5 empty] | 70CRB02 | FCS0705 | 1 | 3 | 32 | ADV151-P | SI | N | %Z013132 | [8 empty] | %Z013132 | DI |  | 70CRB05 | [5 empty] | TBB02 | 63 | 64
|  | 70LAB20AP001XB01 | 电动给水泵A断路器合闸信号 | Electrical feedwater pump A breaker closing | 70CRB02 | FCS0705 | 2 | 6 | 1 | ADV151-P | SI | N | %Z026101 | [8 empty] | %Z026101 | DI |  | 70CRB05 | [5 empty] | TBC01 | 1 | 2 |  |  | 70LAB20AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB20AP001XB11 | 电动给水泵A断路器跳闸信号 | Electrical feedwater pump A breaker tripping | 70CRB02 | FCS0705 | 2 | 6 | 2 | ADV151-P | SI | N | %Z026102 | [8 empty] | %Z026102 | DI |  | 70CRB05 | [5 empty] | TBC01 | 3 | 4 |  |  | 70LAB20AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB20AP001XB21 | 电动给水泵A远控允许 | Electrical feedwater pump A remote operation allowable | 70CRB02 | FCS0705 | 2 | 6 | 3 | ADV151-P | SI | N | %Z026103 | [8 empty] | %Z026103 | DI |  | 70CRB05 | [5 empty] | TBC01 | 5 | 6 |  |  | 70LAB20AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB20AP001XB31 | 电动给水泵A弹簧未储能 | Electrical feedwater pump A spring charge | 70CRB02 | FCS0705 | 2 | 6 | 4 | ADV151-P | SI | N | %Z026104 | [8 empty] | %Z026104 | DI |  | 70CRB05 | [5 empty] | TBC01 | 7 | 8 |  |  | 70LAB20AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB20AP001XB32 | 电动给水泵A装置故障 | Electrical feedwater pump A device fault | 70CRB02 | FCS0705 | 2 | 6 | 5 | ADV151-P | SI | N | %Z026105 | [8 empty] | %Z026105 | DI |  | 70CRB05 | [5 empty] | TBC01 | 9 | 10 |  |  | 70LAB20AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB20AP001XB33 | 电动给水泵A保护动作 | Electrical feedwater pump A trip Output | 70CRB02 | FCS0705 | 2 | 6 | 6 | ADV151-P | SI | N | %Z026106 | [8 empty] | %Z026106 | DI |  | 70CRB05 | [5 empty] | TBC01 | 11 | 12 |  |  | 70LAB20AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB20AP001XB34 | 电动给水泵A控制回路断线 | Electrical feedwater pump A control circuit loss power | 70CRB02 | FCS0705 | 2 | 6 | 7 | ADV151-P | SI | N | %Z026107 | [8 empty] | %Z026107 | DI |  | 70CRB05 | [5 empty] | TBC01 | 13 | 14 |  |  | 70LAB20AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB20CP001H | 电动给水泵A入口滤网差压高 | Electrical feedwater pump A inlet filter DP H | 70CRB02 | FCS0705 | 2 | 6 | 8 | ADV151-P | SI | N | %Z026108 | [7 empty] | KPa | %Z026108 | DI |  | 70CRB05 | [5 empty] | TBC01 | 15 | 16 |  |  | 70LAB20GH002 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0204-006 | 电动给水泵A仪表接线箱 | Electrical feedwater pump A instrument junction box
|  | 70LAB40AA002XB01 | 电动给水泵A出口电动阀全开状态 | Electrical feedwater pump A outlet MOV full opened status | 70CRB02 | FCS0705 | 2 | 6 | 9 | ADV151-P | SI | N | %Z026109 | [8 empty] | %Z026109 | DI |  | 70CRB05 | [5 empty] | TBC01 | 17 | 18 |  |  | 70LAB40AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB40AA002XB11 | 电动给水泵A出口电动阀全关状态 | Electrical feedwater pump A outlet MOV full closed status | 70CRB02 | FCS0705 | 2 | 6 | 10 | ADV151-P | SI | N | %Z026110 | [8 empty] | %Z026110 | DI |  | 70CRB05 | [5 empty] | TBC01 | 19 | 20 |  |  | 70LAB40AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB40AA002XB31 | 电动给水泵A出口电动阀故障 | Electrical feedwater pump A outlet MOV fault | 70CRB02 | FCS0705 | 2 | 6 | 11 | ADV151-P | SI | N | %Z026111 | [8 empty] | %Z026111 | DI |  | 70CRB05 | [5 empty] | TBC01 | 21 | 22 |  |  | 70LAB40AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAH10AA001XB01 | 电动给水泵A给水再循环电动阀全开状态 | Electrical feedwater pump A feedwater recycling MOV full opened status | 70CRB02 | FCS0705 | 2 | 6 | 12 | ADV151-P | SI | N | %Z026112 | [8 empty] | %Z026112 | DI |  | 70CRB05 | [5 empty] | TBC01 | 23 | 24 |  |  | 70LAH10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAH10AA001XB11 | 电动给水泵A给水再循环电动阀全关状态 | Electrical feedwater pump A feedwater recycling MOV full closed status | 70CRB02 | FCS0705 | 2 | 6 | 13 | ADV151-P | SI | N | %Z026113 | [8 empty] | %Z026113 | DI |  | 70CRB05 | [5 empty] | TBC01 | 25 | 26 |  |  | 70LAH10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAH10AA001XB31 | 电动给水泵A给水再循环电动阀故障 | Electrical feedwater pump A feedwater recycling MOV fault | 70CRB02 | FCS0705 | 2 | 6 | 14 | ADV151-P | SI | N | %Z026114 | [8 empty] | %Z026114 | DI |  | 70CRB05 | [5 empty] | TBC01 | 27 | 28 |  |  | 70LAH10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LCA10CP001H | 凝结水泵A入口滤网差压高 | Condensate pump A inlet filter DP H | 70CRB02 | FCS0705 | 2 | 6 | 15 | ADV151-P | SI | N | %Z026115 | [7 empty] | KPa | %Z026115 | DI |  | 70CRB05 | [5 empty] | TBC01 | 29 | 30 |  |  | 70LCA10CP001H | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0204-008
|  | 70LCA20AA001XB01 | 凝结水泵A出口电动阀全开状态 | Condensate pump A outlet MOV full opened status | 70CRB02 | FCS0705 | 2 | 6 | 16 | ADV151-P | SI | N | %Z026116 | [8 empty] | %Z026116 | DI |  | 70CRB05 | [5 empty] | TBC01 | 31 | 32 |  |  | 70LCA20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCA20AA001XB11 | 凝结水泵A出口电动阀全关状态 | Condensate pump A outlet MOV full closed status | 70CRB02 | FCS0705 | 2 | 6 | 17 | ADV151-P | SI | N | %Z026117 | [8 empty] | %Z026117 | DI |  | 70CRB05 | [5 empty] | TBC01 | 33 | 34 |  |  | 70LCA20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCA20AA001XB31 | 凝结水泵A出口电动阀故障 | Condensate pump A outlet MOV fault | 70CRB02 | FCS0705 | 2 | 6 | 18 | ADV151-P | SI | N | %Z026118 | [8 empty] | %Z026118 | DI |  | 70CRB05 | [5 empty] | TBC01 | 35 | 36 |  |  | 70LCA20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LAA20AA001XB01 | 除氧器溢流电动阀全开状态 | Deaerator overflow MOV full opened status | 70CRB02 | FCS0705 | 2 | 6 | 19 | ADV151-P | SI | N | %Z026119 | [8 empty] | %Z026119 | DI |  | 70CRB05 | [5 empty] | TBC01 | 37 | 38 |  |  | 70LAA20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LAA20AA001XB11 | 除氧器溢流电动阀全关状态 | Deaerator overflow MOV full closed status | 70CRB02 | FCS0705 | 2 | 6 | 20 | ADV151-P | SI | N | %Z026120 | [8 empty] | %Z026120 | DI |  | 70CRB05 | [5 empty] | TBC01 | 39 | 40 |  |  | 70LAA20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LAA20AA001XB31 | 除氧器溢流电动阀故障 | Deaerator overflow MOV fault | 70CRB02 | FCS0705 | 2 | 6 | 21 | ADV151-P | SI | N | %Z026121 | [8 empty] | %Z026121 | DI |  | 70CRB05 | [5 empty] | TBC01 | 41 | 42 |  |  | 70LAA20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70QCD11AM001XB01 | 1#氨溶液箱搅拌机运行 | 1# ammonia solution tank agitator running | 70CRB02 | FCS0705 | 2 | 6 | 22 | ADV151-P | SI | N | %Z026122 | [8 empty] | %Z026122 | DI |  | 70CRB05 | [5 empty] | TBC01 | 43 | 44 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD11AM001XB31 | 1#氨溶液箱搅拌机故障 | 1# ammonia solution tank agitator fault | 70CRB02 | FCS0705 | 2 | 6 | 23 | ADV151-P | SI | N | %Z026123 | [8 empty] | %Z026123 | DI |  | 70CRB05 | [5 empty] | TBC01 | 45 | 46 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD11AM001XB21 | 1#氨溶液箱搅拌机远程 | 1# ammonia solution tank agitator remote control | 70CRB02 | FCS0705 | 2 | 6 | 24 | ADV151-P | SI | N | %Z026124 | [8 empty] | %Z026124 | DI |  | 70CRB05 | [5 empty] | TBC01 | 47 | 48 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD11AP001XB01 | 1#给水氨计量泵运行 | 1# feed water ammonia metering pump running | 70CRB02 | FCS0705 | 2 | 6 | 25 | ADV151-P | SI | N | %Z026125 | [8 empty] | %Z026125 | DI |  | 70CRB05 | [5 empty] | TBC01 | 49 | 50 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD11AP001XB31 | 1#给水氨计量泵故障 | 1# feed water ammonia metering pump fault | 70CRB02 | FCS0705 | 2 | 6 | 26 | ADV151-P | SI | N | %Z026126 | [8 empty] | %Z026126 | DI |  | 70CRB05 | [5 empty] | TBC01 | 51 | 52 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD11AP001XB21 | 1#给水氨计量泵远程 | 1# feed water ammonia metering pump remote control | 70CRB02 | FCS0705 | 2 | 6 | 27 | ADV151-P | SI | N | %Z026127 | [8 empty] | %Z026127 | DI |  | 70CRB05 | [5 empty] | TBC01 | 53 | 54 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
[5 empty] | 70CRB02 | FCS0705 | 2 | 6 | 28 | ADV151-P | SI | N | %Z026128 | [8 empty] | %Z026128 | DI |  | 70CRB05 | [5 empty] | TBC01 | 55 | 56
[5 empty] | 70CRB02 | FCS0705 | 2 | 6 | 29 | ADV151-P | SI | N | %Z026129 | [8 empty] | %Z026129 | DI |  | 70CRB05 | [5 empty] | TBC01 | 57 | 58
[5 empty] | 70CRB02 | FCS0705 | 2 | 6 | 30 | ADV151-P | SI | N | %Z026130 | [8 empty] | %Z026130 | DI |  | 70CRB05 | [5 empty] | TBC01 | 59 | 60
[5 empty] | 70CRB02 | FCS0705 | 2 | 6 | 31 | ADV151-P | SI | N | %Z026131 | [8 empty] | %Z026131 | DI |  | 70CRB05 | [5 empty] | TBC01 | 61 | 62
[5 empty] | 70CRB02 | FCS0705 | 2 | 6 | 32 | ADV151-P | SI | N | %Z026132 | [8 empty] | %Z026132 | DI |  | 70CRB05 | [5 empty] | TBC01 | 63 | 64
|  | 70LAB20AP021XB01 | 电动给水泵A液力耦合器直流润滑油泵运行 | Electrical feedwater pump A coupler DC lube oil pump running | 70CRB02 | FCS0705 | 2 | 7 | 1 | ADV151-P | SI | N | %Z027101 | [8 empty] | %Z027101 | DI |  | 70CRB05 | [5 empty] | TBC02 | 1 | 2 |  |  | 70LAB20AP021 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20AP021XB11 | 电动给水泵A液力耦合器直流润滑油泵停止 | Electrical feedwater pump A coupler DC lube oil pump stopped | 70CRB02 | FCS0705 | 2 | 7 | 2 | ADV151-P | SI | N | %Z027102 | [8 empty] | %Z027102 | DI |  | 70CRB05 | [5 empty] | TBC02 | 3 | 4 |  |  | 70LAB20AP021 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20AP021XB21 | 电动给水泵A液力耦合器直流润滑油泵远方控制允许 | Electrical feedwater pump A coupler DC lube oil pump remote control permitted | 70CRB02 | FCS0705 | 2 | 7 | 3 | ADV151-P | SI | N | %Z027103 | [8 empty] | %Z027103 | DI |  | 70CRB05 | [5 empty] | TBC02 | 5 | 6 |  |  | 70LAB20AP021 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20AP021XB31 | 电动给水泵A液力耦合器直流润滑油泵故障 | Electrical feedwater pump A coupler DC lube oil pump fault | 70CRB02 | FCS0705 | 2 | 7 | 4 | ADV151-P | SI | N | %Z027104 | [8 empty] | %Z027104 | DI |  | 70CRB05 | [5 empty] | TBC02 | 7 | 8 |  |  | 70LAB20AP021 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20AP022XB01 | 电动给水泵A液力耦合器交流润滑油泵运行 | Electrical feedwater pump A coupler AC lube oil pump running | 70CRB02 | FCS0705 | 2 | 7 | 5 | ADV151-P | SI | N | %Z027105 | [8 empty] | %Z027105 | DI |  | 70CRB05 | [5 empty] | TBC02 | 9 | 10 |  |  | 70LAB20AP022 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20AP022XB11 | 电动给水泵A液力耦合器交流润滑油泵停止 | Electrical feedwater pump A coupler AC lube oil pump stopped | 70CRB02 | FCS0705 | 2 | 7 | 6 | ADV151-P | SI | N | %Z027106 | [8 empty] | %Z027106 | DI |  | 70CRB05 | [5 empty] | TBC02 | 11 | 12 |  |  | 70LAB20AP022 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20AP022XB21 | 电动给水泵A液力耦合器交流润滑油泵远方控制允许 | Electrical feedwater pump A coupler AC lube oil pump remote control permitted | 70CRB02 | FCS0705 | 2 | 7 | 7 | ADV151-P | SI | N | %Z027107 | [8 empty] | %Z027107 | DI |  | 70CRB05 | [5 empty] | TBC02 | 13 | 14 |  |  | 70LAB20AP022 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20AP022XB31 | 电动给水泵A液力耦合器交流润滑油泵控制电源消失 | Electrical feedwater pump A coupler AC lube oil pump control circuit broken | 70CRB02 | FCS0705 | 2 | 7 | 8 | ADV151-P | SI | N | %Z027108 | [8 empty] | %Z027108 | DI |  | 70CRB05 | [5 empty] | TBC02 | 15 | 16 |  |  | 70LAB20AP022 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB20AP022XB32 | 电动给水泵A液力耦合器交流润滑油泵故障输出 | Electrical feedwater pump A coupler AC lube oil pump fault output | 70CRB02 | FCS0705 | 2 | 7 | 9 | ADV151-P | SI | N | %Z027109 | [8 empty] | %Z027109 | DI |  | 70CRB05 | [5 empty] | TBC02 | 17 | 18 |  |  | 70LAB20AP022 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LCB10AP001XB01 | 凝结水泵A运行 | Condensate pump A running | 70CRB02 | FCS0705 | 2 | 7 | 10 | ADV151-P | SI | N | %Z027110 | [8 empty] | %Z027110 | DI |  | 70CRB05 | [5 empty] | TBC02 | 19 | 20 |  |  | 70LCB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP001XB11 | 凝结水泵A停止 | Condensate pump A stopped | 70CRB02 | FCS0705 | 2 | 7 | 11 | ADV151-P | SI | N | %Z027111 | [8 empty] | %Z027111 | DI |  | 70CRB05 | [5 empty] | TBC02 | 21 | 22 |  |  | 70LCB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP001XB21 | 凝结水泵A远方控制允许 | Condensate pump A remote control permitted | 70CRB02 | FCS0705 | 2 | 7 | 12 | ADV151-P | SI | N | %Z027112 | [8 empty] | %Z027112 | DI |  | 70CRB05 | [5 empty] | TBC02 | 23 | 24 |  |  | 70LCB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP001XB31 | 凝结水泵A装置故障控制电源消失 | Condensate pump A device fault control power loss | 70CRB02 | FCS0705 | 2 | 7 | 13 | ADV151-P | SI | N | %Z027113 | [8 empty] | %Z027113 | DI |  | 70CRB05 | [5 empty] | TBC02 | 25 | 26 |  |  | 70LCB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP001XB32 | 凝结水泵A保护动作 | Condensate pump A protection movement | 70CRB02 | FCS0705 | 2 | 7 | 14 | ADV151-P | SI | N | %Z027114 | [8 empty] | %Z027114 | DI |  | 70CRB05 | [5 empty] | TBC02 | 27 | 28 |  |  | 70LCB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70QCA11AM001XB01 | 1#联氨溶液箱搅拌机运行 | 1# hydrazine solution tank agitator running | 70CRB02 | FCS0705 | 2 | 7 | 15 | ADV151-P | SI | N | %Z027115 | [8 empty] | %Z027115 | DI |  | 70CRB05 | [5 empty] | TBC02 | 29 | 30 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA11AM001XB31 | 1#联氨溶液箱搅拌机故障 | 1# hydrazine solution tank agitator fault | 70CRB02 | FCS0705 | 2 | 7 | 16 | ADV151-P | SI | N | %Z027116 | [8 empty] | %Z027116 | DI |  | 70CRB05 | [5 empty] | TBC02 | 31 | 32 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA11AM001XB21 | 1#联氨溶液箱搅拌机远程 | 1# hydrazine solution tank agitator remote control | 70CRB02 | FCS0705 | 2 | 7 | 17 | ADV151-P | SI | N | %Z027117 | [8 empty] | %Z027117 | DI |  | 70CRB05 | [5 empty] | TBC02 | 33 | 34 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA11AP001XB01 | 1#给水联氨计量泵运行 | 1# feed water hydrazine metering pump running | 70CRB02 | FCS0705 | 2 | 7 | 18 | ADV151-P | SI | N | %Z027118 | [8 empty] | %Z027118 | DI |  | 70CRB05 | [5 empty] | TBC02 | 35 | 36 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA11AP001XB31 | 1#给水联氨计量泵故障 | 1# feed water hydrazine metering pump fault | 70CRB02 | FCS0705 | 2 | 7 | 19 | ADV151-P | SI | N | %Z027119 | [8 empty] | %Z027119 | DI |  | 70CRB05 | [5 empty] | TBC02 | 37 | 38 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA11AP001XB21 | 1#给水联氨计量泵远程 | 1# feed water hydrazine metering pump remote control | 70CRB02 | FCS0705 | 2 | 7 | 20 | ADV151-P | SI | N | %Z027120 | [8 empty] | %Z027120 | DI |  | 70CRB05 | [5 empty] | TBC02 | 39 | 40 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCC11AM001XB01 | 1#磷酸盐溶液箱搅拌机运行 | 1# phosphate solution tank agitator running | 70CRB02 | FCS0705 | 2 | 7 | 21 | ADV151-P | SI | N | %Z027121 | [8 empty] | %Z027121 | DI |  | 70CRB05 | [5 empty] | TBC02 | 41 | 42 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC11AM001XB31 | 1#磷酸盐溶液箱搅拌机故障 | 1# phosphate solution tank agitator fault | 70CRB02 | FCS0705 | 2 | 7 | 22 | ADV151-P | SI | N | %Z027122 | [8 empty] | %Z027122 | DI |  | 70CRB05 | [5 empty] | TBC02 | 43 | 44 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC11AM001XB21 | 1#磷酸盐溶液箱搅拌机远程 | 1# phosphate solution tank agitator remote control | 70CRB02 | FCS0705 | 2 | 7 | 23 | ADV151-P | SI | N | %Z027123 | [8 empty] | %Z027123 | DI |  | 70CRB05 | [5 empty] | TBC02 | 45 | 46 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC11AP001XB01 | 1#磷酸盐计量泵运行 | 1# phosphate metering pump running | 70CRB02 | FCS0705 | 2 | 7 | 24 | ADV151-P | SI | N | %Z027124 | [8 empty] | %Z027124 | DI |  | 70CRB05 | [5 empty] | TBC02 | 47 | 48 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC11AP001XB31 | 1#磷酸盐计量泵故障 | 1# phosphate metering pump fault | 70CRB02 | FCS0705 | 2 | 7 | 25 | ADV151-P | SI | N | %Z027125 | [8 empty] | %Z027125 | DI |  | 70CRB05 | [5 empty] | TBC02 | 49 | 50 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC11AP001XB21 | 1#磷酸盐计量泵远程 | 1# phosphate metering pump remote control | 70CRB02 | FCS0705 | 2 | 7 | 26 | ADV151-P | SI | N | %Z027126 | [8 empty] | %Z027126 | DI |  | 70CRB05 | [5 empty] | TBC02 | 51 | 52 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
[5 empty] | 70CRB02 | FCS0705 | 2 | 7 | 27 | ADV151-P | SI | N | %Z027127 | [8 empty] | %Z027127 | DI |  | 70CRB05 | [5 empty] | TBC02 | 53 | 54
[5 empty] | 70CRB02 | FCS0705 | 2 | 7 | 28 | ADV151-P | SI | N | %Z027128 | [8 empty] | %Z027128 | DI |  | 70CRB05 | [5 empty] | TBC02 | 55 | 56
[5 empty] | 70CRB02 | FCS0705 | 2 | 7 | 29 | ADV151-P | SI | N | %Z027129 | [8 empty] | %Z027129 | DI |  | 70CRB05 | [5 empty] | TBC02 | 57 | 58
[5 empty] | 70CRB02 | FCS0705 | 2 | 7 | 30 | ADV151-P | SI | N | %Z027130 | [8 empty] | %Z027130 | DI |  | 70CRB05 | [5 empty] | TBC02 | 59 | 60
[5 empty] | 70CRB02 | FCS0705 | 2 | 7 | 31 | ADV151-P | SI | N | %Z027131 | [8 empty] | %Z027131 | DI |  | 70CRB05 | [5 empty] | TBC02 | 61 | 62
[5 empty] | 70CRB02 | FCS0705 | 2 | 7 | 32 | ADV151-P | SI | N | %Z027132 | [8 empty] | %Z027132 | DI |  | 70CRB05 | [5 empty] | TBC02 | 63 | 64
|  | 70LAB10AP001XB01 | 电动给水泵B断路器合闸信号 | Electrical feedwater pump B breaker closing | 70CRB02 | FCS0705 | 3 | 6 | 1 | ADV151-P | SI | N | %Z036101 | [8 empty] | %Z036101 | DI |  | 70CRB05 | [5 empty] | TBF01 | 1 | 2 |  |  | 70LAB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LAB10AP001XB11 | 电动给水泵B断路器跳闸信号 | Electrical feedwater pump B breaker tripping | 70CRB02 | FCS0705 | 3 | 6 | 2 | ADV151-P | SI | N | %Z036102 | [8 empty] | %Z036102 | DI |  | 70CRB05 | [5 empty] | TBF01 | 3 | 4 |  |  | 70LAB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LAB10AP001XB21 | 电动给水泵B远控允许 | Electrical feedwater pump B remote operation allowable | 70CRB02 | FCS0705 | 3 | 6 | 3 | ADV151-P | SI | N | %Z036103 | [8 empty] | %Z036103 | DI |  | 70CRB05 | [5 empty] | TBF01 | 5 | 6 |  |  | 70LAB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LAB10AP001XB31 | 电动给水泵B弹簧未储能 | Electrical feedwater pump B spring charge | 70CRB02 | FCS0705 | 3 | 6 | 4 | ADV151-P | SI | N | %Z036104 | [8 empty] | %Z036104 | DI |  | 70CRB05 | [5 empty] | TBF01 | 7 | 8 |  |  | 70LAB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LAB10AP001XB32 | 电动给水泵B装置故障 | Electrical feedwater pump B device fault | 70CRB02 | FCS0705 | 3 | 6 | 5 | ADV151-P | SI | N | %Z036105 | [8 empty] | %Z036105 | DI |  | 70CRB05 | [5 empty] | TBF01 | 9 | 10 |  |  | 70LAB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LAB10AP001XB33 | 电动给水泵B保护动作 | Electrical feedwater pump B trip Output | 70CRB02 | FCS0705 | 3 | 6 | 6 | ADV151-P | SI | N | %Z036106 | [8 empty] | %Z036106 | DI |  | 70CRB05 | [5 empty] | TBF01 | 11 | 12 |  |  | 70LAB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LAB10AP001XB34 | 电动给水泵B控制回路断线 | Electrical feedwater pump B control circuit loss power | 70CRB02 | FCS0705 | 3 | 6 | 7 | ADV151-P | SI | N | %Z036107 | [8 empty] | %Z036107 | DI |  | 70CRB05 | [5 empty] | TBF01 | 13 | 14 |  |  | 70LAB10AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LAB10CP001H | 电动给水泵B入口滤网差压高 | Electrical feedwater pump B inlet filter DP H | 70CRB02 | FCS0705 | 3 | 6 | 8 | ADV151-P | SI | N | %Z036108 | [7 empty] | KPa | %Z036108 | DI |  | 70CRB05 | [5 empty] | TBF01 | 15 | 16 |  |  | 70LAB10GH002 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0204-006 | 电动给水泵B仪表接线箱 | Electrical feedwater pump B instrument junction box
|  | 70LAB30AA002XB01 | 电动给水泵B出口电动阀全开状态 | Electrical feedwater pump B outlet MOV full opened status | 70CRB02 | FCS0705 | 3 | 6 | 9 | ADV151-P | SI | N | %Z036109 | [8 empty] | %Z036109 | DI |  | 70CRB05 | [5 empty] | TBF01 | 17 | 18 |  |  | 70LAB30AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB30AA002XB11 | 电动给水泵B出口电动阀全关状态 | Electrical feedwater pump B outlet MOV full closed status | 70CRB02 | FCS0705 | 3 | 6 | 10 | ADV151-P | SI | N | %Z036110 | [8 empty] | %Z036110 | DI |  | 70CRB05 | [5 empty] | TBF01 | 19 | 20 |  |  | 70LAB30AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAB30AA002XB31 | 电动给水泵B出口电动阀故障 | Electrical feedwater pump B outlet MOV fault | 70CRB02 | FCS0705 | 3 | 6 | 11 | ADV151-P | SI | N | %Z036111 | [8 empty] | %Z036111 | DI |  | 70CRB05 | [5 empty] | TBF01 | 21 | 22 |  |  | 70LAB30AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAH20AA001XB01 | 电动给水泵B给水再循环电动阀全开状态 | Electrical feedwater pump B feedwater recycling MOV full opened status | 70CRB02 | FCS0705 | 3 | 6 | 12 | ADV151-P | SI | N | %Z036112 | [8 empty] | %Z036112 | DI |  | 70CRB05 | [5 empty] | TBF01 | 23 | 24 |  |  | 70LAH20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAH20AA001XB11 | 电动给水泵B给水再循环电动阀全关状态 | Electrical feedwater pump B feedwater recycling MOV full closed status | 70CRB02 | FCS0705 | 3 | 6 | 13 | ADV151-P | SI | N | %Z036113 | [8 empty] | %Z036113 | DI |  | 70CRB05 | [5 empty] | TBF01 | 25 | 26 |  |  | 70LAH20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LAH20AA001XB31 | 电动给水泵B给水再循环电动阀故障 | Electrical feedwater pump B feedwater recycling MOV fault | 70CRB02 | FCS0705 | 3 | 6 | 14 | ADV151-P | SI | N | %Z036114 | [8 empty] | %Z036114 | DI |  | 70CRB05 | [5 empty] | TBF01 | 27 | 28 |  |  | 70LAH20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-006
|  | 70LCA10CP002H | 凝结水泵B入口滤网差压高 | Condensate pump B inlet filter DP H | 70CRB02 | FCS0705 | 3 | 6 | 15 | ADV151-P | SI | N | %Z036115 | [7 empty] | KPa | %Z036115 | DI |  | 70CRB05 | [5 empty] | TBF01 | 29 | 30 |  |  | 70LCA10CP002H | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0204-008
|  | 70LCA20AA002XB01 | 凝结水泵B出口电动阀全开状态 | Condensate pump B outlet MOV full opened status | 70CRB02 | FCS0705 | 3 | 6 | 16 | ADV151-P | SI | N | %Z036116 | [8 empty] | %Z036116 | DI |  | 70CRB05 | [5 empty] | TBF01 | 31 | 32 |  |  | 70LCA20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCA20AA002XB11 | 凝结水泵B出口电动阀全关状态 | Condensate pump B outlet MOV full closed status | 70CRB02 | FCS0705 | 3 | 6 | 17 | ADV151-P | SI | N | %Z036117 | [8 empty] | %Z036117 | DI |  | 70CRB05 | [5 empty] | TBF01 | 33 | 34 |  |  | 70LCA20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCA20AA002XB31 | 凝结水泵B出口电动阀故障 | Condensate pump B outlet MOV fault | 70CRB02 | FCS0705 | 3 | 6 | 18 | ADV151-P | SI | N | %Z036118 | [8 empty] | %Z036118 | DI |  | 70CRB05 | [5 empty] | TBF01 | 35 | 36 |  |  | 70LCA20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70PAB20AA001XB01 | A侧凝汽器循环水进水电动阀全开状态 | Inlet water MOV of condenser by side A full opened status | 70CRB02 | FCS0705 | 3 | 6 | 19 | ADV151-P | SI | N | %Z036119 | [8 empty] | %Z036119 | DI |  | 70CRB05 | [5 empty] | TBF01 | 37 | 38 |  |  | 70PAB20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PAB20AA001XB11 | A侧凝汽器循环水进水电动阀全关状态 | Inlet water MOV of condenser by side A full closed status | 70CRB02 | FCS0705 | 3 | 6 | 20 | ADV151-P | SI | N | %Z036120 | [8 empty] | %Z036120 | DI |  | 70CRB05 | [5 empty] | TBF01 | 39 | 40 |  |  | 70PAB20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PAB20AA001XB31 | A侧凝汽器循环水进水电动阀故障 | Inlet water MOV of condenser by side A fault | 70CRB02 | FCS0705 | 3 | 6 | 21 | ADV151-P | SI | N | %Z036121 | [8 empty] | %Z036121 | DI |  | 70CRB05 | [5 empty] | TBF01 | 41 | 42 |  |  | 70PAB20AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PAB40AA001XB01 | A侧凝汽器循环水出水电动阀全开状态 | Outlet water MOV of condenser by side A full opened status | 70CRB02 | FCS0705 | 3 | 6 | 22 | ADV151-P | SI | N | %Z036122 | [8 empty] | %Z036122 | DI |  | 70CRB05 | [5 empty] | TBF01 | 43 | 44 |  |  | 70PAB40AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PAB40AA001XB11 | A侧凝汽器循环水出水电动阀全关状态 | Outlet water MOV of condenser by side A full closed status | 70CRB02 | FCS0705 | 3 | 6 | 23 | ADV151-P | SI | N | %Z036123 | [8 empty] | %Z036123 | DI |  | 70CRB05 | [5 empty] | TBF01 | 45 | 46 |  |  | 70PAB40AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PAB40AA001XB31 | A侧凝汽器循环水出水电动阀故障 | Outlet water MOV of condenser by side A fault | 70CRB02 | FCS0705 | 3 | 6 | 24 | ADV151-P | SI | N | %Z036124 | [8 empty] | %Z036124 | DI |  | 70CRB05 | [5 empty] | TBF01 | 47 | 48 |  |  | 70PAB40AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70MAG12CP001 | 真空泵A入口气动阀前压力低 | Pressure L before vacuum pump A inlet PV | 70CRB02 | FCS0705 | 3 | 6 | 25 | ADV151-P | SI | N | %Z036125 | [7 empty] | Kpa | %Z036125 | DI |  | 70CRB05 | [5 empty] | TBF01 | 49 | 50 |  |  | 70MAG12GH002 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
|  | 70MAG12CP002 | 真空泵A入口气动阀后压力 | Pressure after vacuum pump A inlet PV | 70CRB02 | FCS0705 | 3 | 6 | 26 | ADV151-P | SI | N | %Z036126 | [7 empty] | Kpa | %Z036126 | DI |  | 70CRB05 | [5 empty] | TBF01 | 51 | 52 |  |  | 70MAG12GH002 | NO | DI | [8 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
|  | 70MAG12CL101H | 真空泵A分离罐液位高 | Vacuum pump A separator level H | 70CRB02 | FCS0705 | 3 | 6 | 27 | ADV151-P | SI | N | %Z036127 | [7 empty] | mm | %Z036127 | DI |  | 70CRB05 | [5 empty] | TBF01 | 53 | 54 |  |  | 70MAG12GH002 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
|  | 70MAG12CL101L | 真空泵A分离罐液位低 | Vacuum pump A separator level L | 70CRB02 | FCS0705 | 3 | 6 | 28 | ADV151-P | SI | N | %Z036128 | [7 empty] | mm | %Z036128 | DI |  | 70CRB05 | [5 empty] | TBF01 | 55 | 56 |  |  | 70MAG12GH002 | NC | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
[5 empty] | 70CRB02 | FCS0705 | 3 | 6 | 29 | ADV151-P | SI | N | %Z036129 | [8 empty] | %Z036129 | DI |  | 70CRB05 | [5 empty] | TBF01 | 57 | 58
[5 empty] | 70CRB02 | FCS0705 | 3 | 6 | 30 | ADV151-P | SI | N | %Z036130 | [8 empty] | %Z036130 | DI |  | 70CRB05 | [5 empty] | TBF01 | 59 | 60
[5 empty] | 70CRB02 | FCS0705 | 3 | 6 | 31 | ADV151-P | SI | N | %Z036131 | [8 empty] | %Z036131 | DI |  | 70CRB05 | [5 empty] | TBF01 | 61 | 62
[5 empty] | 70CRB02 | FCS0705 | 3 | 6 | 32 | ADV151-P | SI | N | %Z036132 | [8 empty] | %Z036132 | DI |  | 70CRB05 | [5 empty] | TBF01 | 63 | 64
|  | 70LAB10AP021XB01 | 电动给水泵B液力耦合器直流润滑油泵运行 | Electrical feedwater pump Bcoupler DC lube oil pump running | 70CRB02 | FCS0705 | 3 | 7 | 1 | ADV151-P | SI | N | %Z037101 | [8 empty] | %Z037101 | DI |  | 70CRB05 | [5 empty] | TBF02 | 1 | 2 |  |  | 70LAB10AP021 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10AP021XB11 | 电动给水泵B液力耦合器直流润滑油泵停止 | Electrical feedwater pump Bcoupler DC lube oil pump stopped | 70CRB02 | FCS0705 | 3 | 7 | 2 | ADV151-P | SI | N | %Z037102 | [8 empty] | %Z037102 | DI |  | 70CRB05 | [5 empty] | TBF02 | 3 | 4 |  |  | 70LAB10AP021 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10AP021XB21 | 电动给水泵B液力耦合器直流润滑油泵远方控制允许 | Electrical feedwater pump Bcoupler DC lube oil pump remote control permitted | 70CRB02 | FCS0705 | 3 | 7 | 3 | ADV151-P | SI | N | %Z037103 | [8 empty] | %Z037103 | DI |  | 70CRB05 | [5 empty] | TBF02 | 5 | 6 |  |  | 70LAB10AP021 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10AP021XB31 | 电动给水泵B液力耦合器直流润滑油泵故障 | Electrical feedwater pump Bcoupler DC lube oil pump fault | 70CRB02 | FCS0705 | 3 | 7 | 4 | ADV151-P | SI | N | %Z037104 | [8 empty] | %Z037104 | DI |  | 70CRB05 | [5 empty] | TBF02 | 7 | 8 |  |  | 70LAB10AP021 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10AP022XB01 | 电动给水泵B液力耦合器交流润滑油泵运行 | Electrical feedwater pump Bcoupler AC lube oil pump running | 70CRB02 | FCS0705 | 3 | 7 | 5 | ADV151-P | SI | N | %Z037105 | [8 empty] | %Z037105 | DI |  | 70CRB05 | [5 empty] | TBF02 | 9 | 10 |  |  | 70LAB10AP022 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10AP022XB11 | 电动给水泵B液力耦合器交流润滑油泵停止 | Electrical feedwater pump Bcoupler AC lube oil pump stopped | 70CRB02 | FCS0705 | 3 | 7 | 6 | ADV151-P | SI | N | %Z037106 | [8 empty] | %Z037106 | DI |  | 70CRB05 | [5 empty] | TBF02 | 11 | 12 |  |  | 70LAB10AP022 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10AP022XB21 | 电动给水泵B液力耦合器交流润滑油泵远方控制允许 | Electrical feedwater pump Bcoupler AC lube oil pump remote control permitted | 70CRB02 | FCS0705 | 3 | 7 | 7 | ADV151-P | SI | N | %Z037107 | [8 empty] | %Z037107 | DI |  | 70CRB05 | [5 empty] | TBF02 | 13 | 14 |  |  | 70LAB10AP022 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10AP022XB31 | 电动给水泵B液力耦合器交流润滑油泵控制电源消失 | Electrical feedwater pump Bcoupler AC lube oil pump control circuit broken | 70CRB02 | FCS0705 | 3 | 7 | 8 | ADV151-P | SI | N | %Z037108 | [8 empty] | %Z037108 | DI |  | 70CRB05 | [5 empty] | TBF02 | 15 | 16 |  |  | 70LAB10AP022 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LAB10AP022XB32 | 电动给水泵B液力耦合器交流润滑油泵故障输出 | Electrical feedwater pump Bcoupler AC lube oil pump fault output | 70CRB02 | FCS0705 | 3 | 7 | 9 | ADV151-P | SI | N | %Z037109 | [8 empty] | %Z037109 | DI |  | 70CRB05 | [5 empty] | TBF02 | 17 | 18 |  |  | 70LAB10AP022 | NO | DI | [8 empty] | SCS | D |  | K0204-007
|  | 70LCB10AP002XB01 | 凝结水泵B运行 | Condensate pump B running | 70CRB02 | FCS0705 | 3 | 7 | 10 | ADV151-P | SI | N | %Z037110 | [8 empty] | %Z037110 | DI |  | 70CRB05 | [5 empty] | TBF02 | 19 | 20 |  |  | 70LCB10AP002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP002XB11 | 凝结水泵B停止 | Condensate pump B stopped | 70CRB02 | FCS0705 | 3 | 7 | 11 | ADV151-P | SI | N | %Z037111 | [8 empty] | %Z037111 | DI |  | 70CRB05 | [5 empty] | TBF02 | 21 | 22 |  |  | 70LCB10AP002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP002XB21 | 凝结水泵B远方控制允许 | Condensate pump B remote control permitted | 70CRB02 | FCS0705 | 3 | 7 | 12 | ADV151-P | SI | N | %Z037112 | [8 empty] | %Z037112 | DI |  | 70CRB05 | [5 empty] | TBF02 | 23 | 24 |  |  | 70LCB10AP002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP002XB31 | 凝结水泵B装置故障控制电源消失 | Condensate pump B device fault control power loss | 70CRB02 | FCS0705 | 3 | 7 | 13 | ADV151-P | SI | N | %Z037113 | [8 empty] | %Z037113 | DI |  | 70CRB05 | [5 empty] | TBF02 | 25 | 26 |  |  | 70LCB10AP002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP002XB32 | 凝结水泵B保护动作 | Condensate pump B protection movement | 70CRB02 | FCS0705 | 3 | 7 | 14 | ADV151-P | SI | N | %Z037114 | [8 empty] | %Z037114 | DI |  | 70CRB05 | [5 empty] | TBF02 | 27 | 28 |  |  | 70LCB10AP002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70MAG12AA012XB01 | 真空泵A入口气动阀全开状态 | Vacuum pump A inlet PV full opened status | 70CRB02 | FCS0705 | 3 | 7 | 15 | ADV151-P | SI | N | %Z037115 | [8 empty] | %Z037115 | DI |  | 70CRB05 | [5 empty] | TBF02 | 29 | 30 |  |  | 70MAG12GH002 | NO | DI | [8 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
|  | 70MAG12AA012XB11 | 真空泵A入口气动阀全关状态 | Vacuum pump A inlet PV full closed status | 70CRB02 | FCS0705 | 3 | 7 | 16 | ADV151-P | SI | N | %Z037116 | [8 empty] | %Z037116 | DI |  | 70CRB05 | [5 empty] | TBF02 | 31 | 32 |  |  | 70MAG12GH002 | NO | DI | [8 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
|  | 70MAG12AA001XB01 | 真空泵A入口电动门全开状态 | Vacuum pump A inlet MOV full opened status | 70CRB02 | FCS0705 | 3 | 7 | 17 | ADV151-P | SI | N | %Z037117 | [8 empty] | %Z037117 | DI |  | 70CRB05 | [5 empty] | TBF02 | 33 | 34 |  |  | 70MAG12AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG12AA001XB11 | 真空泵A入口电动门全关状态 | Vacuum pump A inlet MOV full closed status | 70CRB02 | FCS0705 | 3 | 7 | 18 | ADV151-P | SI | N | %Z037118 | [8 empty] | %Z037118 | DI |  | 70CRB05 | [5 empty] | TBF02 | 35 | 36 |  |  | 70MAG12AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG12AA001XB31 | 真空泵A入口电动门故障状态 | Vacuum pump A inlet MOV fault | 70CRB02 | FCS0705 | 3 | 7 | 19 | ADV151-P | SI | N | %Z037119 | [8 empty] | %Z037119 | DI |  | 70CRB05 | [5 empty] | TBF02 | 37 | 38 |  |  | 70MAG12AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG12AP001XB01 | 真空泵A运行 | Vacuum pump A running | 70CRB02 | FCS0705 | 3 | 7 | 20 | ADV151-P | SI | N | %Z037120 | [8 empty] | %Z037120 | DI |  | 70CRB05 | [5 empty] | TBF02 | 39 | 40 |  |  | 70MAG12AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG12AP001XB11 | 真空泵A停止 | Vacuum pump A stopped | 70CRB02 | FCS0705 | 3 | 7 | 21 | ADV151-P | SI | N | %Z037121 | [8 empty] | %Z037121 | DI |  | 70CRB05 | [5 empty] | TBF02 | 41 | 42 |  |  | 70MAG12AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG12AP001XB21 | 真空泵A远方控制允许 | Vacuum pump A remote control permitted | 70CRB02 | FCS0705 | 3 | 7 | 22 | ADV151-P | SI | N | %Z037122 | [8 empty] | %Z037122 | DI |  | 70CRB05 | [5 empty] | TBF02 | 43 | 44 |  |  | 70MAG12AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG12AP001XB31 | 真空泵A控制电源消失 | Vacuum pump A control circuit broken | 70CRB02 | FCS0705 | 3 | 7 | 23 | ADV151-P | SI | N | %Z037123 | [8 empty] | %Z037123 | DI |  | 70CRB05 | [5 empty] | TBF02 | 45 | 46 |  |  | 70MAG12AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG12AP001XB32 | 真空泵A故障输出 | Vacuum pump A fault output | 70CRB02 | FCS0705 | 3 | 7 | 24 | ADV151-P | SI | N | %Z037124 | [8 empty] | %Z037124 | DI |  | 70CRB05 | [5 empty] | TBF02 | 47 | 48 |  |  | 70MAG12AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG10AA001XB01 | 真空泵破坏电动门全开状态 | Vacuum break MOV full opened status | 70CRB02 | FCS0705 | 3 | 7 | 25 | ADV151-P | SI | N | %Z037125 | [8 empty] | %Z037125 | DI |  | 70CRB05 | [5 empty] | TBF02 | 49 | 50 |  |  | 70MAG10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG10AA001XB11 | 真空泵破坏电动门全关状态 | Vacuum break MOV full closed status | 70CRB02 | FCS0705 | 3 | 7 | 26 | ADV151-P | SI | N | %Z037126 | [8 empty] | %Z037126 | DI |  | 70CRB05 | [5 empty] | TBF02 | 51 | 52 |  |  | 70MAG10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG10AA001XB31 | 真空泵破坏电动门故障状态 | Vacuum break MOV fault | 70CRB02 | FCS0705 | 3 | 7 | 27 | ADV151-P | SI | N | %Z037127 | [8 empty] | %Z037127 | DI |  | 70CRB05 | [5 empty] | TBF02 | 53 | 54 |  |  | 70MAG10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
[5 empty] | 70CRB02 | FCS0705 | 3 | 7 | 28 | ADV151-P | SI | N | %Z037128 | [8 empty] | %Z037128 | DI |  | 70CRB05 | [5 empty] | TBF02 | 55 | 56
[5 empty] | 70CRB02 | FCS0705 | 3 | 7 | 29 | ADV151-P | SI | N | %Z037129 | [8 empty] | %Z037129 | DI |  | 70CRB05 | [5 empty] | TBF02 | 57 | 58
[5 empty] | 70CRB02 | FCS0705 | 3 | 7 | 30 | ADV151-P | SI | N | %Z037130 | [8 empty] | %Z037130 | DI |  | 70CRB05 | [5 empty] | TBF02 | 59 | 60
[5 empty] | 70CRB02 | FCS0705 | 3 | 7 | 31 | ADV151-P | SI | N | %Z037131 | [8 empty] | %Z037131 | DI |  | 70CRB05 | [5 empty] | TBF02 | 61 | 62
[5 empty] | 70CRB02 | FCS0705 | 3 | 7 | 32 | ADV151-P | SI | N | %Z037132 | [8 empty] | %Z037132 | DI |  | 70CRB05 | [5 empty] | TBF02 | 63 | 64
|  | 70LCA10CP003H | 凝结水泵C入口滤网差压高 | Condensate pump C inlet filter DP H | 70CRB02 | FCS0705 | 4 | 6 | 1 | ADV151-P | SI | N | %Z046101 | [7 empty] | KPa | %Z046101 | DI |  | 70CRB05 | [5 empty] | TBG01 | 1 | 2 |  |  | 70LCA10CP003H | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0204-008
|  | 70LCA20AA003XB01 | 凝结水泵C出口电动阀全开状态 | Condensate pump C outlet MOV full opened status | 70CRB02 | FCS0705 | 4 | 6 | 2 | ADV151-P | SI | N | %Z046102 | [8 empty] | %Z046102 | DI |  | 70CRB05 | [5 empty] | TBG01 | 3 | 4 |  |  | 70LCA20AA003 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCA20AA003XB11 | 凝结水泵C出口电动阀全关状态 | Condensate pump C outlet MOV full closed status | 70CRB02 | FCS0705 | 4 | 6 | 3 | ADV151-P | SI | N | %Z046103 | [8 empty] | %Z046103 | DI |  | 70CRB05 | [5 empty] | TBG01 | 5 | 6 |  |  | 70LCA20AA003 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCA20AA003XB31 | 凝结水泵C出口电动阀故障 | Condensate pump C outlet MOV fault | 70CRB02 | FCS0705 | 4 | 6 | 4 | ADV151-P | SI | N | %Z046104 | [8 empty] | %Z046104 | DI |  | 70CRB05 | [5 empty] | TBG01 | 7 | 8 |  |  | 70LCA20AA003 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCA30AA402XB01 | 凝结水有压放水电动阀全开状态 | Condensate water pressure drain MOV full opened status | 70CRB02 | FCS0705 | 4 | 6 | 5 | ADV151-P | SI | N | %Z046105 | [8 empty] | %Z046105 | DI |  | 70CRB05 | [5 empty] | TBG01 | 9 | 10 |  |  | 70LCA30AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCA30AA402XB11 | 凝结水有压放水电动阀全关状态 | Condensate water pressure drain MOV full closed status | 70CRB02 | FCS0705 | 4 | 6 | 6 | ADV151-P | SI | N | %Z046106 | [8 empty] | %Z046106 | DI |  | 70CRB05 | [5 empty] | TBG01 | 11 | 12 |  |  | 70LCA30AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCA30AA402XB31 | 凝结水有压放水电动阀故障 | Condensate water pressure drain MOV fault | 70CRB02 | FCS0705 | 4 | 6 | 7 | ADV151-P | SI | N | %Z046107 | [8 empty] | %Z046107 | DI |  | 70CRB05 | [5 empty] | TBG01 | 13 | 14 |  |  | 70LCA30AA402 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70PAB10AA001XB01 | B侧凝汽器循环水进水电动阀全开状态 | Inlet water MOV of condenser by side B full opened status | 70CRB02 | FCS0705 | 4 | 6 | 8 | ADV151-P | SI | N | %Z046108 | [8 empty] | %Z046108 | DI |  | 70CRB05 | [5 empty] | TBG01 | 15 | 16 |  |  | 70PAB10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PAB10AA001XB11 | B侧凝汽器循环水进水电动阀全关状态 | Inlet water MOV of condenser by side B full closed status | 70CRB02 | FCS0705 | 4 | 6 | 9 | ADV151-P | SI | N | %Z046109 | [8 empty] | %Z046109 | DI |  | 70CRB05 | [5 empty] | TBG01 | 17 | 18 |  |  | 70PAB10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PAB10AA001XB31 | B侧凝汽器循环水进水电动阀故障 | Inlet water MOV of condenser by side B fault | 70CRB02 | FCS0705 | 4 | 6 | 10 | ADV151-P | SI | N | %Z046110 | [8 empty] | %Z046110 | DI |  | 70CRB05 | [5 empty] | TBG01 | 19 | 20 |  |  | 70PAB10AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PAB30AA001XB01 | B侧凝汽器循环水出水电动阀全开状态 | Outlet water MOV of condenser by side B full opened status | 70CRB02 | FCS0705 | 4 | 6 | 11 | ADV151-P | SI | N | %Z046111 | [8 empty] | %Z046111 | DI |  | 70CRB05 | [5 empty] | TBG01 | 21 | 22 |  |  | 70PAB30AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PAB30AA001XB11 | B侧凝汽器循环水出水电动阀全关状态 | Outlet water MOV of condenser by side B full closed status | 70CRB02 | FCS0705 | 4 | 6 | 12 | ADV151-P | SI | N | %Z046112 | [8 empty] | %Z046112 | DI |  | 70CRB05 | [5 empty] | TBG01 | 23 | 24 |  |  | 70PAB30AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PAB30AA001XB31 | B侧凝汽器循环水出水电动阀故障 | Outlet water MOV of condenser by side B fault | 70CRB02 | FCS0705 | 4 | 6 | 13 | ADV151-P | SI | N | %Z046113 | [8 empty] | %Z046113 | DI |  | 70CRB05 | [5 empty] | TBG01 | 25 | 26 |  |  | 70PAB30AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-014
|  | 70PGA10AP001XB01 | 1#除盐水泵运行 | 1# demineralized water pump running | 70CRB02 | FCS0705 | 4 | 6 | 14 | ADV151-P | SI | N | %Z046114 | [8 empty] | %Z046114 | DI |  | 70CRB05 | [5 empty] | TBG01 | 27 | 28 |  |  | 70PGA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
|  | 70PGA10AP001XB31 | 1#除盐水泵故障 | 1# demineralized water pump fault | 70CRB02 | FCS0705 | 4 | 6 | 15 | ADV151-P | SI | N | %Z046115 | [8 empty] | %Z046115 | DI |  | 70CRB05 | [5 empty] | TBG01 | 29 | 30 |  |  | 70PGA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
|  | 70PGA10CL101H | 除盐水箱液位高 | Demineralized water tank level H | 70CRB02 | FCS0705 | 4 | 6 | 16 | ADV151-P | SI | N | %Z046116 | [7 empty] | m | %Z046116 | DI |  | 70CRB05 | [5 empty] | TBG01 | 31 | 32 |  |  | 70PGA10GH001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
|  | 70PGA20CP001L | 工业冷却水入口压力低 | Industrial cooling water inlet pressure L | 70CRB02 | FCS0705 | 4 | 6 | 17 | ADV151-P | SI | N | %Z046117 | [7 empty] | Mpa | %Z046117 | DI |  | 70CRB05 | [5 empty] | TBG01 | 33 | 34 |  |  | 70PGA10GH001 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
|  | 70PGA10AA002XB01 | 除盐水箱入口电磁阀全开状态 | Demineralized water tank inlet SV opened status | 70CRB02 | FCS0705 | 4 | 6 | 18 | ADV151-P | SI | N | %Z046118 | [8 empty] | %Z046118 | DI |  | 70CRB05 | [5 empty] | TBG01 | 35 | 36 |  |  | 70PGA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
|  | 70LAA20AA002XB01 | 除氧器放水电动阀全开状态 | Deaerator discharge MOV full opened status | 70CRB02 | FCS0705 | 4 | 6 | 19 | ADV151-P | SI | N | %Z046119 | [8 empty] | %Z046119 | DI |  | 70CRB05 | [5 empty] | TBG01 | 37 | 38 |  |  | 70LAA20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LAA20AA002XB11 | 除氧器放水电动阀全关状态 | Deaerator discharge MOV full closed status | 70CRB02 | FCS0705 | 4 | 6 | 20 | ADV151-P | SI | N | %Z046120 | [8 empty] | %Z046120 | DI |  | 70CRB05 | [5 empty] | TBG01 | 39 | 40 |  |  | 70LAA20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LAA20AA002XB31 | 除氧器放水电动阀故障 | Deaerator discharge MOV fault | 70CRB02 | FCS0705 | 4 | 6 | 21 | ADV151-P | SI | N | %Z046121 | [8 empty] | %Z046121 | DI |  | 70CRB05 | [5 empty] | TBG01 | 41 | 42 |  |  | 70LAA20AA002 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70QCD12AM001XB01 | 2#氨溶液箱搅拌机运行 | 2# ammonia solution tank agitator running | 70CRB02 | FCS0705 | 4 | 6 | 22 | ADV151-P | SI | N | %Z046122 | [8 empty] | %Z046122 | DI |  | 70CRB05 | [5 empty] | TBG01 | 43 | 44 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD12AM001XB31 | 2#氨溶液箱搅拌机故障 | 2# ammonia solution tank agitator fault | 70CRB02 | FCS0705 | 4 | 6 | 23 | ADV151-P | SI | N | %Z046123 | [8 empty] | %Z046123 | DI |  | 70CRB05 | [5 empty] | TBG01 | 45 | 46 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD12AM001XB21 | 2#氨溶液箱搅拌机远程 | 2# ammonia solution tank agitator remote control | 70CRB02 | FCS0705 | 4 | 6 | 24 | ADV151-P | SI | N | %Z046124 | [8 empty] | %Z046124 | DI |  | 70CRB05 | [5 empty] | TBG01 | 47 | 48 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD12AP001XB01 | 2#给水氨计量泵运行 | 2# feed water ammonia metering pump running | 70CRB02 | FCS0705 | 4 | 6 | 25 | ADV151-P | SI | N | %Z046125 | [8 empty] | %Z046125 | DI |  | 70CRB05 | [5 empty] | TBG01 | 49 | 50 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD12AP001XB31 | 2#给水氨计量泵故障 | 2# feed water ammonia metering pump fault | 70CRB02 | FCS0705 | 4 | 6 | 26 | ADV151-P | SI | N | %Z046126 | [8 empty] | %Z046126 | DI |  | 70CRB05 | [5 empty] | TBG01 | 51 | 52 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD12AP001XB21 | 2#给水氨计量泵远程 | 2# feed water ammonia metering pump remote control | 70CRB02 | FCS0705 | 4 | 6 | 27 | ADV151-P | SI | N | %Z046127 | [8 empty] | %Z046127 | DI |  | 70CRB05 | [5 empty] | TBG01 | 53 | 54 |  |  | 70QCD10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70MAG11CP001 | 真空泵B入口气动阀前压力低 | Pressure L before Vacuum pump B inlet PV | 70CRB02 | FCS0705 | 4 | 6 | 28 | ADV151-P | SI | N | %Z046128 | [7 empty] | Kpa | %Z046128 | DI |  | 70CRB05 | [5 empty] | TBG01 | 55 | 56 |  |  | 70MAG11GH002 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
|  | 70MAG11CP002 | 真空泵B入口气动阀后压力 | Pressure after Vacuum pump B inlet PV | 70CRB02 | FCS0705 | 4 | 6 | 29 | ADV151-P | SI | N | %Z046129 | [7 empty] | Kpa | %Z046129 | DI |  | 70CRB05 | [5 empty] | TBG01 | 57 | 58 |  |  | 70MAG11GH002 | NO | DI | [8 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
|  | 70MAG11CL101H | 真空泵B分离罐液位高 | Vacuum pump B separator level H | 70CRB02 | FCS0705 | 4 | 6 | 30 | ADV151-P | SI | N | %Z046130 | [7 empty] | mm | %Z046130 | DI |  | 70CRB05 | [5 empty] | TBG01 | 59 | 60 |  |  | 70MAG11GH002 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
|  | 70MAG11CL101L | 真空泵B分离罐液位低 | Vacuum pump B separator level L | 70CRB02 | FCS0705 | 4 | 6 | 31 | ADV151-P | SI | N | %Z046131 | [7 empty] | mm | %Z046131 | DI |  | 70CRB05 | [5 empty] | TBG01 | 61 | 62 |  |  | 70MAG11GH002 | NC | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
[5 empty] | 70CRB02 | FCS0705 |  | 6 | 32 | ADV151-P | SI | N | %Z006132 | [8 empty] | %Z006132 | DI |  | 70CRB05 | [5 empty] | TBG01 | 63 | 64
|  | 70LCB10AP003XB01 | 凝结水泵C运行 | Condensate pump C running | 70CRB02 | FCS0705 | 4 | 7 | 1 | ADV151-P | SI | N | %Z047101 | [8 empty] | %Z047101 | DI |  | 70CRB05 | [5 empty] | TBG02 | 1 | 2 |  |  | 70LCB10AP003 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP003XB11 | 凝结水泵C停止 | Condensate pump C stopped | 70CRB02 | FCS0705 | 4 | 7 | 2 | ADV151-P | SI | N | %Z047102 | [8 empty] | %Z047102 | DI |  | 70CRB05 | [5 empty] | TBG02 | 3 | 4 |  |  | 70LCB10AP003 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP003XB21 | 凝结水泵C远方控制允许 | Condensate pump C remote control permitted | 70CRB02 | FCS0705 | 4 | 7 | 3 | ADV151-P | SI | N | %Z047103 | [8 empty] | %Z047103 | DI |  | 70CRB05 | [5 empty] | TBG02 | 5 | 6 |  |  | 70LCB10AP003 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP003XB31 | 凝结水泵C装置故障控制电源消失 | Condensate pump C device fault control power loss | 70CRB02 | FCS0705 | 4 | 7 | 4 | ADV151-P | SI | N | %Z047104 | [8 empty] | %Z047104 | DI |  | 70CRB05 | [5 empty] | TBG02 | 7 | 8 |  |  | 70LCB10AP003 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70LCB10AP003XB32 | 凝结水泵C保护动作 | Condensate pump C protection movement | 70CRB02 | FCS0705 | 4 | 7 | 5 | ADV151-P | SI | N | %Z047105 | [8 empty] | %Z047105 | DI |  | 70CRB05 | [5 empty] | TBG02 | 9 | 10 |  |  | 70LCB10AP003 | NO | DI | [8 empty] | SCS | D |  | K0204-008
|  | 70PGA10AP002XB01 | 2#除盐水泵运行 | 2# demineralized water pump running | 70CRB02 | FCS0705 | 4 | 7 | 6 | ADV151-P | SI | N | %Z047106 | [8 empty] | %Z047106 | DI |  | 70CRB05 | [5 empty] | TBG02 | 11 | 12 |  |  | 70PGA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
|  | 70PGA10AP002XB31 | 2#除盐水泵故障 | 2# demineralized water pump fault | 70CRB02 | FCS0705 | 4 | 7 | 7 | ADV151-P | SI | N | %Z047107 | [8 empty] | %Z047107 | DI |  | 70CRB05 | [5 empty] | TBG02 | 13 | 14 |  |  | 70PGA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
|  | 70PGA10CL101L | 除盐水箱液位低 | Demineralized water tank level L | 70CRB02 | FCS0705 | 4 | 7 | 8 | ADV151-P | SI | N | %Z047108 | [7 empty] | m | %Z047108 | DI |  | 70CRB05 | [5 empty] | TBG02 | 15 | 16 |  |  | 70PGA10GH001 | NO | DI |  |  |  | √ |  |  |  |  | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
|  | 70PGA10CT001H | 换热器出口母管温度高 | Heat exchanger outlet main pipe temperature H | 70CRB02 | FCS0705 | 4 | 7 | 9 | ADV151-P | SI | N | %Z047109 | [7 empty] | ℃ | %Z047109 | DI |  | 70CRB05 | [5 empty] | TBG02 | 17 | 18 |  |  | 70PGA10GH001 | NO | DI |  |  | √ | [5 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
|  | 70QCA12AM001XB01 | 2#联氨溶液箱搅拌机运行 | 2# hydrazine solution tank agitator running | 70CRB02 | FCS0705 | 4 | 7 | 10 | ADV151-P | SI | N | %Z047110 | [8 empty] | %Z047110 | DI |  | 70CRB05 | [5 empty] | TBG02 | 19 | 20 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA12AM001XB31 | 2#联氨溶液箱搅拌机故障 | 2# hydrazine solution tank agitator fault | 70CRB02 | FCS0705 | 4 | 7 | 11 | ADV151-P | SI | N | %Z047111 | [8 empty] | %Z047111 | DI |  | 70CRB05 | [5 empty] | TBG02 | 21 | 22 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA12AM001XB21 | 2#联氨溶液箱搅拌机远程 | 2# hydrazine solution tank agitator remote control | 70CRB02 | FCS0705 | 4 | 7 | 12 | ADV151-P | SI | N | %Z047112 | [8 empty] | %Z047112 | DI |  | 70CRB05 | [5 empty] | TBG02 | 23 | 24 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA12AP001XB01 | 2#给水联氨计量泵运行 | 2# feed water hydrazine metering pump running | 70CRB02 | FCS0705 | 4 | 7 | 13 | ADV151-P | SI | N | %Z047113 | [8 empty] | %Z047113 | DI |  | 70CRB05 | [5 empty] | TBG02 | 25 | 26 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA12AP001XB31 | 2#给水联氨计量泵故障 | 2# feed water hydrazine metering pump fault | 70CRB02 | FCS0705 | 4 | 7 | 14 | ADV151-P | SI | N | %Z047114 | [8 empty] | %Z047114 | DI |  | 70CRB05 | [5 empty] | TBG02 | 27 | 28 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA12AP001XB21 | 2#给水联氨计量泵远程 | 2# feed water hydrazine metering pump remote control | 70CRB02 | FCS0705 | 4 | 7 | 15 | ADV151-P | SI | N | %Z047115 | [8 empty] | %Z047115 | DI |  | 70CRB05 | [5 empty] | TBG02 | 29 | 30 |  |  | 70QCA10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCC12AM001XB01 | 2#磷酸盐溶液箱搅拌机运行 | 2# phosphate solution tank agitator running | 70CRB02 | FCS0705 | 4 | 7 | 16 | ADV151-P | SI | N | %Z047116 | [8 empty] | %Z047116 | DI |  | 70CRB05 | [5 empty] | TBG02 | 31 | 32 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC12AM001XB31 | 2#磷酸盐溶液箱搅拌机故障 | 2# phosphate solution tank agitator fault | 70CRB02 | FCS0705 | 4 | 7 | 17 | ADV151-P | SI | N | %Z047117 | [8 empty] | %Z047117 | DI |  | 70CRB05 | [5 empty] | TBG02 | 33 | 34 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC12AM001XB21 | 2#磷酸盐溶液箱搅拌机远程 | 2# phosphate solution tank agitator remote control | 70CRB02 | FCS0705 | 4 | 7 | 18 | ADV151-P | SI | N | %Z047118 | [8 empty] | %Z047118 | DI |  | 70CRB05 | [5 empty] | TBG02 | 35 | 36 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC12AP001XB01 | 2#磷酸盐计量泵运行 | 2# phosphate metering pump running | 70CRB02 | FCS0705 | 4 | 7 | 19 | ADV151-P | SI | N | %Z047119 | [8 empty] | %Z047119 | DI |  | 70CRB05 | [5 empty] | TBG02 | 37 | 38 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC12AP001XB31 | 2#磷酸盐计量泵故障 | 2# phosphate metering pump fault | 70CRB02 | FCS0705 | 4 | 7 | 20 | ADV151-P | SI | N | %Z047120 | [8 empty] | %Z047120 | DI |  | 70CRB05 | [5 empty] | TBG02 | 39 | 40 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC12AP001XB21 | 2#磷酸盐计量泵远程 | 2# phosphate metering pump remote control | 70CRB02 | FCS0705 | 4 | 7 | 21 | ADV151-P | SI | N | %Z047121 | [8 empty] | %Z047121 | DI |  | 70CRB05 | [5 empty] | TBG02 | 41 | 42 |  |  | 70QCC10GH001 | NO | DI | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70MAG11AA012XB01 | 真空泵B入口气动阀全开状态 | Vacuum pump B inlet PV full opened status | 70CRB02 | FCS0705 | 4 | 7 | 22 | ADV151-P | SI | N | %Z047122 | [8 empty] | %Z047122 | DI |  | 70CRB05 | [5 empty] | TBG02 | 43 | 44 |  |  | 70MAG11GH002 | NO | DI | [8 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
|  | 70MAG11AA012XB11 | 真空泵B入口气动阀全关状态 | Vacuum pump B inlet PV full closed status | 70CRB02 | FCS0705 | 4 | 7 | 23 | ADV151-P | SI | N | %Z047123 | [8 empty] | %Z047123 | DI |  | 70CRB05 | [5 empty] | TBG02 | 45 | 46 |  |  | 70MAG11GH002 | NO | DI | [8 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
|  | 70MAG11AA001XB01 | 真空泵B入口电动门全开状态 | Vacuum pump B inlet MOV full opened status | 70CRB02 | FCS0705 | 4 | 7 | 24 | ADV151-P | SI | N | %Z047124 | [8 empty] | %Z047124 | DI |  | 70CRB05 | [5 empty] | TBG02 | 47 | 48 |  |  | 70MAG11AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG11AA001XB11 | 真空泵B入口电动门全关状态 | Vacuum pump B inlet MOV full closed status | 70CRB02 | FCS0705 | 4 | 7 | 25 | ADV151-P | SI | N | %Z047125 | [8 empty] | %Z047125 | DI |  | 70CRB05 | [5 empty] | TBG02 | 49 | 50 |  |  | 70MAG11AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG11AA001XB31 | 真空泵B入口电动门故障状态 | Vacuum pump B inlet MOV fault | 70CRB02 | FCS0705 | 4 | 7 | 26 | ADV151-P | SI | N | %Z047126 | [8 empty] | %Z047126 | DI |  | 70CRB05 | [5 empty] | TBG02 | 51 | 52 |  |  | 70MAG11AA001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG11AP001XB01 | 真空泵B运行 | Vacuum pump B running | 70CRB02 | FCS0705 | 4 | 7 | 27 | ADV151-P | SI | N | %Z047127 | [8 empty] | %Z047127 | DI |  | 70CRB05 | [5 empty] | TBG02 | 53 | 54 |  |  | 70MAG11AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG11AP001XB11 | 真空泵B停止 | Vacuum pump B stopped | 70CRB02 | FCS0705 | 4 | 7 | 28 | ADV151-P | SI | N | %Z047128 | [8 empty] | %Z047128 | DI |  | 70CRB05 | [5 empty] | TBG02 | 55 | 56 |  |  | 70MAG11AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG11AP001XB21 | 真空泵B远方控制允许 | Vacuum pump B remote control permitted | 70CRB02 | FCS0705 | 4 | 7 | 29 | ADV151-P | SI | N | %Z047129 | [8 empty] | %Z047129 | DI |  | 70CRB05 | [5 empty] | TBG02 | 57 | 58 |  |  | 70MAG11AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG11AP001XB31 | 真空泵B控制电源消失 | Vacuum pump B control circuit broken | 70CRB02 | FCS0705 | 4 | 7 | 30 | ADV151-P | SI | N | %Z047130 | [8 empty] | %Z047130 | DI |  | 70CRB05 | [5 empty] | TBG02 | 59 | 60 |  |  | 70MAG11AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
|  | 70MAG11AP001XB32 | 真空泵B故障输出 | Vacuum pump B fault output | 70CRB02 | FCS0705 | 4 | 7 | 31 | ADV151-P | SI | N | %Z047131 | [8 empty] | %Z047131 | DI |  | 70CRB05 | [5 empty] | TBG02 | 61 | 62 |  |  | 70MAG11AP001 | NO | DI | [8 empty] | SCS | D |  | K0204-003
[5 empty] | 70CRB02 | FCS0705 | 4 | 7 | 32 | ADV151-P | SI | N | %Z047132 | [8 empty] | %Z047132 | DI |  | 70CRB05 | [5 empty] | TBG02 | 63 | 64
|  | 70LAB20AP001YB01 | 电动给水泵A启动指令 | Electrical feedwater pump A start command | 70CRB02 | FCS0705 | 2 | 8 | 1 | ADV551-P | SO | N | %Z028101 | [8 empty] | %Z028101 | DO |  | 70CRB05 | [5 empty] | TBC03 | 1 | 2 |  | 220VDC | 70LAB20AP001 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB20AP001YB11 | 电动给水泵A停止指令 | Electrical feedwater pump A stop command | 70CRB02 | FCS0705 | 2 | 8 | 2 | ADV551-P | SO | N | %Z028102 | [8 empty] | %Z028102 | DO |  | 70CRB05 | [5 empty] | TBC03 | 3 | 4 |  | 220VDC | 70LAB20AP001 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
|  | 70LAB40AA002YB01 | 电动给水泵A出口电动阀打开指令 | Electrical feedwater pump A outlet MOV open command | 70CRB02 | FCS0705 | 2 | 8 | 3 | ADV551-P | SO | N | %Z028103 | [8 empty] | %Z028103 | DO |  | 70CRB05 | [5 empty] | TBC03 | 5 | 6 |  |  | 70LAB40AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAB40AA002YB11 | 电动给水泵A出口电动阀关闭指令 | Electrical feedwater pump A outlet MOV close command | 70CRB02 | FCS0705 | 2 | 8 | 4 | ADV551-P | SO | N | %Z028104 | [8 empty] | %Z028104 | DO |  | 70CRB05 | [5 empty] | TBC03 | 7 | 8 |  |  | 70LAB40AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAH10AA001YB01 | 电动给水泵A给水再循环电动阀打开指令 | Electrical feedwater pump A feedwater recycling MOV open command | 70CRB02 | FCS0705 | 2 | 8 | 5 | ADV551-P | SO | N | %Z028105 | [8 empty] | %Z028105 | DO |  | 70CRB05 | [5 empty] | TBC03 | 9 | 10 |  |  | 70LAH10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAH10AA001YB11 | 电动给水泵A给水再循环电动阀关闭指令 | Electrical feedwater pump A feedwater recycling MOV close command | 70CRB02 | FCS0705 | 2 | 8 | 6 | ADV551-P | SO | N | %Z028106 | [8 empty] | %Z028106 | DO |  | 70CRB05 | [5 empty] | TBC03 | 11 | 12 |  |  | 70LAH10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LCA20AA001YB01 | 凝结水泵A出口电动阀打开指令 | Condensate pump A outlet MOV open command | 70CRB02 | FCS0705 | 2 | 8 | 7 | ADV551-P | SO | N | %Z028107 | [8 empty] | %Z028107 | DO |  | 70CRB05 | [5 empty] | TBC03 | 13 | 14 |  |  | 70LCA20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70LCA20AA001YB11 | 凝结水泵A出口电动阀关闭指令 | Condensate pump A outlet MOV close command | 70CRB02 | FCS0705 | 2 | 8 | 8 | ADV551-P | SO | N | %Z028108 | [8 empty] | %Z028108 | DO |  | 70CRB05 | [5 empty] | TBC03 | 15 | 16 |  |  | 70LCA20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70LCB10AP001YB01 | 凝结水泵A启动指令 | Condensate pump A start command | 70CRB02 | FCS0705 | 2 | 8 | 9 | ADV551-P | SO | N | %Z028109 | [8 empty] | %Z028109 | DO |  | 70CRB05 | [5 empty] | TBC03 | 17 | 18 |  | 220VDC | 70LCB10AP001 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-008
|  | 70LCB10AP001YB11 | 凝结水泵A停止指令 | Condensate pump A stop command | 70CRB02 | FCS0705 | 2 | 8 | 10 | ADV551-P | SO | N | %Z028110 | [8 empty] | %Z028110 | DO |  | 70CRB05 | [5 empty] | TBC03 | 19 | 20 |  | 220VDC | 70LCB10AP001 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-008
|  | 70LAA20AA001YB01 | 除氧器溢流电动阀打开指令 | Deaerator overflow MOV open command | 70CRB02 | FCS0705 | 2 | 8 | 11 | ADV551-P | SO | N | %Z028111 | [8 empty] | %Z028111 | DO |  | 70CRB05 | [5 empty] | TBC03 | 21 | 22 |  |  | 70LAA20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70LAA20AA001YB11 | 除氧器溢流电动阀关闭指令 | Deaerator overflow MOV close command | 70CRB02 | FCS0705 | 2 | 8 | 12 | ADV551-P | SO | N | %Z028112 | [8 empty] | %Z028112 | DO |  | 70CRB05 | [5 empty] | TBC03 | 23 | 24 |  |  | 70LAA20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
[5 empty] | 70CRB02 | FCS0705 | 2 | 8 | 13 | ADV551-P | SO | N | %Z028113 | [8 empty] | %Z028113 | DO |  | 70CRB05 | [5 empty] | TBC03 | 25 | 26
[5 empty] | 70CRB02 | FCS0705 | 2 | 8 | 14 | ADV551-P | SO | N | %Z028114 | [8 empty] | %Z028114 | DO |  | 70CRB05 | [5 empty] | TBC03 | 27 | 28
[5 empty] | 70CRB02 | FCS0705 | 2 | 8 | 15 | ADV551-P | SO | N | %Z028115 | [8 empty] | %Z028115 | DO |  | 70CRB05 | [5 empty] | TBC03 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 2 | 8 | 16 | ADV551-P | SO | N | %Z028116 | [8 empty] | %Z028116 | DO |  | 70CRB05 | [5 empty] | TBC03 | 31 | 32
|  | 70LAB20AP021YB01 | 电动给水泵A液力耦合器直流润滑油泵启动指令 | Electrical feedwater pump A coupler DC lube oil pump start command | 70CRB02 | FCS0705 | 2 | 8 | 17 | ADV551-P | SO | N | %Z028117 | [8 empty] | %Z028117 | DO |  | 70CRB05 | [5 empty] | TBC03 | 33 | 34 |  | 220VDC | 70LAB20AP021 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-007
|  | 70LAB20AP021YB11 | 电动给水泵A液力耦合器直流润滑油泵停止指令 | Electrical feedwater pump A coupler DC lube oil pump stop command | 70CRB02 | FCS0705 | 2 | 8 | 18 | ADV551-P | SO | N | %Z028118 | [8 empty] | %Z028118 | DO |  | 70CRB05 | [5 empty] | TBC03 | 35 | 36 |  | 220VDC | 70LAB20AP021 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-007
|  | 70LAB20AP022YB01 | 电动给水泵A液力耦合器交流润滑油泵启动指令 | Electrical feedwater pump A coupler AC lube oil pump start command | 70CRB02 | FCS0705 | 2 | 8 | 19 | ADV551-P | SO | N | %Z028119 | [8 empty] | %Z028119 | DO |  | 70CRB05 | [5 empty] | TBC03 | 37 | 38 |  |  | 70LAB20AP022 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-007
|  | 70LAB20AP022YB11 | 电动给水泵A液力耦合器交流润滑油泵停止指令 | Electrical feedwater pump A coupler AC lube oil pump stop command | 70CRB02 | FCS0705 | 2 | 8 | 20 | ADV551-P | SO | N | %Z028120 | [8 empty] | %Z028120 | DO |  | 70CRB05 | [5 empty] | TBC03 | 39 | 40 |  |  | 70LAB20AP022 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-007
|  | 70QCD11AM001YB01 | 1#氨溶液箱搅拌机启动/停止指令 | 1# ammonia solution tank agitator start/stop command | 70CRB02 | FCS0705 | 2 | 8 | 21 | ADV551-P | SO | N | %Z028121 | [8 empty] | %Z028121 | DO |  | 70CRB05 | [5 empty] | TBC03 | 41 | 42 |  |  | 70QCD10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD11AP001YB01 | 1#给水氨计量泵启动/停止指令 | 1# feed water ammonia metering pump start/stop command | 70CRB02 | FCS0705 | 2 | 8 | 22 | ADV551-P | SO | N | %Z028122 | [8 empty] | %Z028122 | DO |  | 70CRB05 | [5 empty] | TBC03 | 43 | 44 |  |  | 70QCD10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCA11AM001YB01 | 1#联氨溶液箱搅拌机启动/停止指令 | 1# hydrazine solution tank agitator start/stop command | 70CRB02 | FCS0705 | 2 | 8 | 23 | ADV551-P | SO | N | %Z028123 | [8 empty] | %Z028123 | DO |  | 70CRB05 | [5 empty] | TBC03 | 45 | 46 |  |  | 70QCA10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA11AP001YB01 | 1#给水联氨计量泵启动/停止指令 | 1# feed water hydrazine metering pump start/stop command | 70CRB02 | FCS0705 | 2 | 8 | 24 | ADV551-P | SO | N | %Z028124 | [8 empty] | %Z028124 | DO |  | 70CRB05 | [5 empty] | TBC03 | 47 | 48 |  |  | 70QCA10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCC11AM001YB01 | 1#磷酸盐溶液箱搅拌机启动/停止指令 | 1# phosphate solution tank agitator start/stop command | 70CRB02 | FCS0705 | 2 | 8 | 25 | ADV551-P | SO | N | %Z028125 | [8 empty] | %Z028125 | DO |  | 70CRB05 | [5 empty] | TBC03 | 49 | 50 |  |  | 70QCC10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC11AP001YB01 | 1#磷酸盐计量泵启动/停止指令 | 1# phosphate metering pump start/stop command | 70CRB02 | FCS0705 | 2 | 8 | 26 | ADV551-P | SO | N | %Z028126 | [8 empty] | %Z028126 | DO |  | 70CRB05 | [5 empty] | TBC03 | 51 | 52 |  |  | 70QCC10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
[5 empty] | 70CRB02 | FCS0705 | 2 | 8 | 27 | ADV551-P | SO | N | %Z028127 | [8 empty] | %Z028127 | DO |  | 70CRB05 | [5 empty] | TBC03 | 53 | 54
[5 empty] | 70CRB02 | FCS0705 | 2 | 8 | 28 | ADV551-P | SO | N | %Z028128 | [8 empty] | %Z028128 | DO |  | 70CRB05 | [5 empty] | TBC03 | 55 | 56
[5 empty] | 70CRB02 | FCS0705 | 2 | 8 | 29 | ADV551-P | SO | N | %Z028129 | [8 empty] | %Z028129 | DO |  | 70CRB05 | [5 empty] | TBC03 | 57 | 58
[5 empty] | 70CRB02 | FCS0705 | 2 | 8 | 30 | ADV551-P | SO | N | %Z028130 | [8 empty] | %Z028130 | DO |  | 70CRB05 | [5 empty] | TBC03 | 59 | 60
[5 empty] | 70CRB02 | FCS0705 | 2 | 8 | 31 | ADV551-P | SO | N | %Z028131 | [8 empty] | %Z028131 | DO |  | 70CRB05 | [5 empty] | TBC03 | 61 | 62
[5 empty] | 70CRB02 | FCS0705 | 2 | 8 | 32 | ADV551-P | SO | N | %Z028132 | [8 empty] | %Z028132 | DO |  | 70CRB05 | [5 empty] | TBC03 | 63 | 64
|  | 70LAB10AP001YB01 | 电动给水泵B启动指令 | Electrical feedwater pump B start command | 70CRB02 | FCS0705 | 3 | 8 | 1 | ADV551-P | SO | N | %Z038101 | [8 empty] | %Z038101 | DO |  | 70CRB05 | [5 empty] | TBF03 | 1 | 2 |  | 220VDC | 70LAB10AP001 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LAB10AP001YB11 | 电动给水泵B停止指令 | Electrical feedwater pump B stop command | 70CRB02 | FCS0705 | 3 | 8 | 2 | ADV551-P | SO | N | %Z038102 | [8 empty] | %Z038102 | DO |  | 70CRB05 | [5 empty] | TBF03 | 3 | 4 |  | 220VDC | 70LAB10AP001 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
|  | 70LAB30AA002YB01 | 电动给水泵B出口电动阀打开指令 | Electrical feedwater pump B outlet MOV open command | 70CRB02 | FCS0705 | 3 | 8 | 3 | ADV551-P | SO | N | %Z038103 | [8 empty] | %Z038103 | DO |  | 70CRB05 | [5 empty] | TBF03 | 5 | 6 |  |  | 70LAB30AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAB30AA002YB11 | 电动给水泵B出口电动阀关闭指令 | Electrical feedwater pump B outlet MOV close command | 70CRB02 | FCS0705 | 3 | 8 | 4 | ADV551-P | SO | N | %Z038104 | [8 empty] | %Z038104 | DO |  | 70CRB05 | [5 empty] | TBF03 | 7 | 8 |  |  | 70LAB30AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAH20AA001YB01 | 电动给水泵B给水再循环电动阀打开指令 | Electrical feedwater pump B feedwater recycling MOV open command | 70CRB02 | FCS0705 | 3 | 8 | 5 | ADV551-P | SO | N | %Z038105 | [8 empty] | %Z038105 | DO |  | 70CRB05 | [5 empty] | TBF03 | 9 | 10 |  |  | 70LAH20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LAH20AA001YB11 | 电动给水泵B给水再循环电动阀关闭指令 | Electrical feedwater pump B feedwater recycling MOV close command | 70CRB02 | FCS0705 | 3 | 8 | 6 | ADV551-P | SO | N | %Z038106 | [8 empty] | %Z038106 | DO |  | 70CRB05 | [5 empty] | TBF03 | 11 | 12 |  |  | 70LAH20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-006
|  | 70LCA20AA002YB01 | 凝结水泵B出口电动阀打开指令 | Condensate pump B outlet MOV open command | 70CRB02 | FCS0705 | 3 | 8 | 7 | ADV551-P | SO | N | %Z038107 | [8 empty] | %Z038107 | DO |  | 70CRB05 | [5 empty] | TBF03 | 13 | 14 |  |  | 70LCA20AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70LCA20AA002YB11 | 凝结水泵B出口电动阀关闭指令 | Condensate pump B outlet MOV close command | 70CRB02 | FCS0705 | 3 | 8 | 8 | ADV551-P | SO | N | %Z038108 | [8 empty] | %Z038108 | DO |  | 70CRB05 | [5 empty] | TBF03 | 15 | 16 |  |  | 70LCA20AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70LCB10AP002YB01 | 凝结水泵B启动指令 | Condensate pump B start command | 70CRB02 | FCS0705 | 3 | 8 | 9 | ADV551-P | SO | N | %Z038109 | [8 empty] | %Z038109 | DO |  | 70CRB05 | [5 empty] | TBF03 | 17 | 18 |  | 220VDC | 70LCB10AP002 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-008
|  | 70LCB10AP002YB11 | 凝结水泵B停止指令 | Condensate pump B stop command | 70CRB02 | FCS0705 | 3 | 8 | 10 | ADV551-P | SO | N | %Z038110 | [8 empty] | %Z038110 | DO |  | 70CRB05 | [5 empty] | TBF03 | 19 | 20 |  | 220VDC | 70LCB10AP002 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-008
|  | 70PAB20AA001YB01 | A侧凝汽器循环水进水电动阀打开指令 | Inlet water MOV of condenser by side A open command | 70CRB02 | FCS0705 | 3 | 8 | 11 | ADV551-P | SO | N | %Z038111 | [8 empty] | %Z038111 | DO |  | 70CRB05 | [5 empty] | TBF03 | 21 | 22 |  |  | 70PAB20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-014
|  | 70PAB20AA001YB11 | A侧凝汽器循环水进水电动阀关闭指令 | Inlet water MOV of condenser by side A close command | 70CRB02 | FCS0705 | 3 | 8 | 12 | ADV551-P | SO | N | %Z038112 | [8 empty] | %Z038112 | DO |  | 70CRB05 | [5 empty] | TBF03 | 23 | 24 |  |  | 70PAB20AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-014
|  | 70PAB40AA001YB01 | A侧凝汽器循环水出水电动阀打开指令 | Outlet water MOV of condenser by side A open command | 70CRB02 | FCS0705 | 3 | 8 | 13 | ADV551-P | SO | N | %Z038113 | [8 empty] | %Z038113 | DO |  | 70CRB05 | [5 empty] | TBF03 | 25 | 26 |  |  | 70PAB40AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-014
|  | 70PAB40AA001YB11 | A侧凝汽器循环水出水电动阀关闭指令 | Outlet water MOV of condenser by side A close command | 70CRB02 | FCS0705 | 3 | 8 | 14 | ADV551-P | SO | N | %Z038114 | [8 empty] | %Z038114 | DO |  | 70CRB05 | [5 empty] | TBF03 | 27 | 28 |  |  | 70PAB40AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-014
[5 empty] | 70CRB02 | FCS0705 | 3 | 8 | 15 | ADV551-P | SO | N | %Z038115 | [8 empty] | %Z038115 | DO |  | 70CRB05 | [5 empty] | TBF03 | 29 | 30
[5 empty] | 70CRB02 | FCS0705 | 3 | 8 | 16 | ADV551-P | SO | N | %Z038116 | [8 empty] | %Z038116 | DO |  | 70CRB05 | [5 empty] | TBF03 | 31 | 32
|  | 70LAB10AP021YB01 | 电动给水泵B液力耦合器直流润滑油泵启动指令 | Electrical feedwater pump Bcoupler DC lube oil pump start command | 70CRB02 | FCS0705 | 3 | 8 | 17 | ADV551-P | SO | N | %Z038117 | [8 empty] | %Z038117 | DO |  | 70CRB05 | [5 empty] | TBF03 | 33 | 34 |  | 220VDC | 70LAB10AP021 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-007
|  | 70LAB10AP021YB11 | 电动给水泵B液力耦合器直流润滑油泵停止指令 | Electrical feedwater pump Bcoupler DC lube oil pump stop command | 70CRB02 | FCS0705 | 3 | 8 | 18 | ADV551-P | SO | N | %Z038118 | [8 empty] | %Z038118 | DO |  | 70CRB05 | [5 empty] | TBF03 | 35 | 36 |  | 220VDC | 70LAB10AP021 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-007
|  | 70LAB10AP022YB01 | 电动给水泵B液力耦合器交流润滑油泵启动指令 | Electrical feedwater pump Bcoupler AC lube oil pump start command | 70CRB02 | FCS0705 | 3 | 8 | 19 | ADV551-P | SO | N | %Z038119 | [8 empty] | %Z038119 | DO |  | 70CRB05 | [5 empty] | TBF03 | 37 | 38 |  |  | 70LAB10AP022 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-007
|  | 70LAB10AP022YB11 | 电动给水泵B液力耦合器交流润滑油泵停止指令 | Electrical feedwater pump Bcoupler AC lube oil pump stop command | 70CRB02 | FCS0705 | 3 | 8 | 20 | ADV551-P | SO | N | %Z038120 | [8 empty] | %Z038120 | DO |  | 70CRB05 | [5 empty] | TBF03 | 39 | 40 |  |  | 70LAB10AP022 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-007
|  | 70MAG12AA012YB01 | 真空泵A入口气动阀打开指令 | Vacuum pump A inlet PV open command | 70CRB02 | FCS0705 | 3 | 8 | 21 | ADV551-P | SO | N | %Z038121 | [8 empty] | %Z038121 | DO |  | 70CRB05 | [5 empty] | TBF03 | 41 | 42 |  |  | 70MAG12GH002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
|  | 70MAG12AA012YB11 | 真空泵A入口气动阀关闭指令 | Vacuum pump A inlet PV close command | 70CRB02 | FCS0705 | 3 | 8 | 22 | ADV551-P | SO | N | %Z038122 | [8 empty] | %Z038122 | DO |  | 70CRB05 | [5 empty] | TBF03 | 43 | 44 |  |  | 70MAG12GH002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
|  | 70MAG12AA003YB01 | 真空泵A分离罐补水电磁阀打开/关闭指令 | Vacuum pump A separator water supply SV open/close command | 70CRB02 | FCS0705 | 3 | 8 | 23 | ADV551-P | SO | N | %Z038123 | [8 empty] | %Z038123 | DO |  | 70CRB05 | [5 empty] | TBF03 | 45 | 46 |  |  | 70MAG12GH002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
|  | 70MAG12AA001YB01 | 真空泵A入口电动门打开指令 | Vacuum pump A inlet MOV open command | 70CRB02 | FCS0705 | 3 | 8 | 24 | ADV551-P | SO | N | %Z038124 | [8 empty] | %Z038124 | DO |  | 70CRB05 | [5 empty] | TBF03 | 47 | 48 |  |  | 70MAG12AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003
|  | 70MAG12AA001YB11 | 真空泵A入口电动门关闭指令 | Vacuum pump A inlet MOV close command | 70CRB02 | FCS0705 | 3 | 8 | 25 | ADV551-P | SO | N | %Z038125 | [8 empty] | %Z038125 | DO |  | 70CRB05 | [5 empty] | TBF03 | 49 | 50 |  |  | 70MAG12AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003
|  | 70MAG12AP001YB01 | 真空泵A启动指令 | Vacuum pump A start command | 70CRB02 | FCS0705 | 3 | 8 | 26 | ADV551-P | SO | N | %Z038126 | [8 empty] | %Z038126 | DO |  | 70CRB05 | [5 empty] | TBF03 | 51 | 52 |  |  | 70MAG12AP001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003
|  | 70MAG12AP001YB11 | 真空泵A停止指令 | Vacuum pump A stop command | 70CRB02 | FCS0705 | 3 | 8 | 27 | ADV551-P | SO | N | %Z038127 | [8 empty] | %Z038127 | DO |  | 70CRB05 | [5 empty] | TBF03 | 53 | 54 |  |  | 70MAG12AP001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003
|  | 70MAG10AA001YB01 | 真空泵破坏电动门打开指令 | Vacuum break MOV open command | 70CRB02 | FCS0705 | 3 | 8 | 28 | ADV551-P | SO | N | %Z038128 | [8 empty] | %Z038128 | DO |  | 70CRB05 | [5 empty] | TBF03 | 55 | 56 |  |  | 70MAG10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003
|  | 70MAG10AA001YB11 | 真空泵破坏电动门关闭指令 | Vacuum break MOV close command | 70CRB02 | FCS0705 | 3 | 8 | 29 | ADV551-P | SO | N | %Z038129 | [8 empty] | %Z038129 | DO |  | 70CRB05 | [5 empty] | TBF03 | 57 | 58 |  |  | 70MAG10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003
[5 empty] | 70CRB02 | FCS0705 | 3 | 8 | 30 | ADV551-P | SO | N | %Z038130 | [8 empty] | %Z038130 | DO |  | 70CRB05 | [5 empty] | TBF03 | 59 | 60
[5 empty] | 70CRB02 | FCS0705 | 3 | 8 | 31 | ADV551-P | SO | N | %Z038131 | [8 empty] | %Z038131 | DO |  | 70CRB05 | [5 empty] | TBF03 | 61 | 62
[5 empty] | 70CRB02 | FCS0705 | 3 | 8 | 32 | ADV551-P | SO | N | %Z038132 | [8 empty] | %Z038132 | DO |  | 70CRB05 | [5 empty] | TBF03 | 63 | 64
|  | 70LCA20AA003YB01 | 凝结水泵C出口电动阀打开指令 | Condensate pump C outlet MOV open command | 70CRB02 | FCS0705 | 4 | 8 | 1 | ADV551-P | SO | N | %Z048101 | [8 empty] | %Z048101 | DO |  | 70CRB05 | [5 empty] | TBG03 | 1 | 2 |  |  | 70LCA20AA003 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70LCA20AA003YB11 | 凝结水泵C出口电动阀关闭指令 | Condensate pump C outlet MOV close command | 70CRB02 | FCS0705 | 4 | 8 | 2 | ADV551-P | SO | N | %Z048102 | [8 empty] | %Z048102 | DO |  | 70CRB05 | [5 empty] | TBG03 | 3 | 4 |  |  | 70LCA20AA003 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70LCB10AP003YB01 | 凝结水泵C启动指令 | Condensate pump C start command | 70CRB02 | FCS0705 | 4 | 8 | 3 | ADV551-P | SO | N | %Z048103 | [8 empty] | %Z048103 | DO |  | 70CRB05 | [5 empty] | TBG03 | 5 | 6 |  | 220VDC | 70LCB10AP003 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-008
|  | 70LCB10AP003YB11 | 凝结水泵C停止指令 | Condensate pump C stop command | 70CRB02 | FCS0705 | 4 | 8 | 4 | ADV551-P | SO | N | %Z048104 | [8 empty] | %Z048104 | DO |  | 70CRB05 | [5 empty] | TBG03 | 7 | 8 |  | 220VDC | 70LCB10AP003 | NO | DO | [8 empty] | SCS | U | 220VDC | K0204-008
|  | 70LCA30AA402YB01 | 凝结水有压放水电动阀打开指令 | Condensate water pressure drain MOV open command | 70CRB02 | FCS0705 | 4 | 8 | 5 | ADV551-P | SO | N | %Z048105 | [8 empty] | %Z048105 | DO |  | 70CRB05 | [5 empty] | TBG03 | 9 | 10 |  |  | 70LCA30AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70LCA30AA402YB11 | 凝结水有压放水电动阀关闭指令 | Condensate water pressure drain MOV close command | 70CRB02 | FCS0705 | 4 | 8 | 6 | ADV551-P | SO | N | %Z048106 | [8 empty] | %Z048106 | DO |  | 70CRB05 | [5 empty] | TBG03 | 11 | 12 |  |  | 70LCA30AA402 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70PAB10AA001YB01 | B侧凝汽器循环水进水电动阀打开指令 | Inlet water MOV of condenser by side B open command | 70CRB02 | FCS0705 | 4 | 8 | 7 | ADV551-P | SO | N | %Z048107 | [8 empty] | %Z048107 | DO |  | 70CRB05 | [5 empty] | TBG03 | 13 | 14 |  |  | 70PAB10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-014
|  | 70PAB10AA001YB11 | B侧凝汽器循环水进水电动阀关闭指令 | Inlet water MOV of condenser by side B close command | 70CRB02 | FCS0705 | 4 | 8 | 8 | ADV551-P | SO | N | %Z048108 | [8 empty] | %Z048108 | DO |  | 70CRB05 | [5 empty] | TBG03 | 15 | 16 |  |  | 70PAB10AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-014
|  | 70PAB30AA001YB01 | B侧凝汽器循环水出水电动阀打开指令 | Outlet water MOV of condenser by side B open command | 70CRB02 | FCS0705 | 4 | 8 | 9 | ADV551-P | SO | N | %Z048109 | [8 empty] | %Z048109 | DO |  | 70CRB05 | [5 empty] | TBG03 | 17 | 18 |  |  | 70PAB30AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-014
|  | 70PAB30AA001YB11 | B侧凝汽器循环水出水电动阀关闭指令 | Outlet water MOV of condenser by side B close command | 70CRB02 | FCS0705 | 4 | 8 | 10 | ADV551-P | SO | N | %Z048110 | [8 empty] | %Z048110 | DO |  | 70CRB05 | [5 empty] | TBG03 | 19 | 20 |  |  | 70PAB30AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-014
|  | 70LAA20AA002YB01 | 除氧器放水电动阀打开指令 | Deaerator discharge MOV open command | 70CRB02 | FCS0705 | 4 | 8 | 11 | ADV551-P | SO | N | %Z048111 | [8 empty] | %Z048111 | DO |  | 70CRB05 | [5 empty] | TBG03 | 21 | 22 |  |  | 70LAA20AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70LAA20AA002YB11 | 除氧器放水电动阀关闭指令 | Deaerator discharge MOV close command | 70CRB02 | FCS0705 | 4 | 8 | 12 | ADV551-P | SO | N | %Z048112 | [8 empty] | %Z048112 | DO |  | 70CRB05 | [5 empty] | TBG03 | 23 | 24 |  |  | 70LAA20AA002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-008
|  | 70QCD12AM001YB01 | 2#氨溶液箱搅拌机启动/停止指令 | 2# ammonia solution tank agitator start/stop command | 70CRB02 | FCS0705 | 4 | 8 | 13 | ADV551-P | SO | N | %Z048113 | [8 empty] | %Z048113 | DO |  | 70CRB05 | [5 empty] | TBG03 | 25 | 26 |  |  | 70QCD10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCD12AP001YB01 | 2#给水氨计量泵启动/停止指令 | 2# feed water ammonia metering pump start/stop command | 70CRB02 | FCS0705 | 4 | 8 | 14 | ADV551-P | SO | N | %Z048114 | [8 empty] | %Z048114 | DO |  | 70CRB05 | [5 empty] | TBG03 | 27 | 28 |  |  | 70QCD10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
|  | 70QCA12AM001YB01 | 2#联氨溶液箱搅拌机启动/停止指令 | 2# hydrazine solution tank agitator start/stop command | 70CRB02 | FCS0705 | 4 | 8 | 15 | ADV551-P | SO | N | %Z048115 | [8 empty] | %Z048115 | DO |  | 70CRB05 | [5 empty] | TBG03 | 29 | 30 |  |  | 70QCA10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCA12AP001YB01 | 2#给水联氨计量泵启动/停止指令 | 2# feed water hydrazine metering pump start/stop command | 70CRB02 | FCS0705 | 4 | 8 | 16 | ADV551-P | SO | N | %Z048116 | [8 empty] | %Z048116 | DO |  | 70CRB05 | [5 empty] | TBG03 | 31 | 32 |  |  | 70QCA10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
|  | 70QCC12AM001YB01 | 2#磷酸盐溶液箱搅拌机启动/停止指令 | 2# phosphate solution tank agitator start/stop command | 70CRB02 | FCS0705 | 4 | 8 | 17 | ADV551-P | SO | N | %Z048117 | [8 empty] | %Z048117 | DO |  | 70CRB05 | [5 empty] | TBG03 | 33 | 34 |  |  | 70QCC10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70QCC12AP001YB01 | 2#磷酸盐计量泵启动/停止指令 | 2# phosphate metering pump start/stop command | 70CRB02 | FCS0705 | 4 | 8 | 18 | ADV551-P | SO | N | %Z048118 | [8 empty] | %Z048118 | DO |  | 70CRB05 | [5 empty] | TBG03 | 35 | 36 |  |  | 70QCC10GH001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
|  | 70MAG11AA012YB01 | 真空泵B入口气动阀打开指令 | Vacuum pump B inlet PV open command | 70CRB02 | FCS0705 | 4 | 8 | 19 | ADV551-P | SO | N | %Z048119 | [8 empty] | %Z048119 | DO |  | 70CRB05 | [5 empty] | TBG03 | 37 | 38 |  |  | 70MAG11GH002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
|  | 70MAG11AA012YB11 | 真空泵B入口气动阀关闭指令 | Vacuum pump B inlet PV close command | 70CRB02 | FCS0705 | 4 | 8 | 20 | ADV551-P | SO | N | %Z048120 | [8 empty] | %Z048120 | DO |  | 70CRB05 | [5 empty] | TBG03 | 39 | 40 |  |  | 70MAG11GH002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
|  | 70MAG11AA003YB01 | 真空泵B分离罐补水电磁阀打开/关闭指令 | Vacuum pump B separator water supply SV open/close command | 70CRB02 | FCS0705 | 4 | 8 | 21 | ADV551-P | SO | N | %Z048121 | [8 empty] | %Z048121 | DO |  | 70CRB05 | [5 empty] | TBG03 | 41 | 42 |  |  | 70MAG11GH002 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
|  | 70MAG11AA001YB01 | 真空泵B入口电动门打开指令 | Vacuum pump B inlet MOV open command | 70CRB02 | FCS0705 | 4 | 8 | 22 | ADV551-P | SO | N | %Z048122 | [8 empty] | %Z048122 | DO |  | 70CRB05 | [5 empty] | TBG03 | 43 | 44 |  |  | 70MAG11AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003
|  | 70MAG11AA001YB11 | 真空泵B入口电动门关闭指令 | Vacuum pump B inlet MOV close command | 70CRB02 | FCS0705 | 4 | 8 | 23 | ADV551-P | SO | N | %Z048123 | [8 empty] | %Z048123 | DO |  | 70CRB05 | [5 empty] | TBG03 | 45 | 46 |  |  | 70MAG11AA001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003
|  | 70MAG11AP001YB01 | 真空泵B启动指令 | Vacuum pump B start command | 70CRB02 | FCS0705 | 4 | 8 | 24 | ADV551-P | SO | N | %Z048124 | [8 empty] | %Z048124 | DO |  | 70CRB05 | [5 empty] | TBG03 | 47 | 48 |  |  | 70MAG11AP001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003
|  | 70MAG11AP001YB11 | 真空泵B停止指令 | Vacuum pump B stop command | 70CRB02 | FCS0705 | 4 | 8 | 25 | ADV551-P | SO | N | %Z048125 | [8 empty] | %Z048125 | DO |  | 70CRB05 | [5 empty] | TBG03 | 49 | 50 |  |  | 70MAG11AP001 | NO | DO | [8 empty] | SCS | U | 220VAC | K0204-003
[5 empty] | 70CRB02 | FCS0705 | 4 | 8 | 26 | ADV551-P | SO | N | %Z048126 | [8 empty] | %Z048126 | DO |  | 70CRB05 | [5 empty] | TBG03 | 51 | 52
[5 empty] | 70CRB02 | FCS0705 | 4 | 8 | 27 | ADV551-P | SO | N | %Z048127 | [8 empty] | %Z048127 | DO |  | 70CRB05 | [5 empty] | TBG03 | 53 | 54
[5 empty] | 70CRB02 | FCS0705 | 4 | 8 | 28 | ADV551-P | SO | N | %Z048128 | [8 empty] | %Z048128 | DO |  | 70CRB05 | [5 empty] | TBG03 | 55 | 56
[5 empty] | 70CRB02 | FCS0705 | 4 | 8 | 29 | ADV551-P | SO | N | %Z048129 | [8 empty] | %Z048129 | DO |  | 70CRB05 | [5 empty] | TBG03 | 57 | 58
[5 empty] | 70CRB02 | FCS0705 | 4 | 8 | 30 | ADV551-P | SO | N | %Z048130 | [8 empty] | %Z048130 | DO |  | 70CRB05 | [5 empty] | TBG03 | 59 | 60
[5 empty] | 70CRB02 | FCS0705 | 4 | 8 | 31 | ADV551-P | SO | N | %Z048131 | [8 empty] | %Z048131 | DO |  | 70CRB05 | [5 empty] | TBG03 | 61 | 62
[5 empty] | 70CRB02 | FCS0705 | 4 | 8 | 32 | ADV551-P | SO | N | %Z048132 | [8 empty] | %Z048132 | DO |  | 70CRB05 | [5 empty] | TBG03 | 63 | 64

## IOlist
| PID_TAG | COMMENT(Chinese) | COMMENT | Source | Type | I/O |  | ENG_UNITS | HHH | HH | H | L | LL | LLL | LOG | SOE | DCS Subfunction | Power Supply | Excitation Voltage | Drawing No. | Chinese Remark | English Remark
1 | 70CFA01YB03 | 相对振动报警 | Relative vibration alarm | 70CFA01 | NO | DI | [10 empty] | DAS | D |  | K0203-001 | 汽机TSI控制柜 | Turbine TSI control cabinet
2 | 70CFA01YB05 | 轴向位移报警 | Rotor position alarm | 70CFA01 | NO | DI | [10 empty] | DAS | D |  | K0203-001 | 汽机TSI控制柜 | Turbine TSI control cabinet
3 | 70CFA01YB07 | 差胀报警 | Differential expansion alarm | 70CFA01 | NO | DI | [10 empty] | DAS | D |  | K0203-001 | 汽机TSI控制柜 | Turbine TSI control cabinet
4 | 70CFA01YB09 | 偏心报警 | Eccentricity alarm | 70CFA01 | NO | DI | [10 empty] | DAS | D |  | K0203-001 | 汽机TSI控制柜 | Turbine TSI control cabinet
5 | 70CFA01YB10 | 零转速报警 | Zero rotation speed alarm | 70CFA01 | NO | DI | [10 empty] | DAS | D |  | K0203-001 | 汽机TSI控制柜 | Turbine TSI control cabinet
6 | 70MKA20CT101 | 6#定子槽内线棒层间温度 | Temperature between stator bars in 6# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
7 | 70MKA20CT102 | 12#定子槽内线棒层间温度 | Temperature between stator bars in 12# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
8 | 70MKA20CT103 | 18#定子槽内线棒层间温度 | Temperature between stator bars in 18# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
9 | 70MKA20CT104 | 24#定子槽内线棒层间温度 | Temperature between stator bars in 24# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
10 | 70MKA20CT105 | 30#定子槽内线棒层间温度 | Temperature between stator bars in 30# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
11 | 70MKA20CT106 | 36#定子槽内线棒层间温度 | Temperature between stator bars in 36# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
12 | 70MKA20CT107 | 42#定子槽内线棒层间温度 | Temperature between stator bars in 42# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
13 | 70MKA20CT108 | 48#定子槽内线棒层间温度 | Temperature between stator bars in 48# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
14 | 70MKA20CT109 | 54#定子槽内线棒层间温度 | Temperature between stator bars in 54# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
15 | 70MKA20CT110 | 60#定子槽内线棒层间温度 | Temperature between stator bars in 60# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
16 | 70MKA20CT111 | 66#定子槽内线棒层间温度 | Temperature between stator bars in 66# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
17 | 70MKA20CT112 | 72#定子槽内线棒层间温度 | Temperature between stator bars in 72# slot | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
18 | 70MKA34CT101 | 出线端定子铁心轭部温度1 | Temperature 1 of outlet end stator core yoke | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
19 | 70MKA34CT102 | 出线端定子铁心齿部温度1 | Temperature 1 of outlet end stator core tooth | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
20 | 70MKA34CT103 | 出线端定子铁心轭部温度2 | Temperature 2 of outlet end stator core yoke | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
21 | 70MKA34CT104 | 出线端定子铁心齿部温度2 | Temperature 2 of outlet end stator core tooth | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
22 | 70MKA34CT105 | 出线端定子铁心轭部温度3 | Temperature 3 of outlet end stator core yoke | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
23 | 70MKA34CT106 | 出线端定子铁心齿部温度3 | Temperature 3 of outlet end stator core tooth | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
24 | 70MKA34CT107 | 非出线端定子铁心轭部温度1 | Temperature 1 of non-outlet end stator core yoke | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
25 | 70MKA34CT108 | 非出线端定子铁心齿部温度1 | Temperature 1 of non-outlet end stator core tooth | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
26 | 70MKA34CT109 | 非出线端定子铁心轭部温度2 | Temperature 2 of non-outlet end stator core yoke | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
27 | 70MKA34CT110 | 非出线端定子铁心齿部温度2 | Temperature 2 of non-outlet end stator core tooth | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
28 | 70MKA34CT111 | 非出线端定子铁心轭部温度3 | Temperature 3 of non-outlet end stator core yoke | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
29 | 70MKA34CT112 | 非出线端定子铁心齿部温度3 | Temperature 3 of non-outlet end stator core tooth | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
30 | 70MKA38CT101 | 出线端齿压板温度1 | Temperature 1 of outlet end finger plate | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
31 | 70MKA38CT102 | 出线端齿压板温度2 | Temperature 2 of outlet end finger plate | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
32 | 70MKA38CT103 | 非出线端齿压板温度1 | Temperature 1 of non-outlet end finger plate | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
33 | 70MKA38CT104 | 非出线端齿压板温度2 | Temperature 2 of non-outlet end finger plate | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
34 | 70MKA75CT101 | 出线端冷风温度 | Temperature of outlet end cold air | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
35 | 70MKA75CT102 | 出线端热风温度 | Temperature of outlet end hot air | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
36 | 70MKA75CT103 | 本体段冷风温度 | Temperature of body section cold air | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
37 | 70MKA75CT104 | 非出线端热风温度 | Temperature of non-outlet end hot air | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
38 | 70MKA75CT105 | 非出线端冷风温度 | Temperature of non-outlet end cold air | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
39 | 70MKA75CT106 | 刷架热风温度 | Brush carrier hot air temperature | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
40 | 70MKA75CT107 | 刷架冷风温度 | Brush carrier cold air temperature | 70MKA20GH001 | PT100 | RTD | 0～180 | ℃ | [8 empty] | SCS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
41 | 70MKA75CE101A | 发电机漏液检测1 | Generator leakage detection 1 | 70MKA20GH001 | 4～20mA | AI | 0～500 | MΩ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
42 | 70MKA75CE101B | 发电机漏液检测2 | Generator leakage detection 2 | 70MKA20GH001 | 4～20mA | AI | 0～500 | MΩ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
43 | 70MKA75CE101C | 发电机漏液检测3 | Generator leakage detection 3 | 70MKA20GH001 | 4～20mA | AI | 0～500 | MΩ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
44 | 70MKA75CE101D | 发电机漏液检测4 | Generator leakage detection 4 | 70MKA20GH001 | 4～20mA | AI | 0～500 | MΩ | [8 empty] | DAS | D |  | K0203-002 | 发电机出线板 | Generator outlet flange
45 | 70MAX01CP013 | 1#冷油器回油滤器差压高 | 1# oil cooler return oil differential pressure H | 70MAX01GC001 | NO | DI | 2 | bar | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER | bar: H
46 | 70MAX01CP014 | 2#冷油器回油滤器差压高 | 2# oil cooler return oil differential pressure H | 70MAX01GC001 | NO | DI | 2 | bar | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER | bar: H
47 | 70MAX01CT201 | EH油箱油温 | EH oil tank oil temperature | 70MAX01GC001 | PT100 | RTD | 0～100 | ℃ | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
48 | 70MAX01CL101 | EH油箱油位 | EH oil tank oil level | 70MAX01GC001 | 4～20mA | AI | 0～1 | m | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
49 | 70MAX01CL001H | EH油箱油位高 | EH oil tank oil level H | 70MAX01GC001 | NO | DI | 878.4 | mm | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER | bar: H
50 | 70MAX01CL001LL | EH油箱油位低低 | EH oil tank oil level LL | 70MAX01GC001 | NO | DI | 259.4 | mm | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER | bar: LL
51 | 70MAX01CL002L | EH油箱油位低 | EH oil tank oil level L | 70MAX01GC001 | NO | DI | 402.4 | mm | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER | bar: L
52 | 70MAX01CL002LLL | EH油箱油位低低低 | EH oil tank oil level LLL | 70MAX01GC001 | NO | DI | 156.4 | mm | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER | bar: LLL
53 | 70MAX01CP004 | 1#冷油器前压力 | 1# oil cooler inlet pressure | 70MAX01GC001 | NO | DI | 0.3 | bar | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
54 | 70MAX01CP005 | 2#冷油器前压力 | 2# oil cooler inlet pressure | 70MAX01GC001 | NO | DI | 0.3 | bar | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
55 | 70MAX01CP011 | 1#控制油泵滤器差压高 | 1# control oil pump filter differential pressure H | 70MAX01GC001 | NO | DI | 5 | bar | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER | bar: H
56 | 70MAX01CP012 | 2#控制油泵滤器差压高 | 2# control oil pump filter differential pressure H | 70MAX01GC001 | NO | DI | 5 | bar | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER | bar: H
57 | 70MAX01CP101 | 1#EH油泵出口油压 | 1# EH oil pump outlet oil Pressure | 70MAX01GC001 | 4～20mA | AI | 0～25 | Mpa | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
58 | 70MAX01CP102 | 2#EH油泵出口油压 | 2# EH oil pump outlet oil Pressure | 70MAX01GC001 | 4～20mA | AI | 0～25 | Mpa | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
59 | 70MAX01CP103 | EH油泵出口母管油压 | EH oil pump outlet main pipe oil pressure | 70MAX01GC001 | 4～20mA | AI | 0～25 | Mpa | [8 empty] | SCS | D |  | K0203-003 | EH油接线盒ER | EH oil junction box ER
60 | 70MAX01AP001YB01 | 1# EH油泵启动指令 | 1# EH oil pump start command | 70MAX01GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
61 | 70MAX01AP001YB11 | 1# EH油泵停止指令 | 1# EH oil pump stop command | 70MAX01GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
62 | 70MAX01AP001XB01 | 1# EH油泵运行状态反馈 | 1# EH oil pump running status feedback | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
63 | 70MAX01AP001XB11 | 1# EH油泵停止状态反馈 | 1# EH oil pump stopped status feedback | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
64 | 70MAX01AP001XB31 | 1# EH油泵电源故障 | 1# EH oil pump power fault | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
65 | 70MAX01AP001XQ01 | 1# EH油泵电流 | 1# EH oil pump current | 70MAX01GH001 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
66 | 70MAX01AP002YB01 | 2# EH油泵启动指令 | 2# EH oil pump start command | 70MAX01GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
67 | 70MAX01AP002YB11 | 2# EH油泵停止指令 | 2# EH oil pump stop command | 70MAX01GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
68 | 70MAX01AP002XB01 | 2# EH油泵运行状态反馈 | 2# EH oil pump running status feedback | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
69 | 70MAX01AP002XB11 | 2# EH油泵停止状态反馈 | 2# EH oil pump stopped status feedback | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
70 | 70MAX01AP002XB31 | 2# EH油泵电源故障 | 2# EH oil pump power fault | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
71 | 70MAX01AP002XQ01 | 2# EH油泵电流 | 2# EH oil pump current | 70MAX01GH001 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
72 | 70MAX01AP011YB01 | 1# EH油循环泵启动指令 | 1# EH oil circulating pump start command | 70MAX01GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
73 | 70MAX01AP011YB11 | 1# EH油循环泵停止指令 | 1# EH oil circulating pump stop command | 70MAX01GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
74 | 70MAX01AP011XB01 | 1# EH油循环泵运行状态反馈 | 1# EH oil circulating pump running status feedback | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
75 | 70MAX01AP011XB11 | 1# EH油循环泵停止状态反馈 | 1# EH oil circulating pump stopped status feedback | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
76 | 70MAX01AP011XB31 | 1# EH油循环泵电源故障 | 1# EH oil circulating pump power fault | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
77 | 70MAX01AP012YB01 | 2# EH油循环泵启动指令 | 2# EH oil circulating pump start command | 70MAX01GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
78 | 70MAX01AP012YB11 | 2# EH油循环泵停止指令 | 2# EH oil circulating pump stop command | 70MAX01GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
79 | 70MAX01AP012XB01 | 2# EH油循环泵运行状态反馈 | 2# EH oil circulating pump running status feedback | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
80 | 70MAX01AP012XB11 | 2# EH油循环泵停止状态反馈 | 2# EH oil circulating pump stopped status feedback | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
81 | 70MAX01AP012XB31 | 2# EH油循环泵电源故障 | 2# EH oil circulating pump power fault | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
82 | 70MAX01AH001YB01 | EH油箱电加热器启动指令 | EH oil tank heater start command | 70MAX01GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
83 | 70MAX01AH001YB11 | EH油箱电加热器停止指令 | EH oil tank heater stop command | 70MAX01GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
84 | 70MAX01AH001XB01 | EH油箱电加热器运行状态反馈 | EH oil tank heater running status feedback | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
85 | 70MAX01AH001XB11 | EH油箱电加热器停止状态反馈 | EH oil tank heater stopped status feedback | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
86 | 70MAX01AH001XB31 | EH油箱电加热器电源故障 | EH oil tank heater power fault | 70MAX01GH001 | NO | DI | [10 empty] | SCS | D |  | K0203-003 | EH油泵控制柜 | EH oil pump control cabinet
87 | 70CJJ01YQ04 | 负荷设定值 | Load setpoint | 70CJJ01 | 4～20mA | AI |  | MW | [8 empty] | MCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
88 | 70CJJ01YQ05 | 实际功率 | Actual load | 70CJJ01 | 4～20mA | AI |  | MW | [8 empty] | MCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
89 | 70CJJ01YQ06 | 实际转速 | Actual speed | 70CJJ01 | 4～20mA | AI | 0～3500 | rpm | [8 empty] | MCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
90 | 70CJJ01XQ04 | 遥控负荷给定 | Remote control load given | 70CJJ01 | 4～20mA | AO |  | MW | [8 empty] | MCS | D |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
91 | 70CJJ01XB02 | 遥控功率请求 | Remote control request | 70CJJ01 | NO | DO | [10 empty] | SCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
92 | 70CJJ01XB03 | 投入孤网运行模式 | Into the isolated network operation mode | 70CJJ01 | NO | DO | [10 empty] | SCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
93 | 70CJJ01XB05 | 快速降负荷 | Rapid load shedding | 70CJJ01 | NO | DO | [10 empty] | SCS | U |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
94 | 70CJJ01YB02 | 遥控功率已投 | Remote control power input | 70CJJ01 | NO | DI | [10 empty] | SCS | D |  | K0203-004 | 汽机DEH控制柜 | Turbine DEH control cabinet
95 | 70CAA01YB01 | 真空低遮断 | Low acuum interruption | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
96 | 70CAA01YB02 | 润滑油压低遮断 | Lube oil pressure low trip | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
97 | 70CAA01YB03 | 机头停机按钮遮断 | Emergency stop of turbine head button trip | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
98 | 70CAA01YB04 | 操作台紧急停机按钮遮断 | Console emergency trip turbine button trip | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
99 | 70CAA01YB05 | 电超速遮断 | Electric overspeed trip | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
100 | 70CAA01YB06 | 排汽温度遮断 | Exhaust temperature trip | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
101 | 70CAA01YB07 | 相对振动大遮断 | Relative vibration H trip | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
102 | 70CAA01YB08 | 轴向位移大遮断 | Rotor position H trip | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
103 | 70CAA01YB09 | 差胀大遮断 | Differential expansion H trip | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
104 | 70CAA01YB10 | 画面手动遮断 | Manual trip | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
105 | 70CAA01YB11 | 轴瓦温度遮断 | Bearing temperature H trip | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
106 | 70CAA01YB12 | 遥控遮断1 | Remote trip 1 | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
107 | 70CAA01YB13 | 遥控遮断2 | Remote trip 2 | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
108 | 70CAA01YB14 | 遥控遮断3 | Remote trip 3 | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
109 | 70CAA01YB15 | 遥控遮断4 | Remote trip 4 | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
110 | 70CAA01YB17 | 汽机已遮断2 | Turbine tripped 2 | 70CAA01 | NO | DI | [10 empty] | SCS | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
111 | 70CAA01YB18 | 汽机已遮断3 | Turbine tripped 3 | 70CAA01 | NO | DI | [10 empty] | SCS | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
112 | 70CAA01YB19 | 汽机已遮断4 | Turbine tripped 4 | 70CAA01 | NO | DI | [10 empty] | SCS | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
113 | 70CAA01YB20 | 停机扩展至DCS | Trip expansion to DCS | 70CAA01 | NO | DI | [10 empty] | SCS | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet
114 | 70CAA01YB21 | 停机扩展至SOE | Trip expansion to SOE | 70CAA01 | NO | DI | [10 empty] | SOE | D |  | K0203-004 | 汽机ETS控制柜 | Turbine ETS control cabinet | bar: SOE
115 | 70MAA11CG101B | 主汽门(左)全关#2 | MSV(left) full close #2 | 70MAA11GC001 | NO | DI | [10 empty] | SCS | D |  | K0203-004 | 主汽门油动机(左)接线盒 | MSV actuator (left) junction box
116 | 70MAA21CG101B | 主汽门(右)全关#2 | MSV(right) full close #2 | 70MAA21GC001 | NO | DI | [10 empty] | SCS | D |  | K0203-004 | 主汽门油动机(右)接线盒 | MSV actuator (right) junction box
117 | 70MAV31CP101 | 1#顶轴油泵出口压力 | 1# jacking oil pump outlet pressure | 70MAV01GC001 | 4～20mA | AI | 0～25 | Mpa | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
118 | 70MAV32CP101 | 2#顶轴油泵出口压力 | 2# jacking oil pump outlet pressure | 70MAV01GC001 | 4～20mA | AI | 0～25 | Mpa | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
119 | 70MAV35CP016H | 顶轴油滤油器差压高 | Jacking oil filter differential pressure H | 70MAV01GC001 | NO | DI | [10 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R | bar: H
120 | 70MAV35CP101 | 顶轴油泵母管出口压力 | Jacking oil pump main outlet pressure | 70MAV01GC001 | 4～20mA | AI | 0～25 | Mpa | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
121 | 70MAV35CT101 | 顶轴油泵母管出口温度 | Jacking oil pump main outlet temperature | 70MAV01GC001 | PT100 | RTD | 0～100 | ℃ | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
122 | 70MAV24CP001L | 直流油泵出口压力低 | DC oil pump outlet pressure L | 70MAV01GC001 | NO | DI | 0.22 | Mpa | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R | bar: L
123 | 70MAV21CP005L | 1#主油泵出口压力低 | 1# main oil pump outlet pressure L | 70MAV01GC001 | NO | DI | 0.53 | Mpa | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R | bar: L
124 | 70MAV21CP006L | 2#主油泵出口压力低 | 2# main oil pump outlet pressure L | 70MAV01GC001 | NO | DI | 0.53 | Mpa | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R | bar: L
125 | 70MAV10CT011L | 润滑油箱温度低 | Lube oil tank temperature L | 70MAV01GC001 | NO | DI | 35 | ℃ | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R | bar: L
126 | 70MAV10CT101 | 润滑油箱温度 | Lube oil tank temperature | 70MAV01GC001 | PT100 | RTD | 0～100 | ℃ | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
127 | 70MAV21CP001L | 主油泵出口母管压力低 | Main oil pump outlet main pipe pressure L | 70MAV01GC001 | NO | DI | 0.5 | Mpa | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R | bar: L
128 | 70MAV82CP101 | 排油烟管道压力 | Oil mist exhaust pressure | 70MAV01GC001 | 4～20mA | AI | 0～0.6 | Mpa | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
129 | 70MAV42CP012L | 润滑油母管压力低（直流试验） | Lube oil main pipe pressure L(DC test) | 70MAV01GC001 | NO | DI | [10 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R | bar: L
130 | 70MAV42CP019L | 润滑油母管压力低（交流试验） | Lube oil main pipe pressure L(AC test) | 70MAV01GC001 | NO | DI | [10 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R | bar: L
131 | 70MAV42CP013H | 润滑油滤油器差压高 | Lube oil filter differential pressure H | 70MAV01GC001 | NO | DI | 0.08 | Mpa | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R | bar: H
132 | 70MAV41CT101 | 冷油器出口母管温度 | Oil cooler outlet main pipe temperature | 70MAV01GC001 | PT100 | RTD | 0～100 | ℃ | [8 empty] | SCS | D |  | K0203-005 | 润滑油接线盒R | Lube oil junction box R
133 | 70MAV21AA321YB01 | 交流泵切换试验电磁阀打开/关闭指令 | AC pump xwitch test solenoid valve open/close command | 70MAV01GC001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005 | 润滑油接线盒R | Lube oil junction box R
134 | 70MAV42AA322YB01 | 母管油压低试验电磁阀（直流）打开/关闭指令 | Main pressure low test solenoid valve(DC) open/close command | 70MAV01GC001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005 | 润滑油接线盒R | Lube oil junction box R
135 | 70MAV42AA329YB01 | 母管油压低试验电磁阀（交流）打开/关闭指令 | Main pressure low test solenoid valve(AC) open/close command | 70MAV01GC001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005 | 润滑油接线盒R | Lube oil junction box R
136 | 70MAV24AP001YB01 | 直流油泵启动指令1 | DC oil pump start command 1 | 70MAV24AP001 | NO | DO | [10 empty] | SCS | U | 220VDC | K0203-005
137 | 70MAV24AP001YB11 | 直流油泵停止指令 | DC oil pump stop command | 70MAV24AP001 | NO | DO | [10 empty] | SCS | U | 220VDC | K0203-005
138 | 70MAV24AP001XB01 | 直流油泵运行 | DC oil pump running | 70MAV24AP001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
139 | 70MAV24AP001XB11 | 直流油泵停止 | DC oil pump stopped | 70MAV24AP001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
140 | 70MAV24AP001XB12 | 直流油泵停止(SOE) | DC oil pump stopped(SOE) | 70MAV24AP001 | NO | SOE | [10 empty] | SOE | D |  | K0203-005 | bar: SOE
141 | 70MAV24AP001XB21 | 直流油泵远方控制允许 | DC oil pump remote control permitted | 70MAV24AP001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
142 | 70MAV24AP001XB31 | 直流油泵故障 | DC oil pump fault | 70MAV24AP001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
143 | 70MAV24AP001XQ01 | 直流油泵电流 | DC oil pump current | 70MAV24AP001 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0203-005
144 | 70MAV21AP021YB01 | 1#主油泵启动指令1 | 1# main oil pump start command 1 | 70MAV21AP021 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
145 | 70MAV21AP021YB11 | 1#主油泵停止指令 | 1# main oil pump stop command | 70MAV21AP021 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
146 | 70MAV21AP021XB01 | 1#主油泵运行 | 1# main oil pump running | 70MAV21AP021 | NO | DI | [10 empty] | SCS | D |  | K0203-005
147 | 70MAV21AP021XB11 | 1#主油泵停止 | 1# main oil pump stopped | 70MAV21AP021 | NC | DI | [10 empty] | SCS | D |  | K0203-005
148 | 70MAV21AP021XB12 | 1#主油泵停止(SOE) | 1# main oil pump stopped(SOE) | 70MAV21AP021 | NO | SOE | [10 empty] | SOE | D |  | K0203-005 | bar: SOE
149 | 70MAV21AP021XB21 | 1#主油泵远方控制允许 | 1# main oil pump remote control permitted | 70MAV21AP021 | NO | DI | [10 empty] | SCS | D |  | K0203-005
150 | 70MAV21AP021XB31 | 1#主油泵控制电源消失 | 1# main oil pump control circuit broken | 70MAV21AP021 | NC | DI | [10 empty] | SCS | D |  | K0203-005
151 | 70MAV21AP021XB32 | 1#主油泵故障输出 | 1# main oil pump fault output | 70MAV21AP021 | NC | DI | [10 empty] | SCS | D |  | K0203-005
152 | 70MAV21AP021XQ01 | 1#主油泵电流 | 1# main oil pump current | 70MAV21AP021 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0203-005
153 | 70MAV21AP022YB01 | 2#主油泵启动指令1 | 2# main oil pump start command 1 | 70MAV21AP021 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
154 | 70MAV21AP022YB11 | 2#主油泵停止指令 | 2# main oil pump stop command | 70MAV21AP021 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
155 | 70MAV21AP022XB01 | 2#主油泵运行 | 2# main oil pump running | 70MAV21AP021 | NO | DI | [10 empty] | SCS | D |  | K0203-005
156 | 70MAV21AP022XB11 | 2#主油泵停止 | 2# main oil pump stopped | 70MAV21AP021 | NC | DI | [10 empty] | SCS | D |  | K0203-005
157 | 70MAV21AP022XB12 | 2#主油泵停止(SOE) | 2# main oil pump stopped(SOE) | 70MAV21AP021 | NO | SOE | [10 empty] | SOE | D |  | K0203-005 | bar: SOE
158 | 70MAV21AP022XB21 | 2#主油泵远方控制允许 | 2# main oil pump remote control permitted | 70MAV21AP021 | NO | DI | [10 empty] | SCS | D |  | K0203-005
159 | 70MAV21AP022XB31 | 2#主油泵控制电源消失 | 2# main oil pump control circuit broken | 70MAV21AP021 | NC | DI | [10 empty] | SCS | D |  | K0203-005
160 | 70MAV21AP022XB32 | 2#主油泵故障输出 | 2# main oil pump fault output | 70MAV21AP021 | NC | DI | [10 empty] | SCS | D |  | K0203-005
161 | 70MAV21AP022XQ01 | 2#主油泵电流 | 2# main oil pump current | 70MAV21AP021 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0203-005
162 | 70MAV31AP001YB01 | 1#顶轴油泵启动指令 | 1# jacking oil pump start command | 70MAV31AP001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
163 | 70MAV31AP001YB11 | 1#顶轴油泵停止指令 | 1# jacking oil pump stop command | 70MAV31AP001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
164 | 70MAV31AP001XB01 | 1#顶轴油泵运行 | 1# jacking oil pump running | 70MAV31AP001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
165 | 70MAV31AP001XB11 | 1#顶轴油泵停止 | 1# jacking oil pump stopped | 70MAV31AP001 | NC | DI | [10 empty] | SCS | D |  | K0203-005
166 | 70MAV31AP001XB21 | 1#顶轴油泵远方控制允许 | 1# jacking oil pump remote control permitted | 70MAV31AP001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
167 | 70MAV31AP001XB31 | 1#顶轴油泵控制电源消失 | 1# jacking oil pump control circuit broken | 70MAV31AP001 | NC | DI | [10 empty] | SCS | D |  | K0203-005
168 | 70MAV31AP001XB32 | 1#顶轴油泵故障输出 | 1# jacking oil pump fault output | 70MAV31AP001 | NC | DI | [10 empty] | SCS | D |  | K0203-005
169 | 70MAV31AP001XQ01 | 1#顶轴油泵电流 | 1# jacking oil pump current | 70MAV31AP001 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0203-005
170 | 70MAV32AP001YB01 | 2#顶轴油泵启动指令 | 2# jacking oil pump start command | 70MAV32AP001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
171 | 70MAV32AP001YB11 | 2#顶轴油泵停止指令 | 2# jacking oil pump stop command | 70MAV32AP001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
172 | 70MAV32AP001XB01 | 2#顶轴油泵运行 | 2# jacking oil pump running | 70MAV32AP001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
173 | 70MAV32AP001XB11 | 2#顶轴油泵停止 | 2# jacking oil pump stopped | 70MAV32AP001 | NC | DI | [10 empty] | SCS | D |  | K0203-005
174 | 70MAV32AP001XB21 | 2#顶轴油泵远方控制允许 | 2# jacking oil pump remote control permitted | 70MAV32AP001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
175 | 70MAV32AP001XB31 | 2#顶轴油泵控制电源消失 | 2# jacking oil pump control circuit broken | 70MAV32AP001 | NC | DI | [10 empty] | SCS | D |  | K0203-005
176 | 70MAV32AP001XB32 | 2#顶轴油泵故障输出 | 2# jacking oil pump fault output | 70MAV32AP001 | NC | DI | [10 empty] | SCS | D |  | K0203-005
177 | 70MAV32AP001XQ01 | 2#顶轴油泵电流 | 2# jacking oil pump current | 70MAV32AP001 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0203-005
178 | 70MAV82AN001YB01 | 1#排烟风机启动指令 | 1# exhaust smoke fan start command | 70MAV82AN001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
179 | 70MAV82AN001YB11 | 1#排烟风机停止指令 | 1# exhaust smoke fan stop command | 70MAV82AN001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
180 | 70MAV82AN001XB01 | 1#排烟风机运行 | 1# exhaust smoke fan running | 70MAV82AN001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
181 | 70MAV82AN001XB11 | 1#排烟风机停止 | 1# exhaust smoke fan stopped | 70MAV82AN001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
182 | 70MAV82AN001XB21 | 1#排烟风机远方控制允许 | 1# exhaust smoke fan remote control permitted | 70MAV82AN001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
183 | 70MAV82AN001XB31 | 1#排烟风机控制电源消失 | 1# exhaust smoke fan control circuit broken | 70MAV82AN001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
184 | 70MAV82AN001XB32 | 1#排烟风机故障输出 | 1# exhaust smoke fan fault output | 70MAV82AN001 | NO | DI | [10 empty] | SCS | D |  | K0203-005
185 | 70MAV82AN002YB01 | 2#排烟风机启动指令 | 2# exhaust smoke fan start command | 70MAV82AN002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
186 | 70MAV82AN002YB11 | 2#排烟风机停止指令 | 2# exhaust smoke fan stop command | 70MAV82AN002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-005
187 | 70MAV82AN002XB01 | 2#排烟风机运行 | 2# exhaust smoke fan running | 70MAV82AN002 | NO | DI | [10 empty] | SCS | D |  | K0203-005
188 | 70MAV82AN002XB11 | 2#排烟风机停止 | 2# exhaust smoke fan stopped | 70MAV82AN002 | NO | DI | [10 empty] | SCS | D |  | K0203-005
189 | 70MAV82AN002XB21 | 2#排烟风机远方控制允许 | 2# exhaust smoke fan remote control permitted | 70MAV82AN002 | NO | DI | [10 empty] | SCS | D |  | K0203-005
190 | 70MAV82AN002XB31 | 2#排烟风机控制电源消失 | 2# exhaust smoke fan control circuit broken | 70MAV82AN002 | NO | DI | [10 empty] | SCS | D |  | K0203-005
191 | 70MAV82AN002XB32 | 2#排烟风机故障输出 | 2# exhaust smoke fan fault output | 70MAV82AN002 | NO | DI | [10 empty] | SCS | D |  | K0203-005
192 | 70MKD11CT101 | 发电机汽端轴承瓦温 | Generator bearing(turbine side) bush temperature | 70MKD11CT101 | PT100 | RTD | 0～200 | ℃ | [8 empty] | SCS | D |  | K0203-006
193 | 70MAV71CT103 | 发电机汽端轴承排油温度 | Generator bearing(turbine side) drain oil temperature | 70MAV71CT103 | PT100 | RTD | 0～200 | ℃ | [8 empty] | SCS | D |  | K0203-006
194 | 70MKD12CT101 | 发电机励端轴承瓦温 | Generator bearing(exciter side) bush temperature | 70MKD12CT101 | PT100 | RTD | 0～200 | ℃ | [8 empty] | SCS | D |  | K0203-006
195 | 70MAV71CT104 | 发电机励端轴承排油温度 | Generator bearing(exciter side) drain oil temperature | 70MAV71CT104 | PT100 | RTD | 0～200 | ℃ | [8 empty] | SCS | D |  | K0203-006
196 | 70MAV51AA012YB01 | 盘车装置入口电磁阀打开/关闭指令 | Turning gear inlet SV open/close command | 70MAV51AA012 | NO | DO | [10 empty] | SCS | U | 220VAC | K0203-007
197 | 70LBA10CP101 | 主蒸汽压力1（电动阀前） | Main steam pressure 1（before MOV） | 70LBA10CP101 | 4~20mA | AI | 0~16 | Mpa | [8 empty] | DAS | D |  | K0204-001
198 | 70LBA10CP102 | 主蒸汽压力2（电动阀前） | Main steam pressure 2（before MOV） | 70LBA10CP102 | 4~20mA | AI | 0~16 | Mpa | [8 empty] | DAS | D |  | K0204-001
199 | 70LBA11CP102 | 主汽门(左)前蒸汽压力2 | Steam pressure before MSV(left) | 70LBA11CP102 | 4~20mA | AI | 0~16 | Mpa | [8 empty] | DAS | D |  | K0204-001
200 | 70LBA10CT101 | 主蒸汽温度1(汽机侧) | Main steam temperature 1(turbine side) | 70LBA10CT101 | K | TC | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-001
201 | 70LBA10CT102 | 主蒸汽温度2(汽机侧) | Main steam temperature 2(turbine side) | 70LBA10CT102 | K | TC | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-001
202 | 70LBA10CT103 | 主蒸汽电动阀前疏水阀后温度 | Temperature after turbine main steam MOV front drain valve | 70LBA10CT103 | 4~20mA | AI | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-001
203 | 70LBA10CT104 | 汽机(左)进汽管道疏水阀后温度 | Temperature after turbine(left) main steam inlet pipe drain valve | 70LBA10CT104 | 4~20mA | AI | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-001
204 | 70LBA10CT105 | 汽机(右)进汽管道疏水阀后温度 | Temperature after turbine(right) main steam inlet pipe drain valve | 70LBA10CT105 | 4~20mA | AI | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-001
205 | A0LBA10CT101 | 主蒸汽联络管疏水阀后温度 | Temperature after main steam contact pipe drain valve | A0LBA10CT101 | 4~20mA | AI | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-001
206 | 70LBA20CT101 | 减温减压器A前疏水阀后温度 | Temperature after desuperheater A front drain valve | 70LBA20CT101 | 4~20mA | AI | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-001
207 | 70LBA20CT102 | 减温减压器B前疏水阀后温度 | Temperature after desuperheater B front drain valve | 70LBA20CT102 | 4~20mA | AI | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-001
208 | 70LBA10CF101 | 主蒸汽流量1 | Main steam flow 1 | 70LBA10CF101 | 4~20mA | AI | 0~450 | t/h | [8 empty] | MCS | D |  | K0204-001
209 | 70LBA10CF102 | 主蒸汽流量2 | Main steam flow 2 | 70LBA10CF102 | 4~20mA | AI | 0~450 | t/h | [8 empty] | MCS | D |  | K0204-001
210 | 70LBA10CF103 | 主蒸汽流量3 | Main steam flow 3 | 70LBA10CF103 | 4~20mA | AI | 0~450 | t/h | [8 empty] | MCS | D |  | K0204-001
211 | A0LBA10AA001YB01 | 主蒸汽联络管电动阀打开指令 | Main steam contact pipe MOV open command | A0LBA10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
212 | A0LBA10AA001YB11 | 主蒸汽联络管电动阀关闭指令 | Main steam contact pipe MOV close command | A0LBA10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
213 | A0LBA10AA001XB01 | 主蒸汽联络管电动阀全开状态 | Main steam contact pipe MOV full opened status | A0LBA10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-001
214 | A0LBA10AA001XB11 | 主蒸汽联络管电动阀全关状态 | Main steam contact pipe MOV full closed status | A0LBA10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-001
215 | A0LBA10AA001XB31 | 主蒸汽联络管电动阀故障 | Main steam contact pipe MOV fault | A0LBA10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-001
216 | A0LBA10AA402YB01 | 主蒸汽联络管疏水阀打开/关闭指令 | Main steam contact pipe drain valve open/close command | A0LBA10AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
217 | A0LBA10AA402XB01 | 主蒸汽联络管疏水阀全开状态 | Main steam contact pipe drain valve full opened status | A0LBA10AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-001
218 | A0LBA10AA402XB11 | 主蒸汽联络管疏水阀全关状态 | Main steam contact pipe drain valve full closed status | A0LBA10AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-001
219 | 70LBA10AA002YB01 | 主蒸汽电动阀打开指令 | Main steam MOV open command | 70LBA10AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
220 | 70LBA10AA002YB11 | 主蒸汽电动阀关闭指令 | Main steam MOV close command | 70LBA10AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
221 | 70LBA10AA002XB01 | 主蒸汽电动阀全开状态 | Main steam MOV full opened status | 70LBA10AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-001
222 | 70LBA10AA002XB11 | 主蒸汽电动阀全关状态 | Main steam MOV full closed status | 70LBA10AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-001
223 | 70LBA10AA002XB31 | 主蒸汽电动阀故障 | Main steam MOV fault | 70LBA10AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-001
224 | 70LBA10AA406YB01 | 主蒸汽电动阀前疏水阀打开/关闭指令 | Drain valve before main steam MOV open/close command | 70LBA10AA406 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
225 | 70LBA10AA406XB01 | 主蒸汽电动阀前疏水阀全开状态 | Drain valve before main steam MOV full opened status | 70LBA10AA406 | NO | DI | [10 empty] | SCS | D |  | K0204-001
226 | 70LBA10AA406XB11 | 主蒸汽电动阀前疏水阀全关状态 | Drain valve before main steam MOV full closed status | 70LBA10AA406 | NO | DI | [10 empty] | SCS | D |  | K0204-001
227 | 70LBA10AA402YB01 | 汽机(右)进汽管道疏水阀打开/关闭指令 | Turbine(right) main steam inlet pipe drain valve open/close command | 70LBA10AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
228 | 70LBA10AA402XB01 | 汽机(右)进汽管道疏水阀全开状态 | Turbine(right) main steam inlet pipe drain valve full opened status | 70LBA10AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-001
229 | 70LBA10AA402XB11 | 汽机(右)进汽管道疏水阀全关状态 | Turbine(right) main steam inlet pipe drain valve full closed status | 70LBA10AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-001
230 | 70LBA10AA404YB01 | 汽机(左)进汽管道疏水阀打开/关闭指令 | Turbine(left) main steam inlet pipe drain valve open/close command | 70LBA10AA404 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
231 | 70LBA10AA404XB01 | 汽机(左)进汽管道疏水阀全开状态 | Turbine(left) main steam inlet pipe drain valve full opened status | 70LBA10AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-001
232 | 70LBA10AA404XB11 | 汽机(左)进汽管道疏水阀全关状态 | Turbine(left) main steam inlet pipe drain valve full closed status | 70LBA10AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-001
233 | 70LBA20AA402YB01 | 减温减压器A前疏水阀打开/关闭指令 | Drain valve before desuperheater A open/close command | 70LBA20AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
234 | 70LBA20AA402XB01 | 减温减压器A前疏水阀全开状态 | Drain valve before desuperheater A full opened status | 70LBA20AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-001
235 | 70LBA20AA402XB11 | 减温减压器A前疏水阀全关状态 | Drain valve before desuperheater A full closed status | 70LBA20AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-001
236 | 70LBA20AA404YB01 | 减温减压器B前疏水阀打开/关闭指令 | Drain valve before desuperheater B open/close command | 70LBA20AA404 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
237 | 70LBA20AA404XB01 | 减温减压器B前疏水阀全开状态 | Drain valve before desuperheater B full opened status | 70LBA20AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-001
238 | 70LBA20AA404XB11 | 减温减压器B前疏水阀全关状态 | Drain valve before desuperheater B full closed status | 70LBA20AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-001
239 | 70LBA20AA001YB01 | 减温减压器A前电动阀打开指令 | Desuperheater A front MOV open command | 70LBA20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
240 | 70LBA20AA001YB11 | 减温减压器A前电动阀关闭指令 | Desuperheater A front MOV close command | 70LBA20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
241 | 70LBA20AA001XB01 | 减温减压器A前电动阀全开状态 | Desuperheater A front MOV full opened status | 70LBA20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-001
242 | 70LBA20AA001XB11 | 减温减压器A前电动阀全关状态 | Desuperheater A front MOV full closed status | 70LBA20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-001
243 | 70LBA20AA001XB31 | 减温减压器A前电动阀故障 | Desuperheater A front MOV fault | 70LBA20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-001
244 | 70LBA20AA002YB01 | 减温减压器B前电动阀打开指令 | Desuperheater B front MOV open command | 70LBA20AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
245 | 70LBA20AA002YB11 | 减温减压器B前电动阀关闭指令 | Desuperheater B front MOV close command | 70LBA20AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-001
246 | 70LBA20AA002XB01 | 减温减压器B前电动阀全开状态 | Desuperheater B front MOV full opened status | 70LBA20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-001
247 | 70LBA20AA002XB11 | 减温减压器B前电动阀全关状态 | Desuperheater B front MOV full closed status | 70LBA20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-001
248 | 70LBA20AA002XB31 | 减温减压器B前电动阀故障 | Desuperheater B front MOV fault | 70LBA20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-001
249 | 70MAA50CP111 | #2级调整抽汽压力#5 | #2 regulated extraction steam pressure #5 | 70MAA50CP111 | 4~20mA | AI | 0~1.6 | MPa | [8 empty] | DAS | D |  | K0204-002
250 | 70MAA50CP112 | #2级调整抽汽压力#6 | #2 regulated extraction steam pressure #6 | 70MAA50CP112 | 4~20mA | AI | 0~1.6 | MPa | [8 empty] | DAS | D |  | K0204-002
251 | 70MAA50CT127 | #2级调整抽汽温度#3 | #2 regulated extraction steam temperature #3 | 70MAA50CT127 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-002
252 | 70MAA50CT128 | #2级调整抽汽温度#4 | #2 regulated extraction steam temperature #4 | 70MAA50CT128 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-002
253 | 70LBR20CT101 | #2级调整抽汽逆止阀后管顶温度 | Top temperature of pipe after #2 regulated extraction steam check valve | 70LBR20CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-002
254 | 70LBR20CT102 | #2级调整抽汽逆止阀后管底温度 | Bottom temperature of pipe after #2 regulated extraction steam check valve | 70LBR20CT102 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-002
255 | 70LBR20CT103 | #2级调整抽汽逆止阀后疏水温度 | Drain temperature after #2 regulated extraction steam check valve | 70LBR20CT103 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-002
256 | 70LBR20CP101 | #2级调整抽汽减温减压(D)后蒸汽压力 | Steam pressure after #2 regulated extraction steam temperature and pressure reduction(D) | 70LBR20CP101 | 4~20mA | AI | 0~0.8 | MPa | [8 empty] | DAS | D |  | K0204-002
257 | 70LBR20CT104 | #2级调整抽汽减温减压(D)后蒸汽温度 | Steam temperature after #2 regulated extraction steam temperature and pressure reduction(D) | 70LBR20CT104 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | MCS | D |  | K0204-002
258 | 70LBR20CF101 | #2级调整抽汽减温减压(D)后蒸汽流量 | Steam flow after #2 regulated extraction steam temperature and pressure reduction(D) | 70LBR20CF101 | 4~20mA | AI | 0~140 | t/h | [8 empty] | MCS | D |  | K0204-002
259 | 70LBR20CT109 | #2级调整抽汽电动阀后疏水温度 | Drain temperature after #2 regulated extraction steam MOV | 70LBR20CT109 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-002
260 | 70LBR20AA201YB01 | #2级调整抽汽逆止阀打开/关闭指令 | #2 regulated extraction steam check valve open/close command | 70LBR20AA201 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-002
261 | 70LBR20AA201XB01 | #2级调整抽汽逆止阀全开状态 | #2 regulated extraction steam check valve full opened status | 70LBR20AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-002
262 | 70LBR20AA201XB11 | #2级调整抽汽逆止阀全关状态 | #2 regulated extraction steam check valve full closed status | 70LBR20AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-002
263 | 70LBR20AA102YQ01 | #2级调整抽汽减温减压器D电动减压调节阀控制指令 | #2 regulated extraction steam pressure reducer desuperheater D pressure reduciong regulating MOV position command | 70LBR20AA102 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-002
264 | 70LBR20AA102XQ11 | #2级调整抽汽减温减压器D电动减压调节阀位置反馈 | #2 regulated extraction steam pressure reducer desuperheater D pressure reduciong regulating MOV position feddback | 70LBR20AA102 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-002
265 | 70LBR20AA103YQ01 | #2级调整抽汽减温减压器D电动减温调节阀控制指令 | #2 regulated extraction steam pressure reducer desuperheater D temperature reduciong regulating MOV position command | 70LBR20AA103 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-002
266 | 70LBR20AA103XQ11 | #2级调整抽汽减温减压器D电动减温调节阀位置反馈 | #2 regulated extraction steam pressure reducer desuperheater D temperature reduciong regulating MOV position feddback | 70LBR20AA103 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-002
267 | 70LBR20AA001YB01 | #2级调整抽汽电动阀打开指令 | #2 regulated extraction steam MOV open command | 70LBR20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-002
268 | 70LBR20AA001YB11 | #2级调整抽汽电动阀关闭指令 | #2 regulated extraction steam MOV close command | 70LBR20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-002
269 | 70LBR20AA001XB01 | #2级调整抽汽电动阀全开状态 | #2 regulated extraction steam MOV full opened status | 70LBR20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-002
270 | 70LBR20AA001XB11 | #2级调整抽汽电动阀全关状态 | #2 regulated extraction steam MOV full closed status | 70LBR20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-002
271 | 70LBR20AA001XB31 | #2级调整抽汽电动阀故障 | #2 regulated extraction steam MOV fault | 70LBR20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-002
272 | 70LBR20AA414YB01 | #2级调整抽汽逆止阀后疏水阀打开/关闭指令 | Drain valve after #2 regulated extraction steam check valve open/close command | 70LBR20AA414 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-002
273 | 70LBR20AA414XB01 | #2级调整抽汽逆止阀后疏水阀全开状态 | Drain valve after #2 regulated extraction steam check valve full opened status | 70LBR20AA414 | NO | DI | [10 empty] | SCS | D |  | K0204-002
274 | 70LBR20AA414XB11 | #2级调整抽汽逆止阀后疏水阀全关状态 | Drain valve after #2 regulated extraction steam check valve full closed status | 70LBR20AA414 | NO | DI | [10 empty] | SCS | D |  | K0204-002
275 | 70LBR20AA404YB01 | #2级调整抽汽电动阀后疏水阀打开/关闭指令 | Drain valve after #2 regulated extraction steam MOV open/close command | 70LBR20AA404 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-002
276 | 70LBR20AA404XB01 | #2级调整抽汽电动阀后疏水阀全开状态 | Drain valve after #2 regulated extraction steam MOV full opened status | 70LBR20AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-002
277 | 70LBR20AA404XB11 | #2级调整抽汽电动阀后疏水阀全关状态 | Drain valve after #2 regulated extraction steam MOV full closed status | 70LBR20AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-002
278 | 70LBR20CP102 | 主蒸汽减温减压(B)后蒸汽压力 | Steam pressure after main steam temperature and pressure reduction(B) | 70LBR20CP102 | 4~20mA | AI | 0~0.8 | MPa | [8 empty] | MCS | D |  | K0204-002
279 | 70LBR20CT106 | 主蒸汽减温减压(B)后蒸汽温度 | Steam temperature after main steam temperature and pressure reduction(B) | 70LBR20CT106 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | MCS | D |  | K0204-002
280 | 70LBR20CT105 | 主蒸汽低压旁路管道电动阀后疏水温度 | Drain temperature after main steam LP bypass pipe MOV | 70LBR20CT105 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-002
281 | 70LBR20AA104YQ01 | 主蒸汽减温减压器B电动减压调节阀控制指令 | Main steam pressure reducer desuperheater B pressure reduciong regulating MOV position command | 70LBR20AA104 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-002
282 | 70LBR20AA104XQ11 | 主蒸汽减温减压器B电动减压调节阀位置反馈 | Main steam pressure reducer desuperheater B pressure reduciong regulating MOV position feddback | 70LBR20AA104 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-002
283 | 70LBR20AA105YQ01 | 主蒸汽减温减压器B电动减温调节阀控制指令 | Main steam pressure reducer desuperheater B temperature reduciong regulating MOV position command | 70LBR20AA105 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-002
284 | 70LBR20AA105XQ11 | 主蒸汽减温减压器B电动减温调节阀位置反馈 | Main steam pressure reducer desuperheater B temperature reduciong regulating MOV position feddback | 70LBR20AA105 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-002
285 | 70LBR20AA002YB01 | 主蒸汽低压旁路管道电动阀打开指令 | Main steam LP bypass pipe MOV open command | 70LBR20AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-002
286 | 70LBR20AA002YB11 | 主蒸汽低压旁路管道电动阀关闭指令 | Main steam LP bypass pipe MOV close command | 70LBR20AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-002
287 | 70LBR20AA002XB01 | 主蒸汽低压旁路管道电动阀全开状态 | Main steam LP bypass pipe MOV full opened status | 70LBR20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-002
288 | 70LBR20AA002XB11 | 主蒸汽低压旁路管道电动阀全关状态 | Main steam LP bypass pipe MOV full closed status | 70LBR20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-002
289 | 70LBR20AA002XB31 | 主蒸汽低压旁路管道电动阀故障 | Main steam LP bypass pipe MOV fault | 70LBR20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-002
290 | 70LBR20AA402YB01 | 主蒸汽低压旁路管道电动阀后疏水阀打开/关闭指令 | Drain valve after main steam LP bypass pipe MOV open/close command | 70LBR20AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-002
291 | 70LBR20AA402XB01 | 主蒸汽低压旁路管道电动阀后疏水阀全开状态 | Drain valve after main steam LP bypass pipe MOV full opened status | 70LBR20AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-002
292 | 70LBR20AA402XB11 | 主蒸汽低压旁路管道电动阀后疏水阀全关状态 | Drain valve after main steam LP bypass pipe MOV full closed status | 70LBR20AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-002
293 | 70LBR20CT107 | 低压联箱进汽母管蒸汽温度 | LP steam header inlet main pipe steam temperature | 70LBR20CT107 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-002
294 | 70LBR20CP103 | 低压联箱进汽母管蒸汽压力 | LP steam header inlet main pipe steam pressure | 70LBR20CP103 | 4~20mA | AI | 0~0.8 | MPa | [8 empty] | DAS | D |  | K0204-002
295 | 70LBR20CF102 | 低压联箱进汽母管蒸汽流量 | LP steam header inlet main pipe steam flow | 70LBR20CF102 | 4~20mA | AI | 0~140 | t/h | [8 empty] | DAS | D |  | K0204-002
296 | 70LBR20CT108 | 低压联箱蒸汽温度 | LP steam header steam temperature | 70LBR20CT108 | K | TC | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-002
297 | 70LBR20CP104 | 低压联箱蒸汽压力 | LP steam header steam pressure | 70LBR20CP104 | 4~20mA | AI | 0~1 | MPa | [8 empty] | DAS | D |  | K0204-002
298 | 70LBR20CF103 | 低压联箱至老厂#6机组低压蒸汽管道供热蒸汽流量 | LP steam header to existing LP steam line of #6 unit heating steam flow | 70LBR20CF103 | 4~20mA | AI | 0~70 | t/h | [8 empty] | DAS | D |  | K0204-002
299 | 70LBR20CF104 | 低压联箱至老厂#3机组低压蒸汽管道供热蒸汽流量 | LP steam header to existing LP steam line of #3 unit heating steam flow | 70LBR20CF104 | 4~20mA | AI | 0~70 | t/h | [8 empty] | DAS | D |  | K0204-002
300 | 70LBR20CF105 | 低压联箱至老厂#1机组低压蒸汽管道供热蒸汽流量 | LP steam header to existing LP steam line of #1 unit heating steam flow | 70LBR20CF105 | 4~20mA | AI | 0~70 | t/h | [8 empty] | DAS | D |  | K0204-002
301 | 70LBR20CF106 | 低压联箱至老厂#2机组低压蒸汽管道供热蒸汽流量 | LP steam header to existing LP steam line of #2 unit heating steam flow | 70LBR20CF106 | 4~20mA | AI | 0~70 | t/h | [8 empty] | DAS | D |  | K0204-002
302 | 70LBR20AA003YB01 | 低压联箱启动排汽电动阀打开指令 | LP steam header start exhaust MOV open command | 70LBR20AA003 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-002
303 | 70LBR20AA003YB11 | 低压联箱启动排汽电动阀关闭指令 | LP steam header start exhaust MOV close command | 70LBR20AA003 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-002
304 | 70LBR20AA003XB01 | 低压联箱启动排汽电动阀全开状态 | LP steam header start exhaust MOV full opened status | 70LBR20AA003 | NO | DI | [10 empty] | SCS | D |  | K0204-002
305 | 70LBR20AA003XB11 | 低压联箱启动排汽电动阀全关状态 | LP steam header start exhaust MOV full closed status | 70LBR20AA003 | NO | DI | [10 empty] | SCS | D |  | K0204-002
306 | 70LBR20AA003XB31 | 低压联箱启动排汽电动阀故障 | LP steam header start exhaust MOV fault | 70LBR20AA003 | NO | DI | [10 empty] | SCS | D |  | K0204-002
307 | 70MAG10CP101 | 凝汽器真空1 | Condenser vacuum pressure 1 | 70MAG10CP101 | 4~20mA | AI | 0~0.2 | MPa | [8 empty] | SCS | D |  | K0204-003
308 | 70MAG10CP102 | 凝汽器真空2 | Condenser vacuum pressure 2 | 70MAG10CP102 | 4~20mA | AI | 0~0.2 | MPa | [8 empty] | SCS | D |  | K0204-003
309 | 70MAG12CT101 | 真空泵A电机轴承温度1 | Vacuum pump A motor bearing temperature 1 | 70MAG12GH001 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-003 | 真空泵A电机接线盒 | Vacuum pump A motor JB
310 | 70MAG12CT102 | 真空泵A电机轴承温度2 | Vacuum pump A motor bearing temperature 2 | 70MAG12GH001 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-003 | 真空泵A电机接线盒 | Vacuum pump A motor JB
311 | 70MAG12CT103 | 真空泵A电机绕组温度1 | Vacuum pump A motor stator coil temperature 1 | 70MAG12GH001 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-003 | 真空泵A电机接线盒 | Vacuum pump A motor JB
312 | 70MAG12CT104 | 真空泵A电机绕组温度2 | Vacuum pump A motor stator coil temperature 2 | 70MAG12GH001 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-003 | 真空泵A电机接线盒 | Vacuum pump A motor JB
313 | 70MAG12CT105 | 真空泵A电机绕组温度3 | Vacuum pump A motor stator coil temperature 3 | 70MAG12GH001 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-003 | 真空泵A电机接线盒 | Vacuum pump A motor JB
314 | 70MAG11CT101 | 真空泵B电机轴承温度1 | Vacuum pump B motor bearing temperature 1 | 70MAG11GH001 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-003 | 真空泵B电机接线盒 | Vacuum pump B motor JB
315 | 70MAG11CT102 | 真空泵B电机轴承温度2 | Vacuum pump B motor bearing temperature 2 | 70MAG11GH001 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-003 | 真空泵B电机接线盒 | Vacuum pump B motor JB
316 | 70MAG11CT103 | 真空泵B电机绕组温度1 | Vacuum pump B motor stator coil temperature 1 | 70MAG11GH001 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-003 | 真空泵B电机接线盒 | Vacuum pump B motor JB
317 | 70MAG11CT104 | 真空泵B电机绕组温度2 | Vacuum pump B motor stator coil temperature 2 | 70MAG11GH001 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-003 | 真空泵B电机接线盒 | Vacuum pump B motor JB
318 | 70MAG11CT105 | 真空泵B电机绕组温度3 | Vacuum pump B motor stator coil temperature 3 | 70MAG11GH001 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-003 | 真空泵B电机接线盒 | Vacuum pump B motor JB
319 | 70MAG12CP001 | 真空泵A入口气动阀前压力低 | Pressure L before vacuum pump A inlet PV | 70MAG12GH002 | NO | DI |  | Kpa | [8 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box | bar: L
320 | 70MAG12CP002 | 真空泵A入口气动阀后压力 | Pressure after vacuum pump A inlet PV | 70MAG12GH002 | NO | DI | -85 | Kpa | [8 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
321 | 70MAG12CL101 | 真空泵A分离罐液位 | Vacuum pump A separator level | 70MAG12GH002 | 4~20mA | AI |  | mm | [8 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
322 | 70MAG12CL101H | 真空泵A分离罐液位高 | Vacuum pump A separator level H | 70MAG12GH002 | NO | DI | 180 | mm | [8 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box | bar: H
323 | 70MAG12CL101L | 真空泵A分离罐液位低 | Vacuum pump A separator level L | 70MAG12GH002 | NC | DI | 140 | mm | [8 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box | bar: L
324 | 70MAG12AA012YB01 | 真空泵A入口气动阀打开指令 | Vacuum pump A inlet PV open command | 70MAG12GH002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
325 | 70MAG12AA012YB11 | 真空泵A入口气动阀关闭指令 | Vacuum pump A inlet PV close command | 70MAG12GH002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
326 | 70MAG12AA012XB01 | 真空泵A入口气动阀全开状态 | Vacuum pump A inlet PV full opened status | 70MAG12GH002 | NO | DI | [10 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
327 | 70MAG12AA012XB11 | 真空泵A入口气动阀全关状态 | Vacuum pump A inlet PV full closed status | 70MAG12GH002 | NO | DI | [10 empty] | SCS | D |  | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
328 | 70MAG12AA003YB01 | 真空泵A分离罐补水电磁阀打开/关闭指令 | Vacuum pump A separator water supply SV open/close command | 70MAG12GH002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003 | 真空泵A仪表控制箱 | Vacuum pump A instrument control box
329 | 70MAG12CQ101 | 真空泵A漏气量 | Vacuum pump A leakage | 70MAG12CQ101 | 4~20mA | AI | 0~240 | Kg/h | [8 empty] | DAS | U |  | K0204-003
330 | 70MAG11CP001 | 真空泵B入口气动阀前压力低 | Pressure L before Vacuum pump B inlet PV | 70MAG11GH002 | NO | DI |  | Kpa | [8 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box | bar: L
331 | 70MAG11CP002 | 真空泵B入口气动阀后压力 | Pressure after Vacuum pump B inlet PV | 70MAG11GH002 | NO | DI | -85 | Kpa | [8 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
332 | 70MAG11CL101 | 真空泵B分离罐液位 | Vacuum pump B separator level | 70MAG11GH002 | 4~20mA | AI |  | mm | [8 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
333 | 70MAG11CL101H | 真空泵B分离罐液位高 | Vacuum pump B separator level H | 70MAG11GH002 | NO | DI | 180 | mm | [8 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box | bar: H
334 | 70MAG11CL101L | 真空泵B分离罐液位低 | Vacuum pump B separator level L | 70MAG11GH002 | NC | DI | 140 | mm | [8 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box | bar: L
335 | 70MAG11AA012YB01 | 真空泵B入口气动阀打开指令 | Vacuum pump B inlet PV open command | 70MAG11GH002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
336 | 70MAG11AA012YB11 | 真空泵B入口气动阀关闭指令 | Vacuum pump B inlet PV close command | 70MAG11GH002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
337 | 70MAG11AA012XB01 | 真空泵B入口气动阀全开状态 | Vacuum pump B inlet PV full opened status | 70MAG11GH002 | NO | DI | [10 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
338 | 70MAG11AA012XB11 | 真空泵B入口气动阀全关状态 | Vacuum pump B inlet PV full closed status | 70MAG11GH002 | NO | DI | [10 empty] | SCS | D |  | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
339 | 70MAG11AA003YB01 | 真空泵B分离罐补水电磁阀打开/关闭指令 | Vacuum pump B separator water supply SV open/close command | 70MAG11GH002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003 | 真空泵B仪表控制箱 | Vacuum pump B instrument control box
340 | 70MAG11CQ101 | 真空泵B漏气量 | Vacuum pump B leakage | 70MAG11CQ101 | 4~20mA | AI | 0~240 | Kg/h | [8 empty] | DAS | U |  | K0204-003
341 | 70MAG12AA001YB01 | 真空泵A入口电动门打开指令 | Vacuum pump A inlet MOV open command | 70MAG12AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003
342 | 70MAG12AA001YB11 | 真空泵A入口电动门关闭指令 | Vacuum pump A inlet MOV close command | 70MAG12AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003
343 | 70MAG12AA001XB01 | 真空泵A入口电动门全开状态 | Vacuum pump A inlet MOV full opened status | 70MAG12AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
344 | 70MAG12AA001XB11 | 真空泵A入口电动门全关状态 | Vacuum pump A inlet MOV full closed status | 70MAG12AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
345 | 70MAG12AA001XB31 | 真空泵A入口电动门故障状态 | Vacuum pump A inlet MOV fault | 70MAG12AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
346 | 70MAG11AA001YB01 | 真空泵B入口电动门打开指令 | Vacuum pump B inlet MOV open command | 70MAG11AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003
347 | 70MAG11AA001YB11 | 真空泵B入口电动门关闭指令 | Vacuum pump B inlet MOV close command | 70MAG11AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003
348 | 70MAG11AA001XB01 | 真空泵B入口电动门全开状态 | Vacuum pump B inlet MOV full opened status | 70MAG11AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
349 | 70MAG11AA001XB11 | 真空泵B入口电动门全关状态 | Vacuum pump B inlet MOV full closed status | 70MAG11AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
350 | 70MAG11AA001XB31 | 真空泵B入口电动门故障状态 | Vacuum pump B inlet MOV fault | 70MAG11AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
351 | 70MAG10AA001YB01 | 真空泵破坏电动门打开指令 | Vacuum break MOV open command | 70MAG10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003
352 | 70MAG10AA001YB11 | 真空泵破坏电动门关闭指令 | Vacuum break MOV close command | 70MAG10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003
353 | 70MAG10AA001XB01 | 真空泵破坏电动门全开状态 | Vacuum break MOV full opened status | 70MAG10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
354 | 70MAG10AA001XB11 | 真空泵破坏电动门全关状态 | Vacuum break MOV full closed status | 70MAG10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
355 | 70MAG10AA001XB31 | 真空泵破坏电动门故障状态 | Vacuum break MOV fault | 70MAG10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
356 | 70MAG12AP001YB01 | 真空泵A启动指令 | Vacuum pump A start command | 70MAG12AP001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003
357 | 70MAG12AP001YB11 | 真空泵A停止指令 | Vacuum pump A stop command | 70MAG12AP001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003
358 | 70MAG12AP001XB01 | 真空泵A运行 | Vacuum pump A running | 70MAG12AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
359 | 70MAG12AP001XB11 | 真空泵A停止 | Vacuum pump A stopped | 70MAG12AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
360 | 70MAG12AP001XB12 | 真空泵A停止(SOE) | Vacuum pump A stopped(SOE) | 70MAG12AP001 | NC | SOE | [10 empty] | SOE | D |  | K0204-003
361 | 70MAG12AP001XB21 | 真空泵A远方控制允许 | Vacuum pump A remote control permitted | 70MAG12AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
362 | 70MAG12AP001XB31 | 真空泵A控制电源消失 | Vacuum pump A control circuit broken | 70MAG12AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
363 | 70MAG12AP001XB32 | 真空泵A故障输出 | Vacuum pump A fault output | 70MAG12AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
364 | 70MAG12AP001XQ01 | 真空泵A电流 | Vacuum pump A current | 70MAG12AP001 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0204-003
365 | 70MAG11AP001YB01 | 真空泵B启动指令 | Vacuum pump B start command | 70MAG11AP001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003
366 | 70MAG11AP001YB11 | 真空泵B停止指令 | Vacuum pump B stop command | 70MAG11AP001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-003
367 | 70MAG11AP001XB01 | 真空泵B运行 | Vacuum pump B running | 70MAG11AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
368 | 70MAG11AP001XB11 | 真空泵B停止 | Vacuum pump B stopped | 70MAG11AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
369 | 70MAG11AP001XB12 | 真空泵B停止(SOE) | Vacuum pump B stopped(SOE) | 70MAG11AP001 | NC | SOE | [10 empty] | SOE | D |  | K0204-003
370 | 70MAG11AP001XB21 | 真空泵B远方控制允许 | Vacuum pump B remote control permitted | 70MAG11AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
371 | 70MAG11AP001XB31 | 真空泵B控制电源消失 | Vacuum pump B control circuit broken | 70MAG11AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
372 | 70MAG11AP001XB32 | 真空泵B故障输出 | Vacuum pump B fault output | 70MAG11AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-003
373 | 70MAG11AP001XQ01 | 真空泵B电流 | Vacuum pump B current | 70MAG11AP001 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0204-003
374 | 70LBQ10CP101 | 1#抽汽蒸汽压力 | 1# extraction steam pressure | 70LBQ10CP101 | 4~20mA | AI | 0~4.0 | MPa | [8 empty] | DAS | D |  | K0204-004
375 | 70LBQ10CT101 | 1#抽汽蒸汽温度 | 1# extraction steam temperature | 70LBQ10CT101 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-004
376 | 70LBQ10CT102 | 1#抽汽逆止阀后管顶温度 | Top temperature of pipe after 1# extraction steam check valve | 70LBQ10CT102 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-004
377 | 70LBQ10CT103 | 1#抽汽逆止阀后管底温度 | Bottom temperature of pipe after 1# extraction steam check valve | 70LBQ10CT103 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-004
378 | 70LBQ10CT104 | 1#抽汽逆止阀后疏水温度 | Drain temperature after 1# extraction steam check valve | 70LBQ10CT104 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-004
379 | 70LBQ10AA201YB01 | 1#抽汽逆止阀打开/关闭指令 | 1# extraction steam check valve open/close command | 70LBQ10AA201 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
380 | 70LBQ10AA201XB01 | 1#抽汽逆止阀全开状态 | 1# extraction steam check valve full opened status | 70LBQ10AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-004
381 | 70LBQ10AA201XB11 | 1#抽汽逆止阀全关状态 | 1# extraction steam check valve full closed status | 70LBQ10AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-004
382 | 70LBQ10AA402YB01 | 1#抽汽逆止阀后疏水阀打开/关闭指令 | Drain valve after 1# extraction steam check valve open/close command | 70LBQ10AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
383 | 70LBQ10AA402XB01 | 1#抽汽逆止阀后疏水阀全开状态 | Drain valve after 1# extraction steam check valve full opened status | 70LBQ10AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-004
384 | 70LBQ10AA402XB11 | 1#抽汽逆止阀后疏水阀全关状态 | Drain valve after 1# extraction steam check valve full closed status | 70LBQ10AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-004
385 | 70LBQ10AA001YB01 | 1#抽汽电动阀打开指令 | 1# extraction steam MOV open command | 70LBQ10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
386 | 70LBQ10AA001YB11 | 1#抽汽电动阀关闭指令 | 1# extraction steam MOV close command | 70LBQ10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
387 | 70LBQ10AA001XB01 | 1#抽汽电动阀全开状态 | 1# extraction steam MOV full opened status | 70LBQ10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
388 | 70LBQ10AA001XB11 | 1#抽汽电动阀全关状态 | 1# extraction steam MOV full closed status | 70LBQ10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
389 | 70LBQ10AA001XB31 | 1#抽汽电动阀故障 | 1# extraction steam MOV fault | 70LBQ10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
390 | 70LBQ10CP102 | 2#高压加热器进汽压力 | 2# HP heater inlet steam pressure | 70LBQ10CP102 | 4~20mA | AI | 0~4.0 | MPa | [8 empty] | DAS | D |  | K0204-004
391 | 70LBQ10CT105 | 2#高压加热器进汽温度 | 2# HP heater inlet steam temperature | 70LBQ10CT105 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-004
392 | 70LBR10CP101 | 3#抽汽蒸汽压力 | 3# extraction steam pressure | 70LBR10CP101 | 4~20mA | AI | 0~1.44 | MPa | [8 empty] | DAS | D |  | K0204-004
393 | 70LBR10CT101 | 3#抽汽蒸汽温度 | 3# extraction steam temperature | 70LBR10CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
394 | 70LBR10CT102 | 3#抽汽逆止阀2后管顶温度 | Top temperature of pipe after 3# extraction steam check valve 2 | 70LBR10CT102 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
395 | 70LBR10CT103 | 3#抽汽逆止阀2后管底温度 | Bottom temperature of pipe after 3# extraction steam check valve 2 | 70LBR10CT103 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
396 | 70LBR10CT104 | 3#抽汽逆止阀2后疏水温度1 | Drain temperature 1 after 3# extraction steam check valve 2 | 70LBR10CT104 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
397 | 70LBR10CT105 | 3#抽汽逆止阀2后疏水温度2 | Drain temperature 2 after 3# extraction steam check valve 2 | 70LBR10CT105 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
398 | 70LBR10CT106 | 3#抽汽电动阀后旁路疏水温度 | Bypass drain temperature after 3# extraction steam MOV | 70LBR10CT106 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
399 | 70LBR10CT107 | 3#抽汽电动调节阀后疏水温度1 | Drain temperature 1 after 3# extraction steam regulating MOV | 70LBR10CT107 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
400 | 70LBR10CT108 | 3#抽汽电动调节阀后疏水温度2 | Drain temperature 2 after 3# extraction steam regulating MOV | 70LBR10CT108 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
401 | 70LBR10CP102 | 除氧器进汽压力 | Deaerator inlet steam pressure | 70LBR10CP102 | 4~20mA | AI | 0~1.6 | MPa | [8 empty] | MCS | D |  | K0204-004
402 | 70LBR10CT109 | 除氧器进汽温度 | Deaerator inlet steam temperature | 70LBR10CT109 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
403 | 70LBR10AA201YB01 | 3#抽汽逆止阀1打开/关闭指令 | 3# extraction steam check valve 1 open/close command | 70LBR10AA201 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
404 | 70LBR10AA201XB01 | 3#抽汽逆止阀1全开状态 | 3# extraction steam check valve 1 full opened status | 70LBR10AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-004
405 | 70LBR10AA201XB11 | 3#抽汽逆止阀1全关状态 | 3# extraction steam check valve 1 full closed status | 70LBR10AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-004
406 | 70LBR10AA202YB01 | 3#抽汽逆止阀2打开/关闭指令 | 3# extraction steam check valve 2 open/close command | 70LBR10AA202 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
407 | 70LBR10AA202XB01 | 3#抽汽逆止阀2全开状态 | 3# extraction steam check valve 2 full opened status | 70LBR10AA202 | NO | DI | [10 empty] | SCS | D |  | K0204-004
408 | 70LBR10AA202XB11 | 3#抽汽逆止阀2全关状态 | 3# extraction steam check valve 2 full closed status | 70LBR10AA202 | NO | DI | [10 empty] | SCS | D |  | K0204-004
409 | 70LBR10AA404YB01 | 3#抽汽逆止阀2后疏水阀1打开/关闭指令 | Drain valve 1 after 3# extraction steam check valve 2 open/close command | 70LBR10AA404 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
410 | 70LBR10AA404XB01 | 3#抽汽逆止阀2后疏水阀1全开状态 | Drain valve 1 after 3# extraction steam check valve 2 full opened status | 70LBR10AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-004
411 | 70LBR10AA404XB11 | 3#抽汽逆止阀2后疏水阀1全关状态 | Drain valve 1 after 3# extraction steam check valve 2 full closed status | 70LBR10AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-004
412 | 70LBR10AA410YB01 | 3#抽汽逆止阀2后疏水阀2打开/关闭指令 | Drain valve 2 after 3# extraction steam check valve 2 open/close command | 70LBR10AA410 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
413 | 70LBR10AA410XB01 | 3#抽汽逆止阀2后疏水阀2全开状态 | Drain valve 2 after 3# extraction steam check valve 2 full opened status | 70LBR10AA410 | NO | DI | [10 empty] | SCS | D |  | K0204-004
414 | 70LBR10AA410XB11 | 3#抽汽逆止阀2后疏水阀2全关状态 | Drain valve 2 after 3# extraction steam check valve 2 full closed status | 70LBR10AA410 | NO | DI | [10 empty] | SCS | D |  | K0204-004
415 | 70LBR10AA001YB01 | 3#抽汽电动阀打开指令 | 3# extraction steam MOV open command | 70LBR10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
416 | 70LBR10AA001YB11 | 3#抽汽电动阀关闭指令 | 3# extraction steam MOV close command | 70LBR10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
417 | 70LBR10AA001XB01 | 3#抽汽电动阀全开状态 | 3# extraction steam MOV full opened status | 70LBR10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
418 | 70LBR10AA001XB11 | 3#抽汽电动阀全关状态 | 3# extraction steam MOV full closed status | 70LBR10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
419 | 70LBR10AA001XB31 | 3#抽汽电动阀故障 | 3# extraction steam MOV fault | 70LBR10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
420 | 70LBR10AA101YQ01 | 3#抽汽电动调节阀控制指令 | 3# extraction steam regulating MOV position command | 70LBR10AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-004
421 | 70LBR10AA101XQ11 | 3#抽汽电动调节阀位置指令 | 3# extraction steam regulating MOV position feedback | 70LBR10AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-004
422 | 70LBR10AA412YB01 | 3#抽汽电动阀后旁路疏水阀打开/关闭指令 | Bypass drain valve after 3# extraction steam MOV open/close command | 70LBR10AA412 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
423 | 70LBR10AA412XB01 | 3#抽汽电动阀后旁路疏水阀全开状态 | Bypass drain valve after 3# extraction steam MOV full opened status | 70LBR10AA412 | NO | DI | [10 empty] | SCS | D |  | K0204-004
424 | 70LBR10AA412XB11 | 3#抽汽电动阀后旁路疏水阀全关状态 | Bypass drain valve after 3# extraction steam MOV full closed status | 70LBR10AA412 | NO | DI | [10 empty] | SCS | D |  | K0204-004
425 | 70LBR10AA406YB01 | 3#抽汽电动调节阀后疏水阀1打开/关闭指令 | Drain valve 1 after 3# extraction steam regulating MOV open/close command | 70LBR10AA406 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
426 | 70LBR10AA406XB01 | 3#抽汽电动调节阀后疏水阀1全开状态 | Drain valve 1 after 3# extraction steam regulating MOV full opened status | 70LBR10AA406 | NO | DI | [10 empty] | SCS | D |  | K0204-004
427 | 70LBR10AA406XB11 | 3#抽汽电动调节阀后疏水阀1全关状态 | Drain valve 1 after 3# extraction steam regulating MOV full closed status | 70LBR10AA406 | NO | DI | [10 empty] | SCS | D |  | K0204-004
428 | 70LBR10AA408YB01 | 3#抽汽电动调节阀后疏水阀2打开/关闭指令 | Drain valve 2 after 3# extraction steam regulating MOV open/close command | 70LBR10AA408 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
429 | 70LBR10AA408XB01 | 3#抽汽电动调节阀后疏水阀2全开状态 | Drain valve 2 after 3# extraction steam regulating MOV full opened status | 70LBR10AA408 | NO | DI | [10 empty] | SCS | D |  | K0204-004
430 | 70LBR10AA408XB11 | 3#抽汽电动调节阀后疏水阀2全关状态 | Drain valve 2 after 3# extraction steam regulating MOV full closed status | 70LBR10AA408 | NO | DI | [10 empty] | SCS | D |  | K0204-004
431 | 70LBS30CP101 | 4#抽汽蒸汽压力1 | 4# extraction steam pressure 1 | 70LBS30CP101 | 4~20mA | AI | 0~1.0 | MPa | [8 empty] | ETS | D |  | K0204-004
432 | 70LBS30CP102 | 4#抽汽蒸汽压力2 | 4# extraction steam pressure 2 | 70LBS30CP102 | 4~20mA | AI | 0~1.0 | MPa | [8 empty] | DAS | D |  | K0204-004
433 | 70LBS30CT101 | 4#抽汽蒸汽温度 | 4# extraction steam temperature | 70LBS30CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
434 | 70LBS30CT102 | 4#抽汽逆止阀后管顶温度 | Top temperature of pipe after 4# extraction steam check valve | 70LBS30CT102 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
435 | 70LBS30CT103 | 4#抽汽逆止阀后管底温度 | Bottom temperature of pipe after 4# extraction steam check valve | 70LBS30CT103 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
436 | 70LBS30CT104 | 4#抽汽电动调节阀后疏水温度 | Drain temperature after 4# extraction steam regulating MOV | 70LBS30CT104 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
437 | 70LBS30CP103 | 4#低加进汽压力 | 4# LP. heater inlet steam pressure | 70LBS30CP103 | 4~20mA | AI | 0~1.0 | MPa | [8 empty] | MCS | D |  | K0204-004
438 | 70LBS30CT105 | 4#低加进汽温度 | 4# LP. heater inlet steam temperature | 70LBS30CT105 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-004
439 | 70LBS30AA201YB01 | 4#抽汽逆止阀打开/关闭指令 | 4# extraction steam check valve open/close command | 70LBS30AA201 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
440 | 70LBS30AA201XB01 | 4#抽汽逆止阀全开状态 | 4# extraction steam check valve full opened status | 70LBS30AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-004
441 | 70LBS30AA201XB11 | 4#抽汽逆止阀全关状态 | 4# extraction steam check valve full closed status | 70LBS30AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-004
442 | 70LBS30AA101YQ01 | 4#抽汽电动调节阀控制指令 | 4# extraction steam regulating MOV position command | 70LBS30AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-004
443 | 70LBS30AA101XQ11 | 4#抽汽电动调节阀位置指令 | 4# extraction steam regulating MOV position feedback | 70LBS30AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-004
444 | 70LBS30AA402YB01 | 4#抽汽电动调节阀后疏水阀打开/关闭指令 | Drain valve after 4# extraction steam regulating MOV open/close command | 70LBS30AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
445 | 70LBS30AA402XB01 | 4#抽汽电动调节阀后疏水阀全开状态 | Drain valve after 4# extraction steam regulating MOV full opened status | 70LBS30AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-004
446 | 70LBS30AA402XB11 | 4#抽汽电动调节阀后疏水阀全关状态 | Drain valve after 4# extraction steam regulating MOV full closed status | 70LBS30AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-004
447 | 70LBS30AA001YB01 | 4#抽汽电动阀打开指令 | 4# extraction steam MOV open command | 70LBS30AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
448 | 70LBS30AA001YB11 | 4#抽汽电动阀关闭指令 | 4# extraction steam MOV close command | 70LBS30AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
449 | 70LBS30AA001XB01 | 4#抽汽电动阀全开状态 | 4# extraction steam MOV full opened status | 70LBS30AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
450 | 70LBS30AA001XB11 | 4#抽汽电动阀全关状态 | 4# extraction steam MOV full closed status | 70LBS30AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
451 | 70LBS30AA001XB31 | 4#抽汽电动阀故障 | 4# extraction steam MOV fault | 70LBS30AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
452 | 70LBS20CP101 | 5#抽汽蒸汽压力 | 5# extraction steam pressure | 70LBS20CP101 | 4~20mA | AI | 0~0.2 | MPa | [8 empty] | DAS | D |  | K0204-004
453 | 70LBS20CT101 | 5#抽汽蒸汽温度 | 5# extraction steam temperature | 70LBS20CT101 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-004
454 | 70LBS20CT102 | 5#抽汽逆止阀后管顶温度 | Top temperature of pipe after 5# extraction steam check valve | 70LBS20CT102 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-004
455 | 70LBS20CT103 | 5#抽汽逆止阀后管底温度 | Bottom temperature of pipe after 5# extraction steam check valve | 70LBS20CT103 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-004
456 | 70LBS20CT104 | 5#抽汽逆止阀后疏水温度 | Drain temperature after 5# extraction steam check valve | 70LBS20CT104 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-004
457 | 70LBS20CP102 | 5#低加进汽压力 | 5# LP. heater inlet steam pressure | 70LBS20CP102 | 4~20mA | AI | 0~0.2 | MPa | [8 empty] | DAS | D |  | K0204-004
458 | 70LBS20CT105 | 5#低加进汽温度 | 5# LP. heater inlet steam temperature | 70LBS20CT105 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-004
459 | 70LBS20AA201YB01 | 5#抽汽逆止阀打开/关闭指令 | 5# extraction steam check valve open/close command | 70LBS20AA201 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
460 | 70LBS20AA201XB01 | 5#抽汽逆止阀全开状态 | 5# extraction steam check valve full opened status | 70LBS20AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-004
461 | 70LBS20AA201XB11 | 5#抽汽逆止阀全关状态 | 5# extraction steam check valve full closed status | 70LBS20AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-004
462 | 70LBS20AA402YB01 | 5#抽汽逆止阀后疏水阀打开/关闭指令 | Drain valve after 5# extraction steam check valve open/close command | 70LBS20AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
463 | 70LBS20AA402XB01 | 5#抽汽逆止阀后疏水阀全开状态 | Drain valve after 5# extraction steam check valve full opened status | 70LBS20AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-004
464 | 70LBS20AA402XB11 | 5#抽汽逆止阀后疏水阀全关状态 | Drain valve after 5# extraction steam check valve full closed status | 70LBS20AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-004
465 | 70LBS20AA001YB01 | 5#抽汽电动阀打开指令 | 5# extraction steam MOV open command | 70LBS20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
466 | 70LBS20AA001YB11 | 5#抽汽电动阀关闭指令 | 5# extraction steam MOV close command | 70LBS20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
467 | 70LBS20AA001XB01 | 5#抽汽电动阀全开状态 | 5# extraction steam MOV full opened status | 70LBS20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
468 | 70LBS20AA001XB11 | 5#抽汽电动阀全关状态 | 5# extraction steam MOV full closed status | 70LBS20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
469 | 70LBS20AA001XB31 | 5#抽汽电动阀故障 | 5# extraction steam MOV fault | 70LBS20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
470 | 70LBS10CP101 | 6#抽汽蒸汽压力 | 6# extraction steam pressure | 70LBS10CP101 | 4~20mA | AI | 0~0.1 | MPa | [8 empty] | DAS | D |  | K0204-004
471 | 70LBS10CT101 | 6#抽汽蒸汽温度 | 6# extraction steam temperature | 70LBS10CT101 | 4~20mA | AI | 0~100 | ℃ | [8 empty] | DAS | D |  | K0204-004
472 | 70LBS10CT102 | 6#抽汽电动阀前疏水温度 | Drain temperature before 6# extraction steam MOV | 70LBS10CT102 | 4~20mA | AI | 0~100 | ℃ | [8 empty] | DAS | D |  | K0204-004
473 | 70LBS10CT103 | 6#抽汽电动阀后疏水温度 | Drain temperature after 6# extraction steam MOV | 70LBS10CT103 | 4~20mA | AI | 0~100 | ℃ | [8 empty] | DAS | D |  | K0204-004
474 | 70LBS10CT104 | 6#低加进汽温度 | 6# LP. heater inlet steam temperature | 70LBS10CT104 | 4~20mA | AI | 0~100 | ℃ | [8 empty] | DAS | D |  | K0204-004
475 | 70LBS10CP102 | 6#低加进汽压力 | 6# LP. heater inlet steam pressure | 70LBS10CP102 | 4~20mA | AI | 0~0.1 | MPa | [8 empty] | DAS | D |  | K0204-004
476 | 70LBS10AA404YB01 | 6#抽汽电动阀前疏水阀打开/关闭指令 | Drain valve before 6# extraction steam regulating MOV open/close command | 70LBS10AA404 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
477 | 70LBS10AA404XB01 | 6#抽汽电动阀前疏水阀全开状态 | Drain valve before 6# extraction steam regulating MOV full opened status | 70LBS10AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-004
478 | 70LBS10AA404XB11 | 6#抽汽电动阀前疏水阀全关状态 | Drain valve before 6# extraction steam regulating MOV full closed status | 70LBS10AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-004
479 | 70LBS10AA402YB01 | 6#抽汽电动阀后疏水阀打开/关闭指令 | Drain valve after 6# extraction steam regulating MOV open/close command | 70LBS10AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
480 | 70LBS10AA402XB01 | 6#抽汽电动阀后疏水阀全开状态 | Drain valve after 6# extraction steam regulating MOV full opened status | 70LBS10AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-004
481 | 70LBS10AA402XB11 | 6#抽汽电动阀后疏水阀全关状态 | Drain valve after 6# extraction steam regulating MOV full closed status | 70LBS10AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-004
482 | 70LBS10AA001YB01 | 6#抽汽电动阀打开指令 | 6# extraction steam MOV open command | 70LBS10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
483 | 70LBS10AA001YB11 | 6#抽汽电动阀关闭指令 | 6# extraction steam MOV close command | 70LBS10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-004
484 | 70LBS10AA001XB01 | 6#抽汽电动阀全开状态 | 6# extraction steam MOV full opened status | 70LBS10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
485 | 70LBS10AA001XB11 | 6#抽汽电动阀全关状态 | 6# extraction steam MOV full closed status | 70LBS10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
486 | 70LBS10AA001XB31 | 6#抽汽电动阀故障 | 6# extraction steam MOV fault | 70LBS10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-004
487 | 70LBQ20CP101 | 2#抽汽蒸汽压力 | 2# extraction steam pressure | 70LBQ20CP101 | 4~20mA | AI | 0~2.5 | MPa | [8 empty] | DAS | D |  | K0204-005
488 | 70LBQ20CT101 | 2#抽汽蒸汽温度 | 2# extraction steam temperature | 70LBQ20CT101 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-005
489 | 70LBQ20CT102 | 2#抽汽逆止阀后管顶温度 | Top temperature of pipe after 2# extraction steam check valve | 70LBQ20CT102 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-005
490 | 70LBQ20CT103 | 2#抽汽逆止阀后管底温度 | Bottom temperature of pipe after 2# extraction steam check valve | 70LBQ20CT103 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-005
491 | 70LBQ20CP102 | 1#高压加热器进汽压力 | 1# HP heater inlet steam pressure | 70LBQ20CP102 | 4~20mA | AI | 0~2.5 | MPa | [8 empty] | DAS | D |  | K0204-005
492 | 70LBQ20CT105 | 1#高压加热器进汽温度 | 1# HP heater inlet steam temperature | 70LBQ20CT105 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-005
493 | 70LBQ20CT104 | 2#抽汽电动阀前疏水温度 | Drain temperature before 2# extraction steam MOV | 70LBQ20CT104 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-005
494 | 70LBQ20CP103 | #1级非调整抽汽压力 | #1 non-regulated extraction steam pressure | 70LBQ20CP103 | 4~20mA | AI | 0~2.5 | MPa | [8 empty] | DAS | D |  | K0204-005
495 | 70LBQ20CT106 | #1级非调整抽汽温度 | #1 non-regulated extraction steam temperature | 70LBQ20CT106 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-005
496 | 70LBQ20CT107 | #1级非调整抽汽逆止阀后疏水温度1 | Drain temperature 1 after #1 non-regulated extraction steam check valve | 70LBQ20CT107 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-005
497 | 70LBQ20CT108 | #1级非调整抽汽逆止阀后疏水温度2 | Drain temperature 2 after #1 non-regulated extraction steam check valve | 70LBQ20CT108 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-005
498 | 70LBQ20CP104 | #1级非调整抽汽减温减压(C)后蒸汽压力 | Steam pressure after #1 non-regulated extraction steam temperature and pressure reduction(C) | 70LBQ20CP104 | 4~20mA | AI | 0~2.0 | MPa | [8 empty] | MCS | D |  | K0204-005
499 | 70LBQ20CT109 | #1级非调整抽汽减温减压(C)后蒸汽温度 | Steam temperature after #1 non-regulated extraction steam temperature and pressure reduction(C) | 70LBQ20CT109 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | MCS | D |  | K0204-005
500 | 70LBQ20CT110 | #1级非调整抽汽减温减压(C)后疏水温度 | Drain temperature after #1 non-regulated extraction steam temperature and pressure reduction(C) | 70LBQ20CT110 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-005
501 | 70LBQ20CF101 | #1级非调整抽汽减温减压(C)后蒸汽流量 | Steam flow after #1 non-regulated extraction steam temperature and pressure reduction(C) | 70LBQ20CF101 | 4~20mA | AI | 0~60 | t/h | [8 empty] | MCS | D |  | K0204-005
502 | 70LBQ20CP105 | 主蒸汽减温减压(A)后蒸汽压力 | Steam pressure after main steam temperature and pressure reduction(A) | 70LBQ20CP105 | 4~20mA | AI | 0~2.0 | MPa | [8 empty] | MCS | D |  | K0204-005
503 | 70LBQ20CT111 | 主蒸汽减温减压(A)后蒸汽温度 | Steam temperature after main steam temperature and pressure reduction(A) | 70LBQ20CT111 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | MCS | D |  | K0204-005
504 | 70LBQ20CT112 | 主蒸汽中压旁路管道电动阀后疏水温度 | Drain temperature after main steam MP bypass pipe MOV | 70LBQ20CT112 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-005
505 | 70LBQ20CP106 | 中压联箱进汽母管蒸汽压力 | MP steam header inlet main pipe steam pressure | 70LBQ20CP106 | 4~20mA | AI | 0~2.0 | MPa | [8 empty] | DAS | D |  | K0204-005
506 | 70LBQ20CT113 | 中压联箱进汽母管蒸汽温度 | MP steam header inlet main pipe steam temperature | 70LBQ20CT113 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-005
507 | 70LBQ20CF102 | 中压联箱进汽母管蒸汽流量 | MP steam header inlet main pipe steam flow | 70LBQ20CF102 | 4~20mA | AI | 0~60 | t/h | [8 empty] | DAS | D |  | K0204-005
508 | 70LBQ20CT114 | 中压联箱蒸汽温度 | MP steam header steam temperature | 70LBQ20CT114 | K | TC | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-005
509 | 70LBQ20CP107 | 中压联箱蒸汽压力 | MP steam header steam pressure | 70LBQ20CP107 | 4~20mA | AI | 0~2.0 | MPa | [8 empty] | DAS | D |  | K0204-005
510 | 70LBQ20CF103 | 中压联箱至老厂#6机组中压蒸汽管道供热蒸汽流量 | MP steam header to existing MP steam line of #6 unit heating steam flow | 70LBQ20CF103 | 4~20mA | AI | 0~60 | t/h | [8 empty] | DAS | D |  | K0204-005
511 | 70LBQ20CF104 | 中压联箱至低压联箱蒸汽流量 | MP steam header to LP steam header steam flow | 70LBQ20CF104 | 4~20mA | AI | 0~60 | t/h | [8 empty] | DAS | D |  | K0204-005
512 | 70LBQ20CP108 | 中压蒸汽减温减压(E)后蒸汽压力 | Steam pressure after MP steam temperature and pressure reduction(E) | 70LBQ20CP108 | 4~20mA | AI | 0~1.0 | MPa | [8 empty] | MCS | D |  | K0204-005
513 | 70LBQ20CT115 | 中压蒸汽减温减压(E)后蒸汽温度 | Steam temperature after MP steam temperature and pressure reduction(E) | 70LBQ20CT115 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | MCS | D |  | K0204-005
514 | 70LBQ20AA201YB01 | 2#抽汽逆止阀打开/关闭指令 | 2# extraction steam check valve open/close command | 70LBQ20AA201 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
515 | 70LBQ20AA201XB01 | 2#抽汽逆止阀全开状态 | 2# extraction steam check valve full opened status | 70LBQ20AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-005
516 | 70LBQ20AA201XB11 | 2#抽汽逆止阀全关状态 | 2# extraction steam check valve full closed status | 70LBQ20AA201 | NO | DI | [10 empty] | SCS | D |  | K0204-005
517 | 70LBQ20AA402YB01 | 2#抽汽电动阀前疏水阀打开/关闭指令 | 2# extraction steam MOV front drain vlave open/close command | 70LBQ20AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
518 | 70LBQ20AA402XB01 | 2#抽汽电动阀前疏水阀全开状态 | 2# extraction steam MOV front drain vlave full opened status | 70LBQ20AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-005
519 | 70LBQ20AA402XB11 | 2#抽汽电动阀前疏水阀全关状态 | 2# extraction steam MOV front drain vlave full closed status | 70LBQ20AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-005
520 | 70LBQ20AA001YB01 | 2#抽汽电动阀打开指令 | 2# extraction steam MOV open command | 70LBQ20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
521 | 70LBQ20AA001YB11 | 2#抽汽电动阀关闭指令 | 2# extraction steam MOV close command | 70LBQ20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
522 | 70LBQ20AA001XB01 | 2#抽汽电动阀全开状态 | 2# extraction steam MOV full opened status | 70LBQ20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-005
523 | 70LBQ20AA001XB11 | 2#抽汽电动阀全关状态 | 2# extraction steam MOV full closed status | 70LBQ20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-005
524 | 70LBQ20AA001XB31 | 2#抽汽电动阀故障 | 2# extraction steam MOV fault | 70LBQ20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-005
525 | 70LBQ20AA203YB01 | #1级非调整抽汽逆止阀打开/关闭指令 | #1 non-regulated extraction steam check valve open/close command | 70LBQ20AA203 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
526 | 70LBQ20AA203XB01 | #1级非调整抽汽逆止阀全开状态 | #1 non-regulated extraction steam check valve full opened status | 70LBQ20AA203 | NO | DI | [10 empty] | SCS | D |  | K0204-005
527 | 70LBQ20AA203XB11 | #1级非调整抽汽逆止阀全关状态 | #1 non-regulated extraction steam check valve full closed status | 70LBQ20AA203 | NO | DI | [10 empty] | SCS | D |  | K0204-005
528 | 70LBQ20AA404YB01 | #1级非调整抽汽逆止阀后疏水阀1打开/关闭指令 | Drain valve 1 after #1 non-regulated extraction steam check valve open/close command | 70LBQ20AA404 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
529 | 70LBQ20AA404XB01 | #1级非调整抽汽逆止阀后疏水阀1全开状态 | Drain valve 1 after #1 non-regulated extraction steam check valve full opened status | 70LBQ20AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-005
530 | 70LBQ20AA404XB11 | #1级非调整抽汽逆止阀后疏水阀1全关状态 | Drain valve 1 after #1 non-regulated extraction steam check valve full closed status | 70LBQ20AA404 | NO | DI | [10 empty] | SCS | D |  | K0204-005
531 | 70LBQ20AA406YB01 | #1级非调整抽汽逆止阀后疏水阀2打开/关闭指令 | Drain valve 2 after #1 non-regulated extraction steam check valve open/close command | 70LBQ20AA406 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
532 | 70LBQ20AA406XB01 | #1级非调整抽汽逆止阀后疏水阀2全开状态 | Drain valve 2 after #1 non-regulated extraction steam check valve full opened status | 70LBQ20AA406 | NO | DI | [10 empty] | SCS | D |  | K0204-005
533 | 70LBQ20AA406XB11 | #1级非调整抽汽逆止阀后疏水阀2全关状态 | Drain valve 2 after #1 non-regulated extraction steam check valve full closed status | 70LBQ20AA406 | NO | DI | [10 empty] | SCS | D |  | K0204-005
534 | 70LBQ20AA102YQ01 | #1级非调整抽汽减温减压器C电动减压调节阀控制指令 | #1 non-regulated extraction steam pressure reducer desuperheater C pressure reduciong regulating MOV position command | 70LBQ20AA102 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-005
535 | 70LBQ20AA102XQ11 | #1级非调整抽汽减温减压器C电动减压调节阀位置反馈 | #1 non-regulated extraction steam pressure reducer desuperheater C pressure reduciong regulating MOV position feddback | 70LBQ20AA102 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-005
536 | 70LBQ20AA101YQ01 | #1级非调整抽汽减温减压器C电动减温调节阀控制指令 | #1 non-regulated extraction steam pressure reducer desuperheater C temperature reduciong regulating MOV position command | 70LBQ20AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-005
537 | 70LBQ20AA101XQ11 | #1级非调整抽汽减温减压器C电动减温调节阀位置反馈 | #1 non-regulated extraction steam pressure reducer desuperheater C temperature reduciong regulating MOV position feddback | 70LBQ20AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-005
538 | 70LBQ20AA418YB01 | #1级非调整抽汽减温减压(C)后疏水阀打开/关闭指令 | Drain valve after #1 non-regulated extraction steam temperature and pressure reduction(C) open/close command | 70LBQ20AA418 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
539 | 70LBQ20AA418XB01 | #1级非调整抽汽减温减压(C)后疏水阀全开状态 | Drain valve after #1 non-regulated extraction steam temperature and pressure reduction(C) full opened status | 70LBQ20AA418 | NO | DI | [10 empty] | SCS | D |  | K0204-005
540 | 70LBQ20AA418XB11 | #1级非调整抽汽减温减压(C)后疏水阀全关状态 | Drain valve after #1 non-regulated extraction steam temperature and pressure reduction(C) full closed status | 70LBQ20AA418 | NO | DI | [10 empty] | SCS | D |  | K0204-005
541 | 70LBQ20AA002YB01 | #1级非调整抽汽电动阀打开指令 | #1 non-regulated extraction steam MOV open command | 70LBQ20AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
542 | 70LBQ20AA002YB11 | #1级非调整抽汽电动阀关闭指令 | #1 non-regulated extraction steam MOV close command | 70LBQ20AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
543 | 70LBQ20AA002XB01 | #1级非调整抽汽电动阀全开状态 | #1 non-regulated extraction steam MOV full opened status | 70LBQ20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-005
544 | 70LBQ20AA002XB11 | #1级非调整抽汽电动阀全关状态 | #1 non-regulated extraction steam MOV full closed status | 70LBQ20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-005
545 | 70LBQ20AA002XB31 | #1级非调整抽汽电动阀故障 | #1 non-regulated extraction steam MOV fault | 70LBQ20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-005
546 | 70LBQ20AA104YQ01 | 主蒸汽减温减压器A电动减压调节阀控制指令 | Main steam pressure reducer desuperheater A pressure reduciong regulating MOV position command | 70LBQ20AA104 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-005
547 | 70LBQ20AA104XQ11 | 主蒸汽减温减压器A电动减压调节阀位置反馈 | Main steam pressure reducer desuperheater A pressure reduciong regulating MOV position feddback | 70LBQ20AA104 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-005
548 | 70LBQ20AA103YQ01 | 主蒸汽减温减压器A电动减温调节阀控制指令 | Main steam pressure reducer desuperheater A temperature reduciong regulating MOV position command | 70LBQ20AA103 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-005
549 | 70LBQ20AA103XQ11 | 主蒸汽减温减压器A电动减温调节阀位置反馈 | Main steam pressure reducer desuperheater A temperature reduciong regulating MOV position feddback | 70LBQ20AA103 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-005
550 | 70LBQ20AA003YB01 | 主蒸汽中压旁路管道电动阀打开指令 | Main steam MP bypass pipe MOV open command | 70LBQ20AA003 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
551 | 70LBQ20AA003YB11 | 主蒸汽中压旁路管道电动阀关闭指令 | Main steam MP bypass pipe MOV close command | 70LBQ20AA003 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
552 | 70LBQ20AA003XB01 | 主蒸汽中压旁路管道电动阀全开状态 | Main steam MP bypass pipe MOV full opened status | 70LBQ20AA003 | NO | DI | [10 empty] | SCS | D |  | K0204-005
553 | 70LBQ20AA003XB11 | 主蒸汽中压旁路管道电动阀全关状态 | Main steam MP bypass pipe MOV full closed status | 70LBQ20AA003 | NO | DI | [10 empty] | SCS | D |  | K0204-005
554 | 70LBQ20AA003XB31 | 主蒸汽中压旁路管道电动阀故障 | Main steam MP bypass pipe MOV fault | 70LBQ20AA003 | NO | DI | [10 empty] | SCS | D |  | K0204-005
555 | 70LBR20AA416YB01 | 主蒸汽中压旁路管道电动阀后疏水阀打开/关闭指令 | Drain valve after main steam MP bypass pipe MOV open/close command | 70LBR20AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
556 | 70LBR20AA416XB01 | 主蒸汽中压旁路管道电动阀后疏水阀全开状态 | Drain valve after main steam MP bypass pipe MOV full opened status | 70LBR20AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-005
557 | 70LBR20AA416XB11 | 主蒸汽中压旁路管道电动阀后疏水阀全关状态 | Drain valve after main steam MP bypass pipe MOV full closed status | 70LBR20AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-005
558 | 70LBQ20AA106YQ01 | 中压联箱至低压联箱减温减压器E电动减压调节阀控制指令 | MP steam header to LP steam header pressure reducer desuperheater E pressure reduciong regulating MOV position command | 70LBQ20AA106 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-005
559 | 70LBQ20AA106XQ11 | 中压联箱至低压联箱减温减压器E电动减压调节阀位置反馈 | MP steam header to LP steam header pressure reducer desuperheater E pressure reduciong regulating MOV position feddback | 70LBQ20AA106 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-005
560 | 70LBQ20AA105YQ01 | 中压联箱至低压联箱减温减压器E电动减温调节阀控制指令 | MP steam header to LP steam header pressure reducer desuperheater E temperature reduciong regulating MOV position command | 70LBQ20AA105 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-005
561 | 70LBQ20AA105XQ11 | 中压联箱至低压联箱减温减压器E电动减温调节阀位置反馈 | MP steam header to LP steam header pressure reducer desuperheater E temperature reduciong regulating MOV position feddback | 70LBQ20AA105 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-005
562 | 70LBQ20AA004YB01 | 中压联箱启动排汽电动阀打开指令 | MP steam header start exhaust MOV open command | 70LBQ20AA004 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
563 | 70LBQ20AA004YB11 | 中压联箱启动排汽电动阀关闭指令 | MP steam header start exhaust MOV close command | 70LBQ20AA004 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-005
564 | 70LBQ20AA004XB01 | 中压联箱启动排汽电动阀全开状态 | MP steam header start exhaust MOV full opened status | 70LBQ20AA004 | NO | DI | [10 empty] | SCS | D |  | K0204-005
565 | 70LBQ20AA004XB11 | 中压联箱启动排汽电动阀全关状态 | MP steam header start exhaust MOV full closed status | 70LBQ20AA004 | NO | DI | [10 empty] | SCS | D |  | K0204-005
566 | 70LBQ20AA004XB31 | 中压联箱启动排汽电动阀故障 | MP steam header start exhaust MOV fault | 70LBQ20AA004 | NO | DI | [10 empty] | SCS | D |  | K0204-005
567 | 70LAB20CT101 | 电动给水泵A电机定子线圈U向温度1 | Electrical feedwater pump A motor stator winding U temp.1 | 70LAB20GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
568 | 70LAB20CT102 | 电动给水泵A电机定子线圈U向温度2 | Electrical feedwater pump A motor stator winding U temp.2 | 70LAB20GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
569 | 70LAB20CT103 | 电动给水泵A电机定子线圈V向温度1 | Electrical feedwater pump A motor stator winding V temp.1 | 70LAB20GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
570 | 70LAB20CT104 | 电动给水泵A电机定子线圈V向温度2 | Electrical feedwater pump A motor stator winding V temp.2 | 70LAB20GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
571 | 70LAB20CT105 | 电动给水泵A电机定子线圈W向温度1 | Electrical feedwater pump A motor stator winding W temp.1 | 70LAB20GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
572 | 70LAB20CT106 | 电动给水泵A电机定子线圈W向温度2 | Electrical feedwater pump A motor stator winding W temp.2 | 70LAB20GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
573 | 70LAB20CT107 | 电动给水泵A电机自由端轴承温度 | Electrical feedwater pump A motor free end bearing temp. | 70LAB20GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
574 | 70LAB20CT108 | 电动给水泵A电机传动端轴承温度 | Electrical feedwater pump A motor drive end bearing Temp. | 70LAB20GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A电机接线盒 | Electrical feedwater pump A motor JB
575 | 70LAB20CT109 | 电动给水泵A自由端轴承温度 | Electrical feedwater pump A free end bearing temp. | 70LAB20GH002 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A仪表接线箱 | Electrical feedwater pump A instrument junction box
576 | 70LAB20CT110 | 电动给水泵A传动端轴承温度 | Electrical feedwater pump A drive end bearing temp. | 70LAB20GH002 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A仪表接线箱 | Electrical feedwater pump A instrument junction box
577 | 70LAB20CT111 | 电动给水泵A自由端机封冲洗水温度 | Electrical feedwater pump A motor free end machine seal flushing water Temp. | 70LAB20GH002 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A仪表接线箱 | Electrical feedwater pump A instrument junction box
578 | 70LAB20CT112 | 电动给水泵A传动端机封冲洗水温度 | Electrical feedwater pump A motor drive end machine seal flushing water Temp. | 70LAB20GH002 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A仪表接线箱 | Electrical feedwater pump A instrument junction box
579 | 70LAB20CP001H | 电动给水泵A入口滤网差压高 | Electrical feedwater pump A inlet filter DP H | 70LAB20GH002 | NO | DI | 30 | KPa | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵A仪表接线箱 | Electrical feedwater pump A instrument junction box | bar: H
580 | 70LAB10CT101 | 电动给水泵B电机定子线圈U向温度1 | Electrical feedwater pump B motor stator winding U temp.1 | 70LAB10GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
581 | 70LAB10CT102 | 电动给水泵B电机定子线圈U向温度2 | Electrical feedwater pump B motor stator winding U temp.2 | 70LAB10GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
582 | 70LAB10CT103 | 电动给水泵B电机定子线圈V向温度1 | Electrical feedwater pump B motor stator winding V temp.1 | 70LAB10GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
583 | 70LAB10CT104 | 电动给水泵B电机定子线圈V向温度2 | Electrical feedwater pump B motor stator winding V temp.2 | 70LAB10GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
584 | 70LAB10CT105 | 电动给水泵B电机定子线圈W向温度1 | Electrical feedwater pump B motor stator winding W temp.1 | 70LAB10GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
585 | 70LAB10CT106 | 电动给水泵B电机定子线圈W向温度2 | Electrical feedwater pump B motor stator winding W temp.2 | 70LAB10GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
586 | 70LAB10CT107 | 电动给水泵B电机自由端轴承温度 | Electrical feedwater pump B motor free end bearing temp. | 70LAB10GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
587 | 70LAB10CT108 | 电动给水泵B电机传动端轴承温度 | Electrical feedwater pump B motor drive end bearing Temp. | 70LAB10GH001 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B电机接线盒 | Electrical feedwater pump B motor JB
588 | 70LAB10CT109 | 电动给水泵B自由端轴承温度 | Electrical feedwater pump B free end bearing temp. | 70LAB10GH002 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B仪表接线箱 | Electrical feedwater pump B instrument junction box
589 | 70LAB10CT110 | 电动给水泵B传动端轴承温度 | Electrical feedwater pump B drive end bearing temp. | 70LAB10GH002 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B仪表接线箱 | Electrical feedwater pump B instrument junction box
590 | 70LAB10CT111 | 电动给水泵B自由端机封冲洗水温度 | Electrical feedwater pump B motor free end machine seal flushing water Temp. | 70LAB10GH002 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B仪表接线箱 | Electrical feedwater pump B instrument junction box
591 | 70LAB10CT112 | 电动给水泵B传动端机封冲洗水温度 | Electrical feedwater pump B motor drive end machine seal flushing water Temp. | 70LAB10GH002 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B仪表接线箱 | Electrical feedwater pump B instrument junction box
592 | 70LAB10CP001H | 电动给水泵B入口滤网差压高 | Electrical feedwater pump B inlet filter DP H | 70LAB10GH002 | NO | DI | 30 | KPa | [8 empty] | SCS | D |  | K0204-006 | 电动给水泵B仪表接线箱 | Electrical feedwater pump B instrument junction box | bar: H
593 | 70LAB20CP101 | 电动给水泵A入口压力 | Electrical feedwater pump A inlet pressure | 70LAB20CP101 | 4~20mA | AI | 0~1.0 | MPa | [8 empty] | SCS | D |  | K0204-006
594 | 70LAB20CT113 | 电动给水泵A入口温度 | Electrical feedwater pump A inlet temp. | 70LAB20CT113 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-006
595 | 70LAB20CP102 | 电动给水泵A出口压力 | Electrical feedwater pump A outlet pressure | 70LAB20CP102 | 4~20mA | AI | 0~24 | MPa | [8 empty] | SCS | D |  | K0204-006
596 | 70LAB10CP101 | 电动给水泵B入口压力 | Electrical feedwater pump B inlet pressure | 70LAB10CP101 | 4~20mA | AI | 0~1.0 | MPa | [8 empty] | SCS | D |  | K0204-006
597 | 70LAB10CT113 | 电动给水泵B入口温度 | Electrical feedwater pump B inlet temp. | 70LAB10CT113 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-006
598 | 70LAB10CP102 | 电动给水泵B出口压力 | Electrical feedwater pump B outlet pressure | 70LAB10CP102 | 4~20mA | AI | 0~24 | MPa | [8 empty] | DAS | D |  | K0204-006
599 | 70LAB50CP101 | 电动给水泵出口母管压力 | Electrical feedwater pump outlet main pipe pressure | 70LAB50CP101 | 4~20mA | AI | 0~24 | MPa | [8 empty] | DAS | D |  | K0204-006
600 | 70LAB50CT101 | 电动给水泵出口母管温度 | Electrical feedwater pump outlet main pipe temp. | 70LAB50CT101 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-006
601 | 70LAB50CT102 | 1#高加入口给水温度 | 1# HP heater inlet feedwater temp. | 70LAB50CT102 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-006
602 | 70LAB60CT101 | 1#高加出口给水温度 | 1# HP heater outlet feedwater temp. | 70LAB60CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-006
603 | 70LAB70CT101 | 2#高加出口给水温度 | 2# HP heater outlet feedwater temp. | 70LAB70CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-006
604 | 70LAB20AP001YB01 | 电动给水泵A启动指令 | Electrical feedwater pump A start command | 70LAB20AP001 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
605 | 70LAB20AP001YB11 | 电动给水泵A停止指令 | Electrical feedwater pump A stop command | 70LAB20AP001 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
606 | 70LAB20AP001XB01 | 电动给水泵A断路器合闸信号 | Electrical feedwater pump A breaker closing | 70LAB20AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
607 | 70LAB20AP001XB11 | 电动给水泵A断路器跳闸信号 | Electrical feedwater pump A breaker tripping | 70LAB20AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
608 | 70LAB20AP001XB21 | 电动给水泵A远控允许 | Electrical feedwater pump A remote operation allowable | 70LAB20AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
609 | 70LAB20AP001XB31 | 电动给水泵A弹簧未储能 | Electrical feedwater pump A spring charge | 70LAB20AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
610 | 70LAB20AP001XB32 | 电动给水泵A装置故障 | Electrical feedwater pump A device fault | 70LAB20AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
611 | 70LAB20AP001XB33 | 电动给水泵A保护动作 | Electrical feedwater pump A trip Output | 70LAB20AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
612 | 70LAB20AP001XB34 | 电动给水泵A控制回路断线 | Electrical feedwater pump A control circuit loss power | 70LAB20AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
613 | 70LAB20AP001XB12 | 电动给水泵A断路器跳闸信号(SOE) | Electrical feedwater pump A breaker tripping(SOE) | 70LAB20AP001 | NO | SOE | [10 empty] | SOE | D |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
614 | 70LAB20AP001XQ01 | 电动给水泵A断路器电流 | Electrical feedwater pump A current | 70LAB20AP001 | 4~20mA | AI |  | A | [8 empty] | DAS | U |  | K0204-006 | 电动给水泵A 6KV开关柜 | Electrical feedwater pump A 6KV switch cabinet
615 | 70LAB10AP001YB01 | 电动给水泵B启动指令 | Electrical feedwater pump B start command | 70LAB10AP001 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
616 | 70LAB10AP001YB11 | 电动给水泵B停止指令 | Electrical feedwater pump B stop command | 70LAB10AP001 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
617 | 70LAB10AP001XB01 | 电动给水泵B断路器合闸信号 | Electrical feedwater pump B breaker closing | 70LAB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
618 | 70LAB10AP001XB11 | 电动给水泵B断路器跳闸信号 | Electrical feedwater pump B breaker tripping | 70LAB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
619 | 70LAB10AP001XB21 | 电动给水泵B远控允许 | Electrical feedwater pump B remote operation allowable | 70LAB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
620 | 70LAB10AP001XB31 | 电动给水泵B弹簧未储能 | Electrical feedwater pump B spring charge | 70LAB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
621 | 70LAB10AP001XB32 | 电动给水泵B装置故障 | Electrical feedwater pump B device fault | 70LAB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
622 | 70LAB10AP001XB33 | 电动给水泵B保护动作 | Electrical feedwater pump B trip Output | 70LAB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
623 | 70LAB10AP001XB34 | 电动给水泵B控制回路断线 | Electrical feedwater pump B control circuit loss power | 70LAB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
624 | 70LAB10AP001XB12 | 电动给水泵B断路器跳闸信号(SOE) | Electrical feedwater pump B breaker tripping(SOE) | 70LAB10AP001 | NO | SOE | [10 empty] | SOE | D |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
625 | 70LAB10AP001XQ01 | 电动给水泵B断路器电流 | Electrical feedwater pump B current | 70LAB10AP001 | 4~20mA | AI |  | A | [8 empty] | DAS | U |  | K0204-006 | 电动给水泵B 6KV开关柜 | Electrical feedwater pump B 6KV switch cabinet
626 | 70LAB40AA002YB01 | 电动给水泵A出口电动阀打开指令 | Electrical feedwater pump A outlet MOV open command | 70LAB40AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
627 | 70LAB40AA002YB11 | 电动给水泵A出口电动阀关闭指令 | Electrical feedwater pump A outlet MOV close command | 70LAB40AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
628 | 70LAB40AA002XB01 | 电动给水泵A出口电动阀全开状态 | Electrical feedwater pump A outlet MOV full opened status | 70LAB40AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-006
629 | 70LAB40AA002XB11 | 电动给水泵A出口电动阀全关状态 | Electrical feedwater pump A outlet MOV full closed status | 70LAB40AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-006
630 | 70LAB40AA002XB31 | 电动给水泵A出口电动阀故障 | Electrical feedwater pump A outlet MOV fault | 70LAB40AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-006
631 | 70LAB30AA002YB01 | 电动给水泵B出口电动阀打开指令 | Electrical feedwater pump B outlet MOV open command | 70LAB30AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
632 | 70LAB30AA002YB11 | 电动给水泵B出口电动阀关闭指令 | Electrical feedwater pump B outlet MOV close command | 70LAB30AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
633 | 70LAB30AA002XB01 | 电动给水泵B出口电动阀全开状态 | Electrical feedwater pump B outlet MOV full opened status | 70LAB30AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-006
634 | 70LAB30AA002XB11 | 电动给水泵B出口电动阀全关状态 | Electrical feedwater pump B outlet MOV full closed status | 70LAB30AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-006
635 | 70LAB30AA002XB31 | 电动给水泵B出口电动阀故障 | Electrical feedwater pump B outlet MOV fault | 70LAB30AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-006
636 | 70LAH10AA001YB01 | 电动给水泵A给水再循环电动阀打开指令 | Electrical feedwater pump A feedwater recycling MOV open command | 70LAH10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
637 | 70LAH10AA001YB11 | 电动给水泵A给水再循环电动阀关闭指令 | Electrical feedwater pump A feedwater recycling MOV close command | 70LAH10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
638 | 70LAH10AA001XB01 | 电动给水泵A给水再循环电动阀全开状态 | Electrical feedwater pump A feedwater recycling MOV full opened status | 70LAH10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
639 | 70LAH10AA001XB11 | 电动给水泵A给水再循环电动阀全关状态 | Electrical feedwater pump A feedwater recycling MOV full closed status | 70LAH10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
640 | 70LAH10AA001XB31 | 电动给水泵A给水再循环电动阀故障 | Electrical feedwater pump A feedwater recycling MOV fault | 70LAH10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
641 | 70LAH20AA001YB01 | 电动给水泵B给水再循环电动阀打开指令 | Electrical feedwater pump B feedwater recycling MOV open command | 70LAH20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
642 | 70LAH20AA001YB11 | 电动给水泵B给水再循环电动阀关闭指令 | Electrical feedwater pump B feedwater recycling MOV close command | 70LAH20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
643 | 70LAH20AA001XB01 | 电动给水泵B给水再循环电动阀全开状态 | Electrical feedwater pump B feedwater recycling MOV full opened status | 70LAH20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
644 | 70LAH20AA001XB11 | 电动给水泵B给水再循环电动阀全关状态 | Electrical feedwater pump B feedwater recycling MOV full closed status | 70LAH20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
645 | 70LAH20AA001XB31 | 电动给水泵B给水再循环电动阀故障 | Electrical feedwater pump B feedwater recycling MOV fault | 70LAH20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
646 | 70LAB50AA001YB01 | 1#高加入口给水电动阀打开指令 | 1# HP heater inlet feedwater MOV open command | 70LAB50AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
647 | 70LAB50AA001YB11 | 1#高加入口给水电动阀关闭指令 | 1# HP heater inlet feedwater MOV close command | 70LAB50AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
648 | 70LAB50AA001XB01 | 1#高加入口给水电动阀全开状态 | 1# HP heater inlet feedwater MOV full opened status | 70LAB50AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
649 | 70LAB50AA001XB11 | 1#高加入口给水电动阀全关状态 | 1# HP heater inlet feedwater MOV full closed status | 70LAB50AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
650 | 70LAB50AA001XB31 | 1#高加入口给水电动阀故障 | 1# HP heater inlet feedwater MOV fault | 70LAB50AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
651 | 70LAB70AA001YB01 | 2#高加出口给水电动阀打开指令 | 2# HP heater outlet feedwater MOV open command | 70LAB70AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
652 | 70LAB70AA001YB11 | 2#高加出口给水电动阀关闭指令 | 2# HP heater outlet feedwater MOV close command | 70LAB70AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
653 | 70LAB70AA001XB01 | 2#高加出口给水电动阀全开状态 | 2# HP heater outlet feedwater MOV full opened status | 70LAB70AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
654 | 70LAB70AA001XB11 | 2#高加出口给水电动阀全关状态 | 2# HP heater outlet feedwater MOV full closed status | 70LAB70AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
655 | 70LAB70AA001XB31 | 2#高加出口给水电动阀故障 | 2# HP heater outlet feedwater MOV fault | 70LAB70AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
656 | 70LAB51AA001YB01 | 高加给水旁路电动阀打开指令 | HP feedwater bypass MOV open command | 70LAB51AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
657 | 70LAB51AA001YB11 | 高加给水旁路电动阀关闭指令 | HP feedwater bypass MOV close command | 70LAB51AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
658 | 70LAB51AA001XB01 | 高加给水旁路电动阀全开状态 | HP feedwater bypass MOV full opened status | 70LAB51AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
659 | 70LAB51AA001XB11 | 高加给水旁路电动阀全关状态 | HP feedwater bypass MOV full closed status | 70LAB51AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
660 | 70LAB51AA001XB31 | 高加给水旁路电动阀故障 | HP feedwater bypass MOV fault | 70LAB51AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
661 | 70LAB80AA001YB01 | 7#机组至8#机组给水电动阀打开指令 | 7# unit to 8# unit feedwater MOV open command | 70LAB80AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
662 | 70LAB80AA001YB11 | 7#机组至8#机组给水电动阀关闭指令 | 7# unit to 8# unit feedwater MOV close command | 70LAB80AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-006
663 | 70LAB80AA001XB01 | 7#机组至8#机组给水电动阀全开状态 | 7# unit to 8# unit feedwater MOV full opened status | 70LAB80AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
664 | 70LAB80AA001XB11 | 7#机组至8#机组给水电动阀全关状态 | 7# unit to 8# unit feedwater MOV full closed status | 70LAB80AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
665 | 70LAB80AA001XB31 | 7#机组至8#机组给水电动阀故障 | 7# unit to 8# unit feedwater MOV fault | 70LAB80AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-006
666 | 70LAB20CT121 | 电动给水泵A液力耦合器1#轴瓦温度 | Electrical feedwater pump A coupler 1# bearing temperature | 70LAB20CT121 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
667 | 70LAB20CT122 | 电动给水泵A液力耦合器2#轴瓦温度 | Electrical feedwater pump A coupler 2# bearing temperature | 70LAB20CT122 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
668 | 70LAB20CT123 | 电动给水泵A液力耦合器3#轴瓦温度 | Electrical feedwater pump A coupler 3# bearing temperature | 70LAB20CT123 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
669 | 70LAB20CT124 | 电动给水泵A液力耦合器4#轴瓦温度 | Electrical feedwater pump A coupler 4# bearing temperature | 70LAB20CT124 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
670 | 70LAB20CT125 | 电动给水泵A液力耦合器5#轴瓦温度 | Electrical feedwater pump A coupler 5# bearing temperature | 70LAB20CT125 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
671 | 70LAB20CT126 | 电动给水泵A液力耦合器6#轴瓦温度 | Electrical feedwater pump A coupler 6# bearing temperature | 70LAB20CT126 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
672 | 70LAB20CP121 | 电动给水泵A液力耦合器工作油出油压力 | Electrical feedwater pump A coupler work oil outlet pressure | 70LAB20CP121 | 4~20mA | AI | 0~0.6 | MPa | [8 empty] | SCS | D |  | K0204-007
673 | 70LAB20CT127 | 电动给水泵A液力耦合器工作油出油温度 | Electrical feedwater pump A coupler work oil outlet temperature | 70LAB20CT127 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-007
674 | 70LAB20CT128 | 电动给水泵A液力耦合器工作油进油温度 | Electrical feedwater pump A coupler work oil inlet temperature | 70LAB20CT128 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-007
675 | 70LAB20CP122 | 电动给水泵A液力耦合器滤清器出口油压 | Electrical feedwater pump A coupler percolator outlet oil pressure | 70LAB20CP122 | 4~20mA | AI | 0~0.6 | MPa | [8 empty] | SCS | D |  | K0204-007
676 | 70LAB20CP123 | 电动给水泵A液力耦合器直流润滑油泵出口压力 | Electrical feedwater pump A coupler DC lube oil pump outlet pressure | 70LAB20CP123 | 4~20mA | AI | 0~0.6 | MPa | [8 empty] | SCS | D |  | K0204-007
677 | 70LAB20CT129 | 电动给水泵A液力耦合器直流润滑油泵出口温度 | Electrical feedwater pump A coupler DC lube oil pump outlet temperature | 70LAB20CT129 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-007
678 | 70LAB20CS121 | 电动给水泵A液力耦合器输出转速 | Electrical feedwater pump A coupler outlet speed | 70LAB20CS121 | 4~20mA | AI | [10 empty] | MCS | U |  | K0204-007
679 | 70LAB20AP021YB01 | 电动给水泵A液力耦合器直流润滑油泵启动指令 | Electrical feedwater pump A coupler DC lube oil pump start command | 70LAB20AP021 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-007
680 | 70LAB20AP021YB11 | 电动给水泵A液力耦合器直流润滑油泵停止指令 | Electrical feedwater pump A coupler DC lube oil pump stop command | 70LAB20AP021 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-007
681 | 70LAB20AP021XB01 | 电动给水泵A液力耦合器直流润滑油泵运行 | Electrical feedwater pump A coupler DC lube oil pump running | 70LAB20AP021 | NO | DI | [10 empty] | SCS | D |  | K0204-007
682 | 70LAB20AP021XB11 | 电动给水泵A液力耦合器直流润滑油泵停止 | Electrical feedwater pump A coupler DC lube oil pump stopped | 70LAB20AP021 | NO | DI | [10 empty] | SCS | D |  | K0204-007
683 | 70LAB20AP021XB21 | 电动给水泵A液力耦合器直流润滑油泵远方控制允许 | Electrical feedwater pump A coupler DC lube oil pump remote control permitted | 70LAB20AP021 | NO | DI | [10 empty] | SCS | D |  | K0204-007
684 | 70LAB20AP021XB31 | 电动给水泵A液力耦合器直流润滑油泵故障 | Electrical feedwater pump A coupler DC lube oil pump fault | 70LAB20AP021 | NO | DI | [10 empty] | SCS | D |  | K0204-007
685 | 70LAB20AP022YB01 | 电动给水泵A液力耦合器交流润滑油泵启动指令 | Electrical feedwater pump A coupler AC lube oil pump start command | 70LAB20AP022 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-007
686 | 70LAB20AP022YB11 | 电动给水泵A液力耦合器交流润滑油泵停止指令 | Electrical feedwater pump A coupler AC lube oil pump stop command | 70LAB20AP022 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-007
687 | 70LAB20AP022XB01 | 电动给水泵A液力耦合器交流润滑油泵运行 | Electrical feedwater pump A coupler AC lube oil pump running | 70LAB20AP022 | NO | DI | [10 empty] | SCS | D |  | K0204-007
688 | 70LAB20AP022XB11 | 电动给水泵A液力耦合器交流润滑油泵停止 | Electrical feedwater pump A coupler AC lube oil pump stopped | 70LAB20AP022 | NO | DI | [10 empty] | SCS | D |  | K0204-007
689 | 70LAB20AP022XB21 | 电动给水泵A液力耦合器交流润滑油泵远方控制允许 | Electrical feedwater pump A coupler AC lube oil pump remote control permitted | 70LAB20AP022 | NO | DI | [10 empty] | SCS | D |  | K0204-007
690 | 70LAB20AP022XB31 | 电动给水泵A液力耦合器交流润滑油泵控制电源消失 | Electrical feedwater pump A coupler AC lube oil pump control circuit broken | 70LAB20AP022 | NO | DI | [10 empty] | SCS | D |  | K0204-007
691 | 70LAB20AP022XB32 | 电动给水泵A液力耦合器交流润滑油泵故障输出 | Electrical feedwater pump A coupler AC lube oil pump fault output | 70LAB20AP022 | NO | DI | [10 empty] | SCS | D |  | K0204-007
692 | 70LAB20AA121YQ01 | 电动给水泵A液力耦合器电动调节阀控制指令 | Electrical feedwater pump A coupler regulating MOV position command | 70LAB20AA121 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-007
693 | 70LAB20AA121XQ11 | 电动给水泵A液力耦合器电动调节阀位置反馈 | Electrical feedwater pump A coupler regulating MOV position feedback | 70LAB20AA121 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-007
694 | 70LAB10CT121 | 电动给水泵B液力耦合器1#轴瓦温度 | Electrical feedwater pump Bcoupler 1# bearing temperature | 70LAB10CT121 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
695 | 70LAB10CT122 | 电动给水泵B液力耦合器2#轴瓦温度 | Electrical feedwater pump Bcoupler 2# bearing temperature | 70LAB10CT122 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
696 | 70LAB10CT123 | 电动给水泵B液力耦合器3#轴瓦温度 | Electrical feedwater pump Bcoupler 3# bearing temperature | 70LAB10CT123 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
697 | 70LAB10CT124 | 电动给水泵B液力耦合器4#轴瓦温度 | Electrical feedwater pump Bcoupler 4# bearing temperature | 70LAB10CT124 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
698 | 70LAB10CT125 | 电动给水泵B液力耦合器5#轴瓦温度 | Electrical feedwater pump Bcoupler 5# bearing temperature | 70LAB10CT125 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
699 | 70LAB10CT126 | 电动给水泵B液力耦合器6#轴瓦温度 | Electrical feedwater pump Bcoupler 6# bearing temperature | 70LAB10CT126 | PT100 | RTD | 0~200 | ℃ | [8 empty] | SCS | D |  | K0204-007
700 | 70LAB10CP121 | 电动给水泵B液力耦合器工作油出油压力 | Electrical feedwater pump Bcoupler work oil outlet pressure | 70LAB10CP121 | 4~20mA | AI | 0~0.6 | MPa | [8 empty] | SCS | D |  | K0204-007
701 | 70LAB10CT127 | 电动给水泵B液力耦合器工作油出油温度 | Electrical feedwater pump Bcoupler work oil outlet temperature | 70LAB10CT127 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-007
702 | 70LAB10CT128 | 电动给水泵B液力耦合器工作油进油温度 | Electrical feedwater pump Bcoupler work oil inlet temperature | 70LAB10CT128 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-007
703 | 70LAB10CP122 | 电动给水泵B液力耦合器滤清器出口油压 | Electrical feedwater pump Bcoupler percolator outlet oil pressure | 70LAB10CP122 | 4~20mA | AI | 0~0.6 | MPa | [8 empty] | SCS | D |  | K0204-007
704 | 70LAB10CP123 | 电动给水泵B液力耦合器直流润滑油泵出口压力 | Electrical feedwater pump Bcoupler DC lube oil pump outlet pressure | 70LAB10CP123 | 4~20mA | AI | 0~0.6 | MPa | [8 empty] | SCS | D |  | K0204-007
705 | 70LAB10CT129 | 电动给水泵B液力耦合器直流润滑油泵出口温度 | Electrical feedwater pump Bcoupler DC lube oil pump outlet temperature | 70LAB10CT129 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-007
706 | 70LAB10CS121 | 电动给水泵B液力耦合器输出转速 | Electrical feedwater pump Bcoupler outlet speed | 70LAB10CS121 | 4~20mA | AI | [10 empty] | MCS | U |  | K0204-007
707 | 70LAB10AP021YB01 | 电动给水泵B液力耦合器直流润滑油泵启动指令 | Electrical feedwater pump Bcoupler DC lube oil pump start command | 70LAB10AP021 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-007
708 | 70LAB10AP021YB11 | 电动给水泵B液力耦合器直流润滑油泵停止指令 | Electrical feedwater pump Bcoupler DC lube oil pump stop command | 70LAB10AP021 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-007
709 | 70LAB10AP021XB01 | 电动给水泵B液力耦合器直流润滑油泵运行 | Electrical feedwater pump Bcoupler DC lube oil pump running | 70LAB10AP021 | NO | DI | [10 empty] | SCS | D |  | K0204-007
710 | 70LAB10AP021XB11 | 电动给水泵B液力耦合器直流润滑油泵停止 | Electrical feedwater pump Bcoupler DC lube oil pump stopped | 70LAB10AP021 | NO | DI | [10 empty] | SCS | D |  | K0204-007
711 | 70LAB10AP021XB21 | 电动给水泵B液力耦合器直流润滑油泵远方控制允许 | Electrical feedwater pump Bcoupler DC lube oil pump remote control permitted | 70LAB10AP021 | NO | DI | [10 empty] | SCS | D |  | K0204-007
712 | 70LAB10AP021XB31 | 电动给水泵B液力耦合器直流润滑油泵故障 | Electrical feedwater pump Bcoupler DC lube oil pump fault | 70LAB10AP021 | NO | DI | [10 empty] | SCS | D |  | K0204-007
713 | 70LAB10AP022YB01 | 电动给水泵B液力耦合器交流润滑油泵启动指令 | Electrical feedwater pump Bcoupler AC lube oil pump start command | 70LAB10AP022 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-007
714 | 70LAB10AP022YB11 | 电动给水泵B液力耦合器交流润滑油泵停止指令 | Electrical feedwater pump Bcoupler AC lube oil pump stop command | 70LAB10AP022 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-007
715 | 70LAB10AP022XB01 | 电动给水泵B液力耦合器交流润滑油泵运行 | Electrical feedwater pump Bcoupler AC lube oil pump running | 70LAB10AP022 | NO | DI | [10 empty] | SCS | D |  | K0204-007
716 | 70LAB10AP022XB11 | 电动给水泵B液力耦合器交流润滑油泵停止 | Electrical feedwater pump Bcoupler AC lube oil pump stopped | 70LAB10AP022 | NO | DI | [10 empty] | SCS | D |  | K0204-007
717 | 70LAB10AP022XB21 | 电动给水泵B液力耦合器交流润滑油泵远方控制允许 | Electrical feedwater pump Bcoupler AC lube oil pump remote control permitted | 70LAB10AP022 | NO | DI | [10 empty] | SCS | D |  | K0204-007
718 | 70LAB10AP022XB31 | 电动给水泵B液力耦合器交流润滑油泵控制电源消失 | Electrical feedwater pump Bcoupler AC lube oil pump control circuit broken | 70LAB10AP022 | NO | DI | [10 empty] | SCS | D |  | K0204-007
719 | 70LAB10AP022XB32 | 电动给水泵B液力耦合器交流润滑油泵故障输出 | Electrical feedwater pump Bcoupler AC lube oil pump fault output | 70LAB10AP022 | NO | DI | [10 empty] | SCS | D |  | K0204-007
720 | 70LAB10AA121YQ01 | 电动给水泵B液力耦合器电动调节阀控制指令 | Electrical feedwater pump B coupler regulating MOV position command | 70LAB10AA121 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-007
721 | 70LAB10AA121XQ11 | 电动给水泵B液力耦合器电动调节阀位置反馈 | Electrical feedwater pump B coupler regulating MOV position feedback | 70LAB10AA121 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-007
722 | 70LCB10CT101 | 凝结水泵A推力轴承金属温度1 | Condensate pump A radial bearing metal temperature 1 | 70LCB10CT101 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-008
723 | 70LCB10CT102 | 凝结水泵A推力轴承金属温度2 | Condensate pump A radial bearing metal temperature 2 | 70LCB10CT102 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-008
724 | 70LCB10CT111 | 凝结水泵B推力轴承金属温度1 | Condensate pump B radial bearing metal temperature 1 | 70LCB10CT111 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-008
725 | 70LCB10CT112 | 凝结水泵B推力轴承金属温度2 | Condensate pump B radial bearing metal temperature 2 | 70LCB10CT112 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-008
726 | 70LCB10CT121 | 凝结水泵C推力轴承金属温度1 | Condensate pump C radial bearing metal temperature 1 | 70LCB10CT121 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-008
727 | 70LCB10CT122 | 凝结水泵C推力轴承金属温度2 | Condensate pump C radial bearing metal temperature 2 | 70LCB10CT122 | PT100 | RTD | 0~100 | ℃ | [8 empty] | SCS | D |  | K0204-008
728 | 70MAG10CL101 | 凝汽器热井水位 | Condenser hot well level | 70MAG10CL101 | 4~20mA | AI | 0~1.5 | m | [8 empty] | DAS | D |  | K0204-008
729 | 70MAG10CL102 | 凝汽器热井水位1 | Condenser hot well level 1 | 70MAG10CL102 | 4~20mA | AI | 0~1.5 | m | [8 empty] | MCS | D |  | K0204-008
730 | 70MAG10CL103 | 凝汽器热井水位2 | Condenser hot well level 2 | 70MAG10CL103 | 4~20mA | AI | 0~1.5 | m | [8 empty] | MCS | D |  | K0204-008
731 | 70MAG10CL104 | 凝汽器热井水位3 | Condenser hot well level 3 | 70MAG10CL104 | 4~20mA | AI | 0~1.5 | m | [8 empty] | MCS | D |  | K0204-008
732 | 70LCA10CT101 | 凝汽器出口水温 | Condenser outlet water temperature | 70LCA10CT101 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-008
733 | 70LCA10CP001H | 凝结水泵A入口滤网差压高 | Condensate pump A inlet filter DP H | 70LCA10CP001H | NO | DI | 100 | KPa | [8 empty] | SCS | D |  | K0204-008 | bar: H
734 | 70LCA10CP002H | 凝结水泵B入口滤网差压高 | Condensate pump B inlet filter DP H | 70LCA10CP002H | NO | DI | 100 | KPa | [8 empty] | SCS | D |  | K0204-008 | bar: H
735 | 70LCA10CP003H | 凝结水泵C入口滤网差压高 | Condensate pump C inlet filter DP H | 70LCA10CP003H | NO | DI | 100 | KPa | [8 empty] | SCS | D |  | K0204-008 | bar: H
736 | 70LCA30CP101 | 凝结水泵出口母管压力 | Condensate pump outlet main pipe pressure | 70LCA30CP101 | 4~20mA | AI | 0~2.5 | MPa | [8 empty] | DAS | D |  | K0204-008
737 | 70LCA30CT101 | 凝结水泵出口母管温度 | Condensate pump outlet main pipe temperature | 70LCA30CT101 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-008
738 | 70LCA30CT102 | 轴封冷却器出口水温 | Gland steam condenser outlet temperature | 70LCA30CT102 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-008
739 | 70LCA30CT103 | 6#低加出口水温 | 6# LP. Heater outlet temperature | 70LCA30CT103 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-008
740 | 70LCA30CT104 | 5#低加出口水温 | 5# LP. Heater outlet temperature | 70LCA30CT104 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-008
741 | 70LCA30CT105 | 4#低加出口水温 | 4# LP. Heater outlet temperature | 70LCA30CT105 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-008
742 | 70LCA30CF101 | 除氧器进水流量1 | Deaerator inlet water flow 1 | 70LCA30CF101 | 4~20mA | AI | 57~207 | t/h | [8 empty] | MCS | D |  | K0204-008
743 | 70LCA30CF102 | 除氧器进水流量2 | Deaerator inlet water flow 2 | 70LCA30CF102 | 4~20mA | AI | 57~207 | t/h | [8 empty] | MCS | D |  | K0204-008
744 | 70LAA10CT101 | 除氧器水箱温度 | Deaerator water tank temperature | 70LAA10CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-008
745 | 70LAA10CL104 | 除氧器水箱液位 | Deaerator water tank level | 70LAA10CL104 | 4~20mA | AI | 0~2.8 | m | [8 empty] | MCS | D |  | K0204-008
746 | 70LAA10CL101 | 除氧器水箱液位1 | Deaerator water tank level 1 | 70LAA10CL101 | 4~20mA | AI | 0~2.8 | m | [8 empty] | MCS | D |  | K0204-008
747 | 70LAA10CL102 | 除氧器水箱液位2 | Deaerator water tank level 2 | 70LAA10CL102 | 4~20mA | AI | 0~2.8 | m | [8 empty] | MCS | D |  | K0204-008
748 | 70LAA10CL103 | 除氧器水箱液位3 | Deaerator water tank level 3 | 70LAA10CL103 | 4~20mA | AI | 0~2.8 | m | [8 empty] | MCS | D |  | K0204-008
749 | 70LCA20AA001YB01 | 凝结水泵A出口电动阀打开指令 | Condensate pump A outlet MOV open command | 70LCA20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
750 | 70LCA20AA001YB11 | 凝结水泵A出口电动阀关闭指令 | Condensate pump A outlet MOV close command | 70LCA20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
751 | 70LCA20AA001XB01 | 凝结水泵A出口电动阀全开状态 | Condensate pump A outlet MOV full opened status | 70LCA20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
752 | 70LCA20AA001XB11 | 凝结水泵A出口电动阀全关状态 | Condensate pump A outlet MOV full closed status | 70LCA20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
753 | 70LCA20AA001XB31 | 凝结水泵A出口电动阀故障 | Condensate pump A outlet MOV fault | 70LCA20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
754 | 70LCA20AA002YB01 | 凝结水泵B出口电动阀打开指令 | Condensate pump B outlet MOV open command | 70LCA20AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
755 | 70LCA20AA002YB11 | 凝结水泵B出口电动阀关闭指令 | Condensate pump B outlet MOV close command | 70LCA20AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
756 | 70LCA20AA002XB01 | 凝结水泵B出口电动阀全开状态 | Condensate pump B outlet MOV full opened status | 70LCA20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
757 | 70LCA20AA002XB11 | 凝结水泵B出口电动阀全关状态 | Condensate pump B outlet MOV full closed status | 70LCA20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
758 | 70LCA20AA002XB31 | 凝结水泵B出口电动阀故障 | Condensate pump B outlet MOV fault | 70LCA20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
759 | 70LCA20AA003YB01 | 凝结水泵C出口电动阀打开指令 | Condensate pump C outlet MOV open command | 70LCA20AA003 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
760 | 70LCA20AA003YB11 | 凝结水泵C出口电动阀关闭指令 | Condensate pump C outlet MOV close command | 70LCA20AA003 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
761 | 70LCA20AA003XB01 | 凝结水泵C出口电动阀全开状态 | Condensate pump C outlet MOV full opened status | 70LCA20AA003 | NO | DI | [10 empty] | SCS | D |  | K0204-008
762 | 70LCA20AA003XB11 | 凝结水泵C出口电动阀全关状态 | Condensate pump C outlet MOV full closed status | 70LCA20AA003 | NO | DI | [10 empty] | SCS | D |  | K0204-008
763 | 70LCA20AA003XB31 | 凝结水泵C出口电动阀故障 | Condensate pump C outlet MOV fault | 70LCA20AA003 | NO | DI | [10 empty] | SCS | D |  | K0204-008
764 | 70LCA40AA101YQ01 | 凝结水再循电动调节阀控制指令 | Condensate water recirculation regulating MOV position command | 70LCA40AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-008
765 | 70LCA40AA101XQ11 | 凝结水再循电动调节阀阀位反馈 | Condensate water recirculation regulating MOV position feedback | 70LCA40AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-008
766 | 70LCA30AA101YQ01 | 除氧器入口电动调节阀控制指令 | Deaerator inlet regulating MOV position command | 70LCA30AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-008
767 | 70LCA30AA101XQ11 | 除氧器入口电动调节阀位置反馈 | Deaerator inlet regulating MOV position feedback | 70LCA30AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-008
768 | 70LAA20AA001YB01 | 除氧器溢流电动阀打开指令 | Deaerator overflow MOV open command | 70LAA20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
769 | 70LAA20AA001YB11 | 除氧器溢流电动阀关闭指令 | Deaerator overflow MOV close command | 70LAA20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
770 | 70LAA20AA001XB01 | 除氧器溢流电动阀全开状态 | Deaerator overflow MOV full opened status | 70LAA20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
771 | 70LAA20AA001XB11 | 除氧器溢流电动阀全关状态 | Deaerator overflow MOV full closed status | 70LAA20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
772 | 70LAA20AA001XB31 | 除氧器溢流电动阀故障 | Deaerator overflow MOV fault | 70LAA20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
773 | 70LAA20AA002YB01 | 除氧器放水电动阀打开指令 | Deaerator discharge MOV open command | 70LAA20AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
774 | 70LAA20AA002YB11 | 除氧器放水电动阀关闭指令 | Deaerator discharge MOV close command | 70LAA20AA002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
775 | 70LAA20AA002XB01 | 除氧器放水电动阀全开状态 | Deaerator discharge MOV full opened status | 70LAA20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
776 | 70LAA20AA002XB11 | 除氧器放水电动阀全关状态 | Deaerator discharge MOV full closed status | 70LAA20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
777 | 70LAA20AA002XB31 | 除氧器放水电动阀故障 | Deaerator discharge MOV fault | 70LAA20AA002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
778 | 70LCB10AP001YB01 | 凝结水泵A启动指令 | Condensate pump A start command | 70LCB10AP001 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-008
779 | 70LCB10AP001YB11 | 凝结水泵A停止指令 | Condensate pump A stop command | 70LCB10AP001 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-008
780 | 70LCB10AP001XB01 | 凝结水泵A运行 | Condensate pump A running | 70LCB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
781 | 70LCB10AP001XB11 | 凝结水泵A停止 | Condensate pump A stopped | 70LCB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
782 | 70LCB10AP001XB12 | 凝结水泵A停止(SOE) | Condensate pump A stopped (SOE) | 70LCB10AP001 | NC | SOE | [10 empty] | SOE | D |  | K0204-008
783 | 70LCB10AP001XB21 | 凝结水泵A远方控制允许 | Condensate pump A remote control permitted | 70LCB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
784 | 70LCB10AP001XB31 | 凝结水泵A装置故障控制电源消失 | Condensate pump A device fault control power loss | 70LCB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
785 | 70LCB10AP001XB32 | 凝结水泵A保护动作 | Condensate pump A protection movement | 70LCB10AP001 | NO | DI | [10 empty] | SCS | D |  | K0204-008
786 | 70LCB10AP001XQ01 | 凝结水泵A电流 | Condensate pump A current | 70LCB10AP001 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0204-008
787 | 70LCB10AP002YB01 | 凝结水泵B启动指令 | Condensate pump B start command | 70LCB10AP002 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-008
788 | 70LCB10AP002YB11 | 凝结水泵B停止指令 | Condensate pump B stop command | 70LCB10AP002 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-008
789 | 70LCB10AP002XB01 | 凝结水泵B运行 | Condensate pump B running | 70LCB10AP002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
790 | 70LCB10AP002XB11 | 凝结水泵B停止 | Condensate pump B stopped | 70LCB10AP002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
791 | 70LCB10AP002XB12 | 凝结水泵B停止(SOE) | Condensate pump B stopped (SOE) | 70LCB10AP002 | NC | SOE | [10 empty] | SOE | D |  | K0204-008
792 | 70LCB10AP002XB21 | 凝结水泵B远方控制允许 | Condensate pump B remote control permitted | 70LCB10AP002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
793 | 70LCB10AP002XB31 | 凝结水泵B装置故障控制电源消失 | Condensate pump B device fault control power loss | 70LCB10AP002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
794 | 70LCB10AP002XB32 | 凝结水泵B保护动作 | Condensate pump B protection movement | 70LCB10AP002 | NO | DI | [10 empty] | SCS | D |  | K0204-008
795 | 70LCB10AP002XQ01 | 凝结水泵B电流 | Condensate pump B current | 70LCB10AP002 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0204-008
796 | 70LCB10AP003YB01 | 凝结水泵C启动指令 | Condensate pump C start command | 70LCB10AP003 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-008
797 | 70LCB10AP003YB11 | 凝结水泵C停止指令 | Condensate pump C stop command | 70LCB10AP003 | NO | DO | [10 empty] | SCS | U | 220VDC | K0204-008
798 | 70LCB10AP003XB01 | 凝结水泵C运行 | Condensate pump C running | 70LCB10AP003 | NO | DI | [10 empty] | SCS | D |  | K0204-008
799 | 70LCB10AP003XB11 | 凝结水泵C停止 | Condensate pump C stopped | 70LCB10AP003 | NO | DI | [10 empty] | SCS | D |  | K0204-008
800 | 70LCB10AP003XB12 | 凝结水泵C停止(SOE) | Condensate pump C stopped (SOE) | 70LCB10AP003 | NC | SOE | [10 empty] | SOE | D |  | K0204-008
801 | 70LCB10AP003XB21 | 凝结水泵C远方控制允许 | Condensate pump C remote control permitted | 70LCB10AP003 | NO | DI | [10 empty] | SCS | D |  | K0204-008
802 | 70LCB10AP003XB31 | 凝结水泵C装置故障控制电源消失 | Condensate pump C device fault control power loss | 70LCB10AP003 | NO | DI | [10 empty] | SCS | D |  | K0204-008
803 | 70LCB10AP003XB32 | 凝结水泵C保护动作 | Condensate pump C protection movement | 70LCB10AP003 | NO | DI | [10 empty] | SCS | D |  | K0204-008
804 | 70LCB10AP003XQ01 | 凝结水泵C电流 | Condensate pump C current | 70LCB10AP003 | 4～20mA | AI |  | A | [8 empty] | DAS | U |  | K0204-008
805 | 70LCA30AA402YB01 | 凝结水有压放水电动阀打开指令 | Condensate water pressure drain MOV open command | 70LCA30AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
806 | 70LCA30AA402YB11 | 凝结水有压放水电动阀关闭指令 | Condensate water pressure drain MOV close command | 70LCA30AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-008
807 | 70LCA30AA402XB01 | 凝结水有压放水电动阀全开状态 | Condensate water pressure drain MOV full opened status | 70LCA30AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-008
808 | 70LCA30AA402XB11 | 凝结水有压放水电动阀全关状态 | Condensate water pressure drain MOV full closed status | 70LCA30AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-008
809 | 70LCA30AA402XB31 | 凝结水有压放水电动阀故障 | Condensate water pressure drain MOV fault | 70LCA30AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-008
810 | 70MAC01AA051YQ01 | 排汽缸减温水气动调节阀控制指令 | Exhaust hood attemperating water regulating PV position command | 70MAC01AA051 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-009
811 | 70MAC01AA051XQ11 | 排汽缸减温水气动调节阀位置反馈 | Exhaust hood attemperating water regulating PV position feedback | 70MAC01AA051 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-009
812 | 70LCA33AA101YQ01 | 本体疏水集管B1减温水气动调节阀控制指令 | Body drain header nozzle B1 attemperating water regulating PV position command | 70LCA33AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-009
813 | 70LCA33AA101XQ11 | 本体疏水集管B1减温水气动调节阀位置反馈 | Body drain header nozzle B1 attemperating water regulating PV position feedback | 70LCA33AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-009
814 | 70LBG10AA402YB01 | 辅助蒸汽母管疏水阀打开/关闭指令 | Auxiliary steam main pipe drain valve open/close command | 70LBG10AA402 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-010
815 | 70LBG10AA402XB01 | 辅助蒸汽母管疏水阀全开状态 | Auxiliary steam main pipe drain valve full opened status | 70LBG10AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-010
816 | 70LBG10AA402XB11 | 辅助蒸汽母管疏水阀全关状态 | Auxiliary steam main pipe drain valve full closed status | 70LBG10AA402 | NO | DI | [10 empty] | SCS | D |  | K0204-010
817 | 70LBG10AA001YB01 | 辅助蒸汽母管电动阀打开指令 | Auxiliary steam main pipe MOV open command | 70LBG10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-010
818 | 70LBG10AA001YB11 | 辅助蒸汽母管电动阀关闭指令 | Auxiliary steam main pipe MOV close command | 70LBG10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-010
819 | 70LBG10AA001XB01 | 辅助蒸汽母管电动阀全开状态 | Auxiliary steam main pipe MOV full opened status | 70LBG10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-010
820 | 70LBG10AA001XB11 | 辅助蒸汽母管电动阀全关状态 | Auxiliary steam main pipe MOV full closed status | 70LBG10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-010
821 | 70LBG10AA001XB31 | 辅助蒸汽母管电动阀故障 | Auxiliary steam main pipe MOV fault | 70LBG10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-010
822 | 70LAD10CL101 | 1#高加水位1 | 1# HP heater level 1 | 70LAD10CL101 | 4~20mA | AI | 0~1.5 | m | [8 empty] | MCS | D |  | K0204-011
823 | 70LAD10CL102 | 1#高加水位2 | 1# HP heater level 2 | 70LAD10CL102 | 4~20mA | AI | 0~1.5 | m | [8 empty] | MCS | D |  | K0204-011
824 | 70LAD10CL103 | 1#高加水位3 | 1# HP heater level 3 | 70LAD10CL103 | 4~20mA | AI | 0~1.5 | m | [8 empty] | MCS | D |  | K0204-011
825 | 70LAD10CT101 | 1#高加正常疏水温度 | 1# HP heater drain water temperature | 70LAD10CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-011
826 | 70LAD10CT102 | 1#高加危急疏水温度 | 1# HP heater emergency drain water temperature | 70LAD10CT102 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-011
827 | 70LAD10AA101YQ01 | 1#高加正常疏水气动调节阀控制指令 | 1# HP heater drain water regulating PV position command | 70LAD10AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-011
828 | 70LAD10AA101XQ11 | 1#高加正常疏水气动调节阀位置反馈 | 1# HP heater drain water regulating PV position feedback | 70LAD10AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-011
829 | 70LAD10AA005YB01 | 1#高加危急疏水电动阀打开指令 | 1# HP heater emergency drain water MOV open command | 70LAD10AA005 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-011
830 | 70LAD10AA005YB11 | 1#高加危急疏水电动阀关闭指令 | 1# HP heater emergency drain water MOV close command | 70LAD10AA005 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-011
831 | 70LAD10AA005XB01 | 1#高加危急疏水电动阀全开状态 | 1# HP heater emergency drain water MOV full opened status | 70LAD10AA005 | NO | DI | [10 empty] | SCS | D |  | K0204-011
832 | 70LAD10AA005XB11 | 1#高加危急疏水电动阀全关状态 | 1# HP heater emergency drain water MOV full closed status | 70LAD10AA005 | NO | DI | [10 empty] | SCS | D |  | K0204-011
833 | 70LAD10AA005XB31 | 1#高加危急疏水电动阀故障 | 1# HP heater emergency drain water MOV fault | 70LAD10AA005 | NO | DI | [10 empty] | SCS | D |  | K0204-011
834 | 70LAD20CL101 | 2#高加水位1 | 2# HP heater level 1 | 70LAD20CL101 | 4~20mA | AI | 0~1.5 | m | [8 empty] | MCS | D |  | K0204-011
835 | 70LAD20CL102 | 2#高加水位2 | 2# HP heater level 2 | 70LAD20CL102 | 4~20mA | AI | 0~1.5 | m | [8 empty] | MCS | D |  | K0204-011
836 | 70LAD20CL103 | 2#高加水位3 | 2# HP heater level 3 | 70LAD20CL103 | 4~20mA | AI | 0~1.5 | m | [8 empty] | MCS | D |  | K0204-011
837 | 70LAD20CT101 | 2#高加正常疏水温度 | 2# HP heater drain water temperature | 70LAD20CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-011
838 | 70LAD20CT102 | 2#高加危急疏水温度 | 2# HP heater emergency drain water temperature | 70LAD20CT102 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-011
839 | 70LAD20AA101YQ01 | 2#高加正常疏水气动调节阀控制指令 | 2# HP heater drain water regulating PV position command | 70LAD20AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-011
840 | 70LAD20AA101XQ11 | 2#高加正常疏水气动调节阀位置反馈 | 2# HP heater drain water regulating PV position feedback | 70LAD20AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-011
841 | 70LAD20AA005YB01 | 2#高加危急疏水电动阀打开指令 | 2# HP heater emergency drain water MOV open command | 70LAD20AA005 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-011
842 | 70LAD20AA005YB11 | 2#高加危急疏水电动阀关闭指令 | 2# HP heater emergency drain water MOV close command | 70LAD20AA005 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-011
843 | 70LAD20AA005XB01 | 2#高加危急疏水电动阀全开状态 | 2# HP heater emergency drain water MOV full opened status | 70LAD20AA005 | NO | DI | [10 empty] | SCS | D |  | K0204-011
844 | 70LAD20AA005XB11 | 2#高加危急疏水电动阀全关状态 | 2# HP heater emergency drain water MOV full closed status | 70LAD20AA005 | NO | DI | [10 empty] | SCS | D |  | K0204-011
845 | 70LAD20AA005XB31 | 2#高加危急疏水电动阀故障 | 2# HP heater emergency drain water MOV fault | 70LAD20AA005 | NO | DI | [10 empty] | SCS | D |  | K0204-011
846 | 70LCC30CL001H | 4#低加水位高 | 4# LP heater level H | 70LCC30CL001 | NO | DI | [10 empty] | SCS | D |  | K0204-012
847 | 70LCC30CL002HH | 4#低加水位高高 | 4# LP heater level HH | 70LCC30CL002 | NO | DI | [10 empty] | SCS | D |  | K0204-012
848 | 70LCC30CL101 | 4#低加水位1 | 4# LP heater level 1 | 70LCC30CL101 | 4~20mA | AI | 0~1.0 | m | [8 empty] | MCS | D |  | K0204-012
849 | 70LCC30CL102 | 4#低加水位2 | 4# LP heater level 2 | 70LCC30CL102 | 4~20mA | AI | 0~1.0 | m | [8 empty] | MCS | D |  | K0204-012
850 | 70LCC30CL103 | 4#低加水位3 | 4# LP heater level 3 | 70LCC30CL103 | 4~20mA | AI | 0~1.0 | m | [8 empty] | MCS | D |  | K0204-012
851 | 70LCC30CT101 | 4#低加正常疏水温度 | 4# LP heater drain water temperature | 70LCC30CT101 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-012
852 | 70LCC30CT102 | 4#低加危急疏水温度 | 4# LP heater emergency drain water temperature | 70LCC30CT102 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-012
853 | 70LCC30AA101YQ01 | 4#低加正常疏水气动调节阀控制指令 | 4# LP heater drain water regulating PV position command | 70LCC30AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-012
854 | 70LCC30AA101XQ11 | 4#低加正常疏水气动调节阀位置反馈 | 4# LP heater drain water regulating PV position feedback | 70LCC30AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-012
855 | 70LCC30AA102YQ01 | 4#低加危急疏水气动调节阀控制指令 | 4# LP heater emergency drain water regulating PV position command | 70LCC30AA102 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-012
856 | 70LCC30AA102XQ11 | 4#低加危急疏水气动调节阀位置反馈 | 4# LP heater emergency drain water regulating PV position feedback | 70LCC30AA102 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-012
857 | 70LCC20CL001H | 5#低加水位高 | 5# LP heater level H | 70LCC20CL001 | NO | DI | [10 empty] | SCS | D |  | K0204-012
858 | 70LCC20CL002HH | 5#低加水位高高 | 5# LP heater level HH | 70LCC20CL002 | NO | DI | [10 empty] | SCS | D |  | K0204-012
859 | 70LCC20CL101 | 5#低加水位1 | 5# LP heater level 1 | 70LCC20CL101 | 4~20mA | AI | 0~1.0 | m | [8 empty] | MCS | D |  | K0204-012
860 | 70LCC20CL102 | 5#低加水位2 | 5# LP heater level 2 | 70LCC20CL102 | 4~20mA | AI | 0~1.0 | m | [8 empty] | MCS | D |  | K0204-012
861 | 70LCC20CL103 | 5#低加水位3 | 5# LP heater level 3 | 70LCC20CL103 | 4~20mA | AI | 0~1.0 | m | [8 empty] | MCS | D |  | K0204-012
862 | 70LCC20CT101 | 5#低加正常疏水温度 | 5# LP heater drain water temperature | 70LCC20CT101 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-012
863 | 70LCC20CT102 | 5#低加危急疏水温度 | 5# LP heater emergency drain water temperature | 70LCC20CT102 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-012
864 | 70LCC20AA101YQ01 | 5#低加正常疏水气动调节阀控制指令 | 5# LP heater drain water regulating PV position command | 70LCC20AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-012
865 | 70LCC20AA101XQ11 | 5#低加正常疏水气动调节阀位置反馈 | 5# LP heater drain water regulating PV position feedback | 70LCC20AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-012
866 | 70LCC20AA102YQ01 | 5#低加危急疏水气动调节阀控制指令 | 5# LP heater emergency drain water regulating PV position command | 70LCC20AA102 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-012
867 | 70LCC20AA102XQ11 | 5#低加危急疏水气动调节阀位置反馈 | 5# LP heater emergency drain water regulating PV position feedback | 70LCC20AA102 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-012
868 | 70LCC10CL001H | 6#低加水位高 | 6# LP heater level H | 70LCC10CL001 | NO | DI | [10 empty] | SCS | D |  | K0204-012
869 | 70LCC10CL002HH | 6#低加水位高高 | 6# LP heater level HH | 70LCC10CL002 | NO | DI | [10 empty] | SCS | D |  | K0204-012
870 | 70LCC10CL101 | 6#低加水位1 | 6# LP heater level 1 | 70LCC10CL101 | 4~20mA | AI | 0~1.0 | m | [8 empty] | MCS | D |  | K0204-012
871 | 70LCC10CL102 | 6#低加水位2 | 6# LP heater level 2 | 70LCC10CL102 | 4~20mA | AI | 0~1.0 | m | [8 empty] | MCS | D |  | K0204-012
872 | 70LCC10CL103 | 6#低加水位3 | 6# LP heater level 3 | 70LCC10CL103 | 4~20mA | AI | 0~1.0 | m | [8 empty] | MCS | D |  | K0204-012
873 | 70LCC10CT101 | 6#低加正常疏水温度 | 6# LP heater drain water temperature | 70LCC10CT101 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-012
874 | 70LCC10CT102 | 6#低加危急疏水温度 | 6# LP heater emergency drain water temperature | 70LCC10CT102 | 4~20mA | AI | 0~200 | ℃ | [8 empty] | DAS | D |  | K0204-012
875 | 70LCC10AA101YQ01 | 6#低加正常疏水气动调节阀控制指令 | 6# LP heater drain water regulating PV position command | 70LCC10AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-012
876 | 70LCC10AA101XQ11 | 6#低加正常疏水气动调节阀位置反馈 | 6# LP heater drain water regulating PV position feedback | 70LCC10AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-012
877 | 70LCC10AA102YQ01 | 6#低加危急疏水气动调节阀控制指令 | 6# LP heater emergency drain water regulating PV position command | 70LCC10AA102 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-012
878 | 70LCC10AA102XQ11 | 6#低加危急疏水气动调节阀位置反馈 | 6# LP heater emergency drain water regulating PV position feedback | 70LCC10AA102 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-012
879 | 70MAW10CL101 | 轴封冷却器液位 | Gland steam condenser level | 70MAW10CL101 | 4~20mA | AI |  | m | [8 empty] | SCS | D |  | K0204-012
880 | 70MAW10CL001H | 轴封冷却器液位高 | Gland steam condenser level H | 70MAW10CL001 | NO | DI | [10 empty] | SCS | D |  | K0204-012
881 | 70PAB20CT101 | A侧凝汽器循环水进水温度 | Inlet water temperature of condenser by side A | 70PAB20CT101 | 4~20mA | AI | 0~100 | ℃ | [8 empty] | DAS | D |  | K0204-014
882 | 70PAB20CP101 | A侧凝汽器循环水进水压力 | Inlet water pressure of condenser by side A | 70PAB20CP101 | 4~20mA | AI | 0~0.25 | MPa | [8 empty] | DAS | D |  | K0204-014
883 | 70PAB40CP101 | A侧凝汽器循环水出水压力 | Outlet water pressure of condenser by side A | 70PAB40CP101 | 4~20mA | AI | 0~0.25 | MPa | [8 empty] | DAS | D |  | K0204-014
884 | 70PAB40CT101 | A侧凝汽器循环水出水温度 | Outlet water pressure of condenser by side A | 70PAB40CT101 | 4~20mA | AI | 0~100 | ℃ | [8 empty] | DAS | D |  | K0204-014
885 | 70PAB20AA001YB01 | A侧凝汽器循环水进水电动阀打开指令 | Inlet water MOV of condenser by side A open command | 70PAB20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-014
886 | 70PAB20AA001YB11 | A侧凝汽器循环水进水电动阀关闭指令 | Inlet water MOV of condenser by side A close command | 70PAB20AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-014
887 | 70PAB20AA001XB01 | A侧凝汽器循环水进水电动阀全开状态 | Inlet water MOV of condenser by side A full opened status | 70PAB20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
888 | 70PAB20AA001XB11 | A侧凝汽器循环水进水电动阀全关状态 | Inlet water MOV of condenser by side A full closed status | 70PAB20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
889 | 70PAB20AA001XB31 | A侧凝汽器循环水进水电动阀故障 | Inlet water MOV of condenser by side A fault | 70PAB20AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
890 | 70PAB40AA001YB01 | A侧凝汽器循环水出水电动阀打开指令 | Outlet water MOV of condenser by side A open command | 70PAB40AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-014
891 | 70PAB40AA001YB11 | A侧凝汽器循环水出水电动阀关闭指令 | Outlet water MOV of condenser by side A close command | 70PAB40AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-014
892 | 70PAB40AA001XB01 | A侧凝汽器循环水出水电动阀全开状态 | Outlet water MOV of condenser by side A full opened status | 70PAB40AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
893 | 70PAB40AA001XB11 | A侧凝汽器循环水出水电动阀全关状态 | Outlet water MOV of condenser by side A full closed status | 70PAB40AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
894 | 70PAB40AA001XB31 | A侧凝汽器循环水出水电动阀故障 | Outlet water MOV of condenser by side A fault | 70PAB40AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
895 | 70PAB10CT101 | B侧凝汽器循环水进水温度 | Inlet water temperature of condenser by side B | 70PAB10CT101 | 4~20mA | AI | 0~100 | ℃ | [8 empty] | DAS | D |  | K0204-014
896 | 70PAB10CP101 | B侧凝汽器循环水进水压力 | Inlet water pressure of condenser by side B | 70PAB10CP101 | 4~20mA | AI | 0~0.25 | MPa | [8 empty] | DAS | D |  | K0204-014
897 | 70PAB30CP101 | B侧凝汽器循环水出水压力 | Outlet water pressure of condenser by side B | 70PAB30CP101 | 4~20mA | AI | 0~0.25 | MPa | [8 empty] | DAS | D |  | K0204-014
898 | 70PAB30CT101 | B侧凝汽器循环水出水温度 | Outlet water pressure of condenser by side B | 70PAB30CT101 | 4~20mA | AI | 0~100 | ℃ | [8 empty] | DAS | D |  | K0204-014
899 | 70PAB10AA001YB01 | B侧凝汽器循环水进水电动阀打开指令 | Inlet water MOV of condenser by side B open command | 70PAB10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-014
900 | 70PAB10AA001YB11 | B侧凝汽器循环水进水电动阀关闭指令 | Inlet water MOV of condenser by side B close command | 70PAB10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-014
901 | 70PAB10AA001XB01 | B侧凝汽器循环水进水电动阀全开状态 | Inlet water MOV of condenser by side B full opened status | 70PAB10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
902 | 70PAB10AA001XB11 | B侧凝汽器循环水进水电动阀全关状态 | Inlet water MOV of condenser by side B full closed status | 70PAB10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
903 | 70PAB10AA001XB31 | B侧凝汽器循环水进水电动阀故障 | Inlet water MOV of condenser by side B fault | 70PAB10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
904 | 70PAB30AA001YB01 | B侧凝汽器循环水出水电动阀打开指令 | Outlet water MOV of condenser by side B open command | 70PAB30AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-014
905 | 70PAB30AA001YB11 | B侧凝汽器循环水出水电动阀关闭指令 | Outlet water MOV of condenser by side B close command | 70PAB30AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-014
906 | 70PAB30AA001XB01 | B侧凝汽器循环水出水电动阀全开状态 | Outlet water MOV of condenser by side B full opened status | 70PAB30AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
907 | 70PAB30AA001XB11 | B侧凝汽器循环水出水电动阀全关状态 | Outlet water MOV of condenser by side B full closed status | 70PAB30AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
908 | 70PAB30AA001XB31 | B侧凝汽器循环水出水电动阀故障 | Outlet water MOV of condenser by side B fault | 70PAB30AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-014
909 | 70GHC50CF101 | 凝汽器补水流量 | Condensate make-up water flow | 70GHC50CF101 | 4~20mA | AI | 0~12 | t/h | [8 empty] | MCS | D |  | K0204-015
910 | 70GHC50AA101YQ01 | 凝汽器补水电动调节阀控制指令 | Condensate make-up water regulating MOV position command | 70GHC50AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-015
911 | 70GHC50AA101XQ11 | 凝汽器补水电动调节阀位置反馈 | Condensate make-up water regulating MOV position feedback | 70GHC50AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-015
912 | 70GHC10CP101 | 除盐水母管压力 | Demineralized water pressure | 70GHC10CP101 | 4~20mA | AI | 0~2.2 | MPa | [8 empty] | DAS | D |  | K0204-015
913 | 70GHC20CT101 | 冷渣机入口冷却水温度 | Slag cooler inlet cooling water temperature | 70GHC20CT101 | 4~20mA | AI | 0~100 | ℃ | [8 empty] | DAS | D |  | K0204-015
914 | 70GHC30CT101 | 冷渣机出口冷却水温度 | Slag cooler outlet cooling water temperature | 70GHC30CT101 | 4~20mA | AI | 0~100 | ℃ | [8 empty] | DAS | D |  | K0204-015
915 | 70GHC30CF101 | 冷渣机出口冷却水回水流量 | Slag cooler outlet cooling water returning flow | 70GHC30CF101 | 4~20mA | AI | 0~150 | t/h | [8 empty] | DAS | D |  | K0204-015
916 | 70GHC10CF101 | 除氧器补水流量 | Deaerator make-up water flow | 70GHC10CF101 | 4~20mA | AI | 0~200 | t/h | [8 empty] | MCS | D |  | K0204-015
917 | 70GHC10AA101YQ01 | 除氧器补水电动调节阀控制指令 | Deaerator make-up water regulating MOV position command | 70GHC10AA101 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-015
918 | 70GHC10AA101XQ11 | 除氧器补水电动调节阀位置反馈 | Deaerator make-up water regulating MOV position feedback | 70GHC10AA101 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-015
919 | 70MAW10CP101 | 汽封母管供汽压力1 | Gland seal main steam pressure 1 | 70MAW10CP101 | 4~20mA | AI | -10~90 | mbar | [8 empty] | MCS | D |  | K0204-016
920 | 70MAW10CP102 | 汽封母管供汽压力2 | Gland seal main steam pressure 2 | 70MAW10CP102 | 4~20mA | AI | -10~90 | mbar | [8 empty] | MCS | D |  | K0204-016
921 | 70MAW10CT101 | 汽封供汽支管温度1 | Gland seal by-Pass steam temperature 1 | 70MAW10CT101 | PT100 | RTD | 0~400 | ℃ | [8 empty] | MCS | D |  | K0204-016
922 | 70MAW10CT102 | 汽封供汽支管温度2 | Gland seal by-Pass steam temperature 2 | 70MAW10CT102 | PT100 | RTD | 0~400 | ℃ | [8 empty] | MCS | D |  | K0204-016
923 | 70MAW10AA001YB01 | 汽封母管供汽电动阀打开指令 | Gland seal main steam MOV open command | 70MAW10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-016
924 | 70MAW10AA001YB11 | 汽封母管供汽电动阀关闭指令 | Gland seal main steam MOV close command | 70MAW10AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-016
925 | 70MAW10AA001XB01 | 汽封母管供汽电动阀全开状态 | Gland seal main steam MOV full opened status | 70MAW10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-016
926 | 70MAW10AA001XB11 | 汽封母管供汽电动阀全关状态 | Gland seal main steam MOV full closed status | 70MAW10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-016
927 | 70MAW10AA001XB31 | 汽封母管供汽电动阀故障 | Gland seal main steam MOV fault | 70MAW10AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-016
928 | 70MAW10AA051YQ01 | 汽封母管供汽气动调节阀控制指令 | Gland seal main steam regulating PV position command | 70MAW10AA051 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-016
929 | 70MAW10AA051XQ11 | 汽封母管供汽气动调节阀位置反馈 | Gland seal main steam regulating PV position feedback | 70MAW10AA051 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-016
930 | 70MAW50AA051YQ01 | 汽封母管供汽溢流气动调节阀控制指令 | Gland seal main steam overflow regulating PV position command | 70MAW50AA051 | 4~20mA | AO | 0~100 | % | [8 empty] | MCS | D |  | K0204-016
931 | 70MAW50AA051XQ11 | 汽封母管供汽溢流气动调节阀位置反馈 | Gland seal main steam overflow regulating PV position feedback | 70MAW50AA051 | 4~20mA | AI | 0~100 | % | [8 empty] | MCS | U |  | K0204-016
932 | 70MAW10AN001YB01 | 1#汽封冷却器风机启动指令 | 1# gland seal fan start command | 70MAW10AN001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-016
933 | 70MAW10AN001YB11 | 1#汽封冷却器风机停止指令 | 1# gland seal fan stop command | 70MAW10AN001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-016
934 | 70MAW10AN001XB01 | 1#汽封冷却器风机运行 | 1# gland seal fan running | 70MAW10AN001 | NO | DI | [10 empty] | SCS | D |  | K0204-016
935 | 70MAW10AN001XB11 | 1#汽封冷却器风机停止 | 1# gland seal fan stopped | 70MAW10AN001 | NO | DI | [10 empty] | SCS | D |  | K0204-016
936 | 70MAW10AN001XB21 | 1#汽封冷却器风机远方控制允许 | 1# gland seal fan remote control permitted | 70MAW10AN001 | NO | DI | [10 empty] | SCS | D |  | K0204-016
937 | 70MAW10AN001XB31 | 1#汽封冷却器风机控制电源消失 | 1# gland seal fan control circuit broken | 70MAW10AN001 | NO | DI | [10 empty] | SCS | D |  | K0204-016
938 | 70MAW10AN001XB32 | 1#汽封冷却器风机故障输出 | 1# gland seal fan fault output | 70MAW10AN001 | NO | DI | [10 empty] | SCS | D |  | K0204-016
939 | 70MAW10AN002YB01 | 2#汽封冷却器风机启动指令 | 2# gland seal fan start command | 70MAW10AN002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-016
940 | 70MAW10AN002YB11 | 2#汽封冷却器风机停止指令 | 2# gland seal fan stop command | 70MAW10AN002 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-016
941 | 70MAW10AN002XB01 | 2#汽封冷却器风机运行 | 2# gland seal fan running | 70MAW10AN002 | NO | DI | [10 empty] | SCS | D |  | K0204-016
942 | 70MAW10AN002XB11 | 2#汽封冷却器风机停止 | 2# gland seal fan stopped | 70MAW10AN002 | NO | DI | [10 empty] | SCS | D |  | K0204-016
943 | 70MAW10AN002XB21 | 2#汽封冷却器风机远方控制允许 | 2# gland seal fan remote control permitted | 70MAW10AN002 | NO | DI | [10 empty] | SCS | D |  | K0204-016
944 | 70MAW10AN002XB31 | 2#汽封冷却器风机控制电源消失 | 2# gland seal fan control circuit broken | 70MAW10AN002 | NO | DI | [10 empty] | SCS | D |  | K0204-016
945 | 70MAW10AN002XB32 | 2#汽封冷却器风机故障输出 | 2# gland seal fan fault output | 70MAW10AN002 | NO | DI | [10 empty] | SCS | D |  | K0204-016
946 | 70MAW40AA001YB01 | 汽封母管疏水阀打开/关闭指令 | Gland seal main drain valve open/close command | 70MAW40AA001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-016
947 | 70MAW40AA001XB01 | 汽封母管疏水阀全开状态 | Gland seal main drain valve full opened status | 70MAW40AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-016
948 | 70MAW40AA001XB11 | 汽封母管疏水阀全关状态 | Gland seal main drain valve full closed status | 70MAW40AA001 | NO | DI | [10 empty] | SCS | D |  | K0204-016
949 | 70MAL19AA051YB01 | 调节级前疏水阀(左)打开/关闭指令 | Drain valve before djusting stage(left) open/close command | 70MAL19AA051 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-017
950 | 70MAL19AA051XB01 | 调节级前疏水阀(左)全开状态 | Drain valve before djusting stage(left) full opened status | 70MAL19AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
951 | 70MAL19AA051XB11 | 调节级前疏水阀(左)全关状态 | Drain valve before djusting stage(left) full closed status | 70MAL19AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
952 | 70MAL19CT101 | 调节级前疏水阀(左)后温度 | Temperature after drain valve before djusting stage(left) | 70MAL19CT101 | 4~20mA | AI | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-017
953 | 70MAL21AA051YB01 | 调节级前疏水阀(右)打开/关闭指令 | Drain valve before djusting stage(right) open/close command | 70MAL21AA051 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-017
954 | 70MAL21AA051XB01 | 调节级前疏水阀(右)全开状态 | Drain valve before djusting stage(right) full opened status | 70MAL21AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
955 | 70MAL21AA051XB11 | 调节级前疏水阀(右)全关状态 | Drain valve before djusting stage(right) full closed status | 70MAL21AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
956 | 70MAL21CT101 | 调节级前疏水阀(右)后温度 | Temperature after drain valve before djusting stage(right) | 70MAL21CT101 | 4~20mA | AI | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-017
957 | 70MAL22AA051YB01 | 调节级后疏水阀打开/关闭指令 | Drain valve after djusting stage open/close command | 70MAL22AA051 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-017
958 | 70MAL22AA051XB01 | 调节级后疏水阀全开状态 | Drain valve after djusting stage full opened status | 70MAL22AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
959 | 70MAL22AA051XB11 | 调节级后疏水阀全关状态 | Drain valve after djusting stage full closed status | 70MAL22AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
960 | 70MAL22CT101 | 调节级后疏水阀后温度 | Temperature after drain valve after djusting stage | 70MAL22CT101 | 4~20mA | AI | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-017
961 | 70MAL14AA051YB01 | 主调门阀前疏水阀打开/关闭指令 | Drain valve before GV open/close command | 70MAL14AA051 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-017
962 | 70MAL14AA051XB01 | 主调门阀前疏水阀全开状态 | Drain valve before GV full opened status | 70MAL14AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
963 | 70MAL14AA051XB11 | 主调门阀前疏水阀全关状态 | Drain valve before GV full closed status | 70MAL14AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
964 | 70MAL14CT101 | 主调门阀前疏水阀后温度 | Temperature after drain valve before GV | 70MAL14CT101 | 4~20mA | AI | 0~600 | ℃ | [8 empty] | DAS | D |  | K0204-017
965 | 70MAL49AA051YB01 | 5#抽汽逆止阀前疏水阀打开/关闭指令 | Drain valve before 5# extraction steam check valve open/close command | 70MAL49AA051 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-017
966 | 70MAL49AA051XB01 | 5#抽汽逆止阀前疏水阀全开状态 | Drain valve before 5# extraction steam check valve full opened status | 70MAL49AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
967 | 70MAL49AA051XB11 | 5#抽汽逆止阀前疏水阀全关状态 | Drain valve before 5# extraction steam check valve full closed status | 70MAL49AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
968 | 70MAL49CT101 | 5#抽汽逆止阀前疏水阀后温度 | Temperature after drain valve before 5# extraction steam check valve | 70MAL49CT101 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-017
969 | 70MAL47AA051YB01 | 4#抽汽逆止阀前疏水阀打开/关闭指令 | Drain valve before 4# extraction steam check valve open/close command | 70MAL47AA051 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-017
970 | 70MAL47AA051XB01 | 4#抽汽逆止阀前疏水阀全开状态 | Drain valve before 4# extraction steam check valve full opened status | 70MAL47AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
971 | 70MAL47AA051XB11 | 4#抽汽逆止阀前疏水阀全关状态 | Drain valve before 4# extraction steam check valve full closed status | 70MAL47AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
972 | 70MAL47CT101 | 4#抽汽逆止阀前疏水阀后温度 | Temperature after drain valve before 4# extraction steam check valve | 70MAL47CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-017
973 | 70MAL46AA501YB01 | 蒸汽室疏水阀打开/关闭指令 | Steam chamber drain valve open/close command | 70MAL46AA501 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-017
974 | 70MAL46AA501XB01 | 蒸汽室疏水阀全开状态 | Steam chamber drain valve full opened status | 70MAL46AA501 | NO | DI | [10 empty] | SCS | D |  | K0204-017
975 | 70MAL46AA501XB11 | 蒸汽室疏水阀全关状态 | Steam chamber drain valve full closed status | 70MAL46AA501 | NO | DI | [10 empty] | SCS | D |  | K0204-017
976 | 70MAL46CT101 | 蒸汽室疏水阀后温度 | Temperature after steam chamber drain valve | 70MAL46CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-017
977 | 70MAL45AA051YB01 | #2级调整抽汽逆止阀前和各插管母管疏水阀打开/关闭指令 | Drain valve before #2 adjusting extraction steam check valve and intubation pipe open/close command | 70MAL45AA051 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-017
978 | 70MAL45AA051XB01 | #2级调整抽汽逆止阀前和各插管母管疏水阀全开状态 | Drain valve before #2 adjusting extraction steam check valve and intubation pipe full opened status | 70MAL45AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
979 | 70MAL45AA051XB11 | #2级调整抽汽逆止阀前和各插管母管疏水阀全关状态 | Drain valve before #2 adjusting extraction steam check valve and intubation pipe full closed status | 70MAL45AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
980 | 70MAL45CT101 | #2级调整抽汽逆止阀前和各插管母管疏水阀后温度 | Temperature after drain valve before #2 adjusting extraction steam check valve and intubation pipe | 70MAL45CT101 | 4~20mA | AI | 0~300 | ℃ | [8 empty] | DAS | D |  | K0204-017
981 | 70MAL43AA051YB01 | 2#抽汽和#1级非调整抽汽逆止阀前疏水阀打开/关闭指令 | Drain valve before 2# extraction steam and #1 non-adjusting extraction steam check valve open/close command | 70MAL43AA051 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-017
982 | 70MAL43AA051XB01 | 2#抽汽和#1级非调整抽汽逆止阀前疏水阀全开状态 | Drain valve before 2# extraction steam and #1 non-adjusting extraction steam check valve full opened status | 70MAL43AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
983 | 70MAL43AA051XB11 | 2#抽汽和#1级非调整抽汽逆止阀前疏水阀全关状态 | Drain valve before 2# extraction steam and #1 non-adjusting extraction steam check valve full closed status | 70MAL43AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
984 | 70MAL43CT101 | 2#抽汽和#1级非调整抽汽逆止阀前疏水阀后温度 | Temperature after drain valve before 2# extraction steam and #1 non-adjusting extraction steam check valve | 70MAL43CT101 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-017
985 | 70MAL41AA051YB01 | 1#抽汽逆止阀前疏水阀打开/关闭指令 | Drain valve before 1# extraction steam check valve open/close command | 70MAL41AA051 | NO | DO | [10 empty] | SCS | U | 220VAC | K0204-017
986 | 70MAL41AA051XB01 | 1#抽汽逆止阀前疏水阀全开状态 | Drain valve before 1# extraction steam check valve full opened status | 70MAL41AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
987 | 70MAL41AA051XB11 | 1#抽汽逆止阀前疏水阀全关状态 | Drain valve before 1# extraction steam check valve full closed status | 70MAL41AA051 | NO | DI | [10 empty] | SCS | D |  | K0204-017
988 | 70MAL41CT101 | 1#抽汽逆止阀前疏水阀后温度 | Temperature after drain valve before 1# extraction steam check valve | 70MAL41CT101 | 4~20mA | AI | 0~400 | ℃ | [8 empty] | DAS | D |  | K0204-017
989 | 70QUH10CT001H | 汽包炉水左/右侧取样水温度高 | The left /right side of boiler drum sampling Temp.H | 70QUH10GH001 | NO | DI |  | ℃ | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet | bar: H
990 | 70QUA10CT001H | 饱和蒸汽左/右侧取样水温度高 | The left /right side of saturated steam sampling Temp.H | 70QUH10GH001 | NO | DI |  | ℃ | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet | bar: H
991 | 70QUA30CT001H | 过热蒸汽取样水温度高 | Superheated steam sampling Temp.H | 70QUH10GH001 | NO | DI |  | ℃ | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet | bar: H
992 | 70QUB20CT001H | 省煤器入口给水取样水温度高 | Economizer inlet feedwater sampling Temp.H | 70QUH10GH001 | NO | DI |  | ℃ | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet | bar: H
993 | 70QUC10CT001H | 凝结水泵出口取样水温度高 | Condensate pump outlet water sampling Temp.H | 70QUH10GH001 | NO | DI |  | ℃ | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet | bar: H
994 | 70QUB30CT001H | 除氧器出口给水取样水温度高 | Deaerator outlet feedwater sampling Temp.H | 70QUH10GH001 | NO | DI |  | ℃ | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet | bar: H
995 | 70QUH10CF001L | 除盐水冷却水进水流量低 | Demineralized cooling water inlet water flow L | 70QUH10GH001 | NC | DI |  | mL/min | [8 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet | bar: L
996 | 70QUP01AP001XB01 | 恒温箱压缩机运行 | Thermostat compressor running | 70QUH10GH001 | NO | DI | [10 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
997 | 70QUP01AP001XB31 | 恒温箱压缩机故障 | Thermostat compressor fault | 70QUH10GH001 | NO | DI | [10 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
998 | 70QUP01AP002XB01 | 恒温箱循环泵运行 | Thermostat cyclic pump running | 70QUH10GH001 | NO | DI | [10 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
999 | 70QUP01AP002XB31 | 恒温箱循环泵故障 | Thermostat cyclic pump fault | 70QUH10GH001 | NO | DI | [10 empty] | SCS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1000 | 70QUH10CQ101 | 汽包炉水左/右侧取样水比导率 | The left /right side of boiler drum sampling specific conductivity | 70QUH10GH001 | 4~20mA | AI | 0.055~1000 | us/cm | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1001 | 70QUH10CQ102 | 汽包炉水左/右侧取样水pH | The left /right side of boiler drum sampling pH | 70QUH10GH001 | 4~20mA | AI | 0~14 | [9 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1002 | 70QUA10CQ101 | 饱和蒸汽左/右侧取样水氢电导率 | The left /right side of saturated steam sampling cation conductivity | 70QUH10GH001 | 4~20mA | AI | 0.055~1000 | us/cm | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1003 | 70QUA30CQ101 | 过热蒸汽取样水氢电导率 | Superheated steam sampling cation conductivity | 70QUH10GH001 | 4~20mA | AI | 0.055~1000 | us/cm | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1004 | 70QUB20CQ101 | 省煤器入口给水取样水氢电导率 | Economizer inlet feedwater sampling cation conductivity | 70QUH10GH001 | 4~20mA | AI | 0.055~1000 | us/cm | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1005 | 70QUB20CQ102 | 省煤器入口给水取样水比导率 | Economizer inlet feedwater sampling specific conductivity | 70QUH10GH001 | 4~20mA | AI | 0.055~1000 | us/cm | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1006 | 70QUB20CQ103 | 省煤器入口给水取样水pH | Economizer inlet feedwater sampling pH | 70QUH10GH001 | 4~20mA | AI | 0~14 | [9 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1007 | 70QUC10CQ101 | 凝结水泵出口取样水氢电导率 | Condensate pump outlet water sampling cation conductivity | 70QUH10GH001 | 4~20mA | AI | 0.055~1000 | us/cm | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1008 | 70QUC10CQ102 | 凝结水泵出口取样水含氧量 | Condensate pump outlet water sampling dissolved oxygen | 70QUH10GH001 | 4~20mA | AI | 0.01~300 | ppb | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1009 | 70QUB30CQ101 | 除氧器出口给水取样水含氧量 | Deaerator outlet feedwater sampling dissolved oxygen | 70QUH10GH001 | 4~20mA | AI | 0.01~300 | ppb | [8 empty] | DAS | U |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1010 | 70QUH10CP101 | 除盐水冷却水进水压力 | Demineralized cooling water inlet water pressure | 70QUH10GH001 | 4~20mA | AI | 0~1.6 | Mpa | [8 empty] | DAS | D |  | K0605-001 | 汽水取样装置控制柜 | Water steam sampling device control cabinet
1011 | 70PGA10AP001XB01 | 1#除盐水泵运行 | 1# demineralized water pump running | 70PGA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
1012 | 70PGA10AP001XB31 | 1#除盐水泵故障 | 1# demineralized water pump fault | 70PGA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
1013 | 70PGA10AP002XB01 | 2#除盐水泵运行 | 2# demineralized water pump running | 70PGA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
1014 | 70PGA10AP002XB31 | 2#除盐水泵故障 | 2# demineralized water pump fault | 70PGA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
1015 | 70PGA10CL101H | 除盐水箱液位高 | Demineralized water tank level H | 70PGA10GH001 | NO | DI |  | m | [8 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet | bar: H
1016 | 70PGA10CL101L | 除盐水箱液位低 | Demineralized water tank level L | 70PGA10GH001 | NO | DI |  | m | [8 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet | bar: L
1017 | 70PGA20CP001L | 工业冷却水入口压力低 | Industrial cooling water inlet pressure L | 70PGA10GH001 | NO | DI |  | Mpa | [8 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet | bar: L
1018 | 70PGA10CT001H | 换热器出口母管温度高 | Heat exchanger outlet main pipe temperature H | 70PGA10GH001 | NO | DI |  | ℃ | [8 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet | bar: H
1019 | 70PGA10AA002XB01 | 除盐水箱入口电磁阀全开状态 | Demineralized water tank inlet SV opened status | 70PGA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0605-002 | 除盐水装置控制柜 | Demineralized water device control cabinet
1020 | 70QCD11CL101 | 1#氨溶液箱液位 | 1# ammonia solution tank level | 70QCD10GH001 | 4~20mA | AI |  | m | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1021 | 70QCD12CL101 | 2#氨溶液箱液位 | 2# ammonia solution tank level | 70QCD10GH001 | 4~20mA | AI |  | m | [8 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1022 | 70QCD11AM001YB01 | 1#氨溶液箱搅拌机启动/停止指令 | 1# ammonia solution tank agitator start/stop command | 70QCD10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1023 | 70QCD11AM001XB01 | 1#氨溶液箱搅拌机运行 | 1# ammonia solution tank agitator running | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1024 | 70QCD11AM001XB31 | 1#氨溶液箱搅拌机故障 | 1# ammonia solution tank agitator fault | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1025 | 70QCD11AM001XB21 | 1#氨溶液箱搅拌机远程 | 1# ammonia solution tank agitator remote control | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1026 | 70QCD12AM001YB01 | 2#氨溶液箱搅拌机启动/停止指令 | 2# ammonia solution tank agitator start/stop command | 70QCD10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1027 | 70QCD12AM001XB01 | 2#氨溶液箱搅拌机运行 | 2# ammonia solution tank agitator running | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1028 | 70QCD12AM001XB31 | 2#氨溶液箱搅拌机故障 | 2# ammonia solution tank agitator fault | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1029 | 70QCD12AM001XB21 | 2#氨溶液箱搅拌机远程 | 2# ammonia solution tank agitator remote control | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1030 | 70QCD11AP001YB01 | 1#给水氨计量泵启动/停止指令 | 1# feed water ammonia metering pump start/stop command | 70QCD10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1031 | 70QCD11AP001XB01 | 1#给水氨计量泵运行 | 1# feed water ammonia metering pump running | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1032 | 70QCD11AP001XB31 | 1#给水氨计量泵故障 | 1# feed water ammonia metering pump fault | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1033 | 70QCD11AP001XB21 | 1#给水氨计量泵远程 | 1# feed water ammonia metering pump remote control | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1034 | 70QCD11AP001YQ01 | 1#给水氨计量泵频率给定 | 1# feed water ammonia metering pump frequency given | 70QCD10GH001 | 4~20mA | AO | 0~50 | Hz | [8 empty] | MCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1035 | 70QCD11AP001XQ11 | 1#给水氨计量泵频率反馈 | 1# feed water ammonia metering pump frequency feedback | 70QCD10GH001 | 4~20mA | AI | 0~50 | Hz | [8 empty] | MCS | U |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1036 | 70QCD12AP001YB01 | 2#给水氨计量泵启动/停止指令 | 2# feed water ammonia metering pump start/stop command | 70QCD10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1037 | 70QCD12AP001XB01 | 2#给水氨计量泵运行 | 2# feed water ammonia metering pump running | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1038 | 70QCD12AP001XB31 | 2#给水氨计量泵故障 | 2# feed water ammonia metering pump fault | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1039 | 70QCD12AP001XB21 | 2#给水氨计量泵远程 | 2# feed water ammonia metering pump remote control | 70QCD10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1040 | 70QCD12AP001YQ01 | 2#给水氨计量泵频率给定 | 2# feed water ammonia metering pump frequency given | 70QCD10GH001 | 4~20mA | AO | 0~50 | Hz | [8 empty] | MCS | D |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1041 | 70QCD12AP001XQ11 | 2#给水氨计量泵频率反馈 | 2# feed water ammonia metering pump frequency feedback | 70QCD10GH001 | 4~20mA | AI | 0~50 | Hz | [8 empty] | MCS | U |  | K0601-001 | 加氨装置控制箱 | Ammonia dosing device control cabinet
1042 | 70QCA11CL101 | 1#联氨溶液箱液位 | 1# hydrazine solution tank level | 70QCA10GH001 | 4~20mA | AI |  | m | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1043 | 70QCA12CL101 | 2#联氨溶液箱液位 | 2# hydrazine solution tank level | 70QCA10GH001 | 4~20mA | AI |  | m | [8 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1044 | 70QCA11AM001YB01 | 1#联氨溶液箱搅拌机启动/停止指令 | 1# hydrazine solution tank agitator start/stop command | 70QCA10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1045 | 70QCA11AM001XB01 | 1#联氨溶液箱搅拌机运行 | 1# hydrazine solution tank agitator running | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1046 | 70QCA11AM001XB31 | 1#联氨溶液箱搅拌机故障 | 1# hydrazine solution tank agitator fault | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1047 | 70QCA11AM001XB21 | 1#联氨溶液箱搅拌机远程 | 1# hydrazine solution tank agitator remote control | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1048 | 70QCA12AM001YB01 | 2#联氨溶液箱搅拌机启动/停止指令 | 2# hydrazine solution tank agitator start/stop command | 70QCA10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1049 | 70QCA12AM001XB01 | 2#联氨溶液箱搅拌机运行 | 2# hydrazine solution tank agitator running | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1050 | 70QCA12AM001XB31 | 2#联氨溶液箱搅拌机故障 | 2# hydrazine solution tank agitator fault | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1051 | 70QCA12AM001XB21 | 2#联氨溶液箱搅拌机远程 | 2# hydrazine solution tank agitator remote control | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1052 | 70QCA11AP001YB01 | 1#给水联氨计量泵启动/停止指令 | 1# feed water hydrazine metering pump start/stop command | 70QCA10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1053 | 70QCA11AP001XB01 | 1#给水联氨计量泵运行 | 1# feed water hydrazine metering pump running | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1054 | 70QCA11AP001XB31 | 1#给水联氨计量泵故障 | 1# feed water hydrazine metering pump fault | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1055 | 70QCA11AP001XB21 | 1#给水联氨计量泵远程 | 1# feed water hydrazine metering pump remote control | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1056 | 70QCA11AP001YQ01 | 1#给水联氨计量泵频率给定 | 1# feed water hydrazine metering pump frequency given | 70QCA10GH001 | 4~20mA | AO | 0~50 | Hz | [8 empty] | MCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1057 | 70QCA11AP001XQ11 | 1#给水联氨计量泵频率反馈 | 1# feed water hydrazine metering pump frequency feedback | 70QCA10GH001 | 4~20mA | AI | 0~50 | Hz | [8 empty] | MCS | U |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1058 | 70QCA12AP001YB01 | 2#给水联氨计量泵启动/停止指令 | 2# feed water hydrazine metering pump start/stop command | 70QCA10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1059 | 70QCA12AP001XB01 | 2#给水联氨计量泵运行 | 2# feed water hydrazine metering pump running | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1060 | 70QCA12AP001XB31 | 2#给水联氨计量泵故障 | 2# feed water hydrazine metering pump fault | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1061 | 70QCA12AP001XB21 | 2#给水联氨计量泵远程 | 2# feed water hydrazine metering pump remote control | 70QCA10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1062 | 70QCA12AP001YQ01 | 2#给水联氨计量泵频率给定 | 2# feed water hydrazine metering pump frequency given | 70QCA10GH001 | 4~20mA | AO | 0~50 | Hz | [8 empty] | MCS | D |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1063 | 70QCA12AP001XQ11 | 2#给水联氨计量泵频率反馈 | 2# feed water hydrazine metering pump frequency feedback | 70QCA10GH001 | 4~20mA | AI | 0~50 | Hz | [8 empty] | MCS | U |  | K0601-001 | 加联氨装置控制箱 | Hydrazine dosing device control cabinet
1064 | 70QCC11CL101 | 1#磷酸盐溶液箱液位 | 1# phosphate solution tank level | 70QCC10GH001 | 4~20mA | AI |  | m | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1065 | 70QCC12CL101 | 2#磷酸盐溶液箱液位 | 2# phosphate solution tank level | 70QCC10GH001 | 4~20mA | AI |  | m | [8 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1066 | 70QCC11AM001YB01 | 1#磷酸盐溶液箱搅拌机启动/停止指令 | 1# phosphate solution tank agitator start/stop command | 70QCC10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1067 | 70QCC11AM001XB01 | 1#磷酸盐溶液箱搅拌机运行 | 1# phosphate solution tank agitator running | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1068 | 70QCC11AM001XB31 | 1#磷酸盐溶液箱搅拌机故障 | 1# phosphate solution tank agitator fault | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1069 | 70QCC11AM001XB21 | 1#磷酸盐溶液箱搅拌机远程 | 1# phosphate solution tank agitator remote control | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1070 | 70QCC12AM001YB01 | 2#磷酸盐溶液箱搅拌机启动/停止指令 | 2# phosphate solution tank agitator start/stop command | 70QCC10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1071 | 70QCC12AM001XB01 | 2#磷酸盐溶液箱搅拌机运行 | 2# phosphate solution tank agitator running | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1072 | 70QCC12AM001XB31 | 2#磷酸盐溶液箱搅拌机故障 | 2# phosphate solution tank agitator fault | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1073 | 70QCC12AM001XB21 | 2#磷酸盐溶液箱搅拌机远程 | 2# phosphate solution tank agitator remote control | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1074 | 70QCC11AP001YB01 | 1#磷酸盐计量泵启动/停止指令 | 1# phosphate metering pump start/stop command | 70QCC10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1075 | 70QCC11AP001XB01 | 1#磷酸盐计量泵运行 | 1# phosphate metering pump running | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1076 | 70QCC11AP001XB31 | 1#磷酸盐计量泵故障 | 1# phosphate metering pump fault | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1077 | 70QCC11AP001XB21 | 1#磷酸盐计量泵远程 | 1# phosphate metering pump remote control | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1078 | 70QCC12AP001YB01 | 2#磷酸盐计量泵启动/停止指令 | 2# phosphate metering pump start/stop command | 70QCC10GH001 | NO | DO | [10 empty] | SCS | U | 220VAC | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1079 | 70QCC12AP001XB01 | 2#磷酸盐计量泵运行 | 2# phosphate metering pump running | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1080 | 70QCC12AP001XB31 | 2#磷酸盐计量泵故障 | 2# phosphate metering pump fault | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1081 | 70QCC12AP001XB21 | 2#磷酸盐计量泵远程 | 2# phosphate metering pump remote control | 70QCC10GH001 | NO | DI | [10 empty] | SCS | D |  | K0601-001 | 加磷酸盐装置控制箱 | Phosphate dosing device control cabinet
1082 | 70GNR10CQ101 | 机组排水槽pH | Unit drain pit pH | 70GNR10CQ101 | 4~20mA | AI | 0~14 | [9 empty] | DAS | U |  | K0607-001
1083 | 70GNR10CP101 | 机组排水槽废水泵出口母管压力 | Unit drain pit waste water pump outlet main pipe pressure | 70GNR10CP101 | 4~20mA | AI | 0~0.6 | Mpa | [8 empty] | DAS | D |  | K0607-001
1084 | 70CSB11XB31 | 主厂房热控400VAC电源柜电源失电报警 | Main building I&C 400VAC power cabinet power lost alarm | 70CSB11 | NO | DI | [10 empty] | DAS | D |  |  | 主厂房热控400VAC电源柜A | Main building I&C 400VAC power cabinet A
1085 | 70CSB11XB32 | 主厂房热控400VAC电源柜ATS主电源失去报警 | Main building I&C 400VAC power cabinet ATS main Power Lost Alarm | 70CSB11 | NO | DI | [10 empty] | DAS | D |  |  | 主厂房热控400VAC电源柜A | Main building I&C 400VAC power cabinet A
1086 | 70CSB11XB33 | 主厂房热控400VAC电源柜ATS副电源失去报警 | Main building I&C 400VAC power cabinet A Vice Power Lost Alarm | 70CSB11 | NO | DI | [10 empty] | DAS | D |  |  | 主厂房热控400VAC电源柜A | Main building I&C 400VAC power cabinet A
1087 | 70CSB02XB31 | 主厂房热控220VAC电源柜电源失电报警 | Main building I&C 220VAC power cabinet power lost alarm | 70CSB02 | NO | DI | [10 empty] | DAS | D |  |  | 主厂房热控220VAC电源柜A | Main building I&C 220VAC power cabinet A
1088 | 70CSB02XB32 | 主厂房热控220VAC电源柜ATS主电源失去报警 | Main building I&C 220VAC power cabinet ATS main Power Lost Alarm | 70CSB02 | NO | DI | [10 empty] | DAS | D |  |  | 主厂房热控220VAC电源柜A | Main building I&C 220VAC power cabinet A
1089 | 70CSB02XB33 | 主厂房热控220VAC电源柜ATS副电源失去报警 | Main building I&C 220VAC power cabinet ATS Vice Power Lost Alarm | 70CSB02 | NO | DI | [10 empty] | DAS | D |  |  | 主厂房热控220VAC电源柜A | Main building I&C 220VAC power cabinet A